## Slide 1: Interior LED Parking Garage External Driver Lamp-Style Retrofit Kits (UL Type C)
Martin Vu, RMS
July 2016

## Slide 2: Presentation Overview
Objective: Seeking TF approval of draft workpaper
Measure Description
Workpaper Methodology
Results
Issues and Concerns
Questions or Comments

## Slide 3: Measure Description
Base Case
Measure Case
Base case technology
Four foot 2-lamp 2nd generation normal light output (NLO) F32T8 Linear Fluorescent fixture with bi-level occupancy sensor and photocell controls in day lit zones
Four foot 2-lamp 2nd generation normal light output (NLO) F32T8 Linear Fluorescent fixture with bi-level occupancy sensing control in non-day lit zones
Measure case technology
Four foot 2-lamp LED External Driver Lamp-Style Retrofit Kit (UL Type C) fixture with bi-level occupancy sensor and photocell controls in day lit zones
Four foot 2-lamp LED External Driver Lamp-Style Retrofit Kit (UL Type C) fixture with bi-level occupancy sensing control in non-day lit zones

## Slide 4: Measure Description
Linear LED retrofit kits are designed to
  replace existing fluorescent lamps
  require some form of rewiring such as replacing the ballasts
  come prepackaged with all the required components to complete the retrofit
  come in two forms:
    LED retrofit kit, such as light bar and lamp-style replacement, or
    LED troffer retrofit kit with new doorframe and lens assemblies.
This wp focuses on a four foot 2-lamp External Driver Lamp-Style Linear LED Retrofit Kit (UL Type C) fixture
  employ lamp holders to connect to the fixture being retrofitted,
  do not operate off the existing fluorescent ballast, and
  require rewiring of the existing fixture to replace the ballast with an external driver.
Lamp holders are then wired to receive only the low-voltage electricity that is supplied by that external driver.

## Slide 5: Measure Description
Units: per fixture
Measure Application and Delivery Type
  Downstream Deemed (ROB)
Eligibility
  Climate Zones: All
  Building Types: All
Target Market
  Commercial
    Large Office
    Large Retail
    Hotel
    Hospital
    Education – Universities and Community Colleges
    Mixed Use both retail and residential sharing the garage
  High-rise multifamily residential (8-units or more)
Market Potential
  CA indoor parking garages 63 GWh energy savings
    (Derived from US DOE LED Adoption Report 2015).

## Slide 6: Measure Description
Measure Costs
  Baseline cost:
    Day lit zone fixtures: $322.46/fixture
      Material Cost includes: F32T8 2-lamp fixture, occupancy sensor and photocell
    Non-day lit zone fixtures: $207.07
      Material Cost includes: F32T8 2-lamp fixture, occupancy sensor and photocell
  Measure cost:
    Day lit zone fixtures: $412.22/fixture
      Material Cost includes: LED External Driver Retrofit Kit fixture , occupancy sensor and photocell
    Non-day lit zone fixtures: $296.83
      Material Cost includes: LED External Driver Retrofit Kit fixture , occupancy sensor and photocell
  Incremental cost:
    Day lit zone fixtures: $412.22 - $322.46 = $89.76/fixture
    Non-day lit zone fixtures: $296.83 - $207.07 = $89.76/fixture
EUL
  Day lit zone fixtures: 16 years (DEER EUL ID: ILtg-Lfluor-fix)
  Non-day lit zone fixtures: 8.3 years (Need new DEER EUL ID)
NTG
  0.70 (DEER NTG ID: All-Default<=2yrs)
    All other EEM with no evaluated NTGR; new technology in program for 2 or fewer years
  0.85 (DEER NTG ID: Res-Default-HTR-di) All other EEM with no evaluated NTGR; direct install hard-to-reach only.
  0.85 (DEER NTG ID: Com-Default-HTR-di) All other EEM with no evaluated NTGR; direct install hard-to-reach only.

## Slide 7: Workpaper Methodology: Baseline
Baseline data collection – Operating Hours
  CPUC 2015 Workpaper Guidance – Lighting Retrofits, dated January 27, 2015
  California Marshal 2014 Code Interpretation Means of Egress Illumination
  California Utilities Codes and Standards Team 2011 Statewide Parking Garage Lighting and Controls Codes and Standards Enhancement (CASE) Initiative Draft Measure Report
  Energy Solutions’ 2012 Energy Technology Assistance Program Field Study Final Report (ETAP Report)
  IOU Table of Standard Fixture Wattages

## Slide 8: Workpaper Methodology: Baseline
Baseline data collection – Existing Base Case Fixtures
  Energy Solutions’ 2012 Energy Technology Assistance Program Field Study Final Report (ETAP Report)
  California Utilities Codes and Standards Team 2011 Statewide Parking Garage Lighting and Controls Codes and Standards Enhancement (CASE) Initiative Draft Measure Report
  DOE’s July 2015 Adoption of Light-Emitting Diodes in Common Lighting Applications
  Southern California Edison (SCE) 2013-2015 Custom Project Files
  Benya Burnett Consultancy Parking Garage Lighting Background and Basis of Recommendations

## Slide 9: Workpaper Methodology: Baseline
Baseline Methodology
Based on 2012 ETAP Report, existing fixtures located in non-day lit zones are
  in low power mode 62% of the time.
    Low power mode is estimated to be 50% of full power.
  in high power mode for 38% at 100% full power.
[(0.059 kW*0.5*8760*0.62) + (0.059 kW*1.0*8760*0.38)] = 357 kWh
Equation 1. Baseline kWh for a four foot 2-lamp 2nd generation F32T8 NLO fixture in non-day lit zones

## Slide 10: Workpaper Methodology: Baseline
Baseline Methodology
Based on 2012 ETAP Report, existing fixtures located in day lit zones are
  in low power mode 74% of the time.
    Low power mode is estimated to be 50% of full power.
  in high power mode for 26% at 100% full power.
[(0.059 kW*0.5*4380*0.74) + (0.059 kW*1.0*4380*0.26)] = 160 kWh
Equation 2. Baseline kWh for a four foot 2-lamp 2nd generation F32T8 NLO fixture in day lit zones

## Slide 11: Workpaper Methodology: Measure
Measure data collection
Design Lights Consortium (DLC) Qualified Products List (QPL)
  To ensure that the Linear LED retrofit kit fixtures provides equal performance to the fluorescent lighting being replaced, External Driver Lamp-Style Retrofit Kits (UL Type C) filtered from the DLC’s QPL must provide at least 2,300 lumens (2-lamp configuration).
Commission Staff Observations for Interior Parking Garage Linear Fluorescent to LED Luminaires or Retrofit Kits – July 13, 2016 Email
DOE’s July 2015 Adoption of Light-Emitting Diodes in Common Lighting Applications
Benya Burnett Consultancy Parking Garage Lighting Background and Basis of Recommendations

## Slide 12: Workpaper Methodology: Measure
As shown in Table 13, the average LED lamp generates 2,620 lumens and consumes 20.8 watts.
The driver loss is included in the system rating.
Since there are no standards for TLEDs, Table 13 provides a provisional reference table to aid in policy decisions.

## Slide 13: Workpaper Methodology: Baseline
Measure Case Methodology
Based on 2012 ETAP Report, new LED retrofit kit fixtures located in day lit zones are
  in low power mode 74% of the time.
    Low power mode is estimated to be 50% of full power.
  in high power mode for 26% at 100% full power.
  Fixtures with photocells operate 7PM to 7AM or 4,380 annual hours
[(0.042 kW*0.5*4380*0.74) + (0.042 kW*1.0*4380*0.26)] = 114 kWh
Equation 3. Measure Case kWh for a Linear LED External Driver Lamp-Style Retrofit Kits (UL Type C) fixture in day lit zones

## Slide 14: Workpaper Methodology: Baseline
Measure Case Methodology
Based on 2012 ETAP Report, existing fixtures located in non-day lit zones are
  in low power mode 62% of the time.
    Low power mode is estimated to be 50% of full power.
  in high power mode for 38% at 100% full power.
[(0.042 kW*0.5*8760*0.62) + (0.042 kW*1.0*8760*0.38)] = 254 kWh
Equation 4. Measure Case kWh for a Linear LED External Driver Lamp-Style Retrofit Kits (UL Type C) fixture in non-day lit zones

## Slide 15: Results
Project Name: | SAMPLE FOR ILLUSTRATION ONLY |  |  |  |  |  |  | 
 |  | COST/BENEFIT INPUTS |  |  |  |  | COST/BENEFIT OUTPUTS | 
 | ROB | ER | ROB |  |  | ROB | ER | ROB
Target Sector | NON_RES | Non_RES | Non_RES |  | A. TOTAL Resource Cost (TRC) Test: |  |  | 
Measure End Use Shape | DEER:Indoor_Non-CFL_Ltg | DEER:Indoor_Non-CFL_Ltg | DEER:Indoor_Non-CFL_Ltg |  | Net Benefits (TRC) | $ (1,175,758) | $ 9,958,921 | $ (2,067,134)
Climate Zone | System | System | System |  | B/C Ratio (TRC) | 0.79 | 2.06 | 0.62
Valid Sector/ End Use Combo? | TRUE | TRUE | TRUE |  |  |  |  | 
Unit Definition (HP, Ton, Sq Ft, etc) | Fixture | Fixture | Fixture |  | B. Program Adminstrator Cost (PAC) Test: |  |  | 
Market Size (Units) | 1,500,000 | 1,500,000 | 1,500,000 |  | Net Benefits (PAC) | $ 1,817,186 | $ 13,833,620 | $ 1,039,999
Annual Penetration Rate (%) | 5% | 5% | 5% |  | B/C Ratio (PAC) | 1.69 | 3.52 | 1.45
Annual Penetration (Units) | 75,000 | 75,000 | 75,000 |  | SCE Cost $/ Lifecycle kWh | $ 0.061 | $ 0.128 | $ 0.062
Annual kWh Savings per Unit | 103 | 103 | 46 |  | SCE Cost $/ kW | $ 3,781 | $ 821 | #DIV/0!
kW Savings per Unit | 0.01 | 0.13 | - |  |  |  |  | 
Gross Measure Cost($)/Unit | $ 90 | $ 90 | $ 90 |  | C. Annual Goal Achievement: |  |  | 
Incentive ($) per Unit | $ 30 | $ 70 | $ 28 |  | Gross Annual kWh Savings | 7,725,000 | 7,725,000 | 3,450,000
Effective Useful Life (yrs) | 8.3 | 8.3 | 16 |  | Gross Annual kW Savings | 1,033 | 9,975 | -
Administrative Costs ($) | $ 463,500 | $ 463,500 | $ 207,000 |  |  |  |  | 
Marketing & Other Costs ($) | $ 20,000 | $ 20,000 | $ 100,000 |  |  |  |  | 
Adjustment Factors: |  |  |  |  |  |  |  | 
Net-to-Gross Ratio (NTG) | 70% | 70% | 70% |  |  |  |  | 
Installation/Gross Realization Rt | 100% | 100% | 100% |  |  |  |  | 
Results are close approximations. Actual E3 calculation may vary depending on additional inputs. |  |  |  |  |  |  |  | 

## Slide 16: Issues and Concerns
Abstract Review Comments from the Cal TF
Cal TF comments

## Slide 17: Issues and Concerns – Other Comments
CPUC Early Observation
EAR Team comment

## Slide 18: Issues and Concerns – Future Updates
Future update Industry Standard Practice
  EAR team observes the standard practice is changing extremely rapidly on this technology. The EAR team representative indicated that when determining industry standard practice, to consider limiting the time frame to the last ~1 year (summer of 2015 to present day) due to the uncertainty of whether a project designed or retrofit today would normally install T8s or LEDs.
  Therefore, to help substantiate the energy savings for an early retirement option, baseline data can be collected during program implementation as a future data collection effort.

## Slide 19: Issues and Concerns – Future Updates
Collecting Baseline Data to Support ER
  CalTF recommended collecting baseline data during program implementation to support a future early retirement (ER) application type for consideration in a future workpaper update to address current industry standard practice and because of the higher energy savings opportunity.
Collecting Baseline Data to update eligibility requirements
  American Medical Association Article:
    In addition to its impact on drivers, blue-rich LED streetlights operate at a wavelength that most adversely suppresses melatonin during night. It is estimated that white LED lamps have five times greater impact on circadian sleep rhythms than conventional street lamps. Recent large surveys found that brighter residential nighttime lighting is associated with reduced sleep times, dissatisfaction with sleep quality, excessive sleepiness, impaired daytime functioning and obesity.
    It appears that this article does not directly apply to interior parking garage lighting but should be monitored during program implementation.

## Slide 20: Questions or Comments?