## Field names
Category Fields | E-5152 |  | E-5152 | E-5152 |  | Combine fields | Permutation also |  | Inspection Documentation | QPL | QPL | MAT specific; video link | Formulas, Capacity
Workpaper ID | SWFS001 | SWAP006 | SWHC005 | SWHC005 | SWHC001 | SWHC031 | SWCR017 | SWFS010 | SWHC038 | SWFS004 | SWFS004 | SWWH001 | SWHC013 | SWFS003 | SWHC004 | SWHC005 | SWWH006 | SWHC018 | Measure ID | SWHC004
Revision # | 2 | 2 | 3 | 3 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 5 | 2 | Measure Version ID | 2
WP Name | Convection Oven, Commercial | Dishwasher, Residential | Water Cooled Chiller | Water Cooled Chiller | Wall Furnace, Residential | High Efficiency Furnace, Residential | High Efficiency Ultra-Low Temperature Freezers | Commercial Hand-Wrap Machine, Electric | Brushless Fan Motor Replacement, Residential | Griddle, Commercial | Griddle, Commercial | Faucet Aerator, Residential | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 kBtuh, Commercial | Combination Oven, Commercial | Space Heating Boiler | Water-Cooled Chiller | Tankless Water Heater, Commercial | VSD for HVAC Fan Controls, Commercial | Measure Name | Space Heating Boiler
WP Offering ID | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | A,E,I,M,U,Q | A,B,C,D,N,O | D | S | Q | A | Any | Offering ID – Offering ID referenced from Offering ID value table within the measure | Any
MeasAppType | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | AR | Any | Any | Any | Any | Any | Any | MeasAppType – Measure application type (choice) | Any
DeliveryType | Any | Any | UpDeemed | DnDeemed, DnDeemDI | UpDeemed | UpDeemed | Any | Any | Any | Any | Any | DnDeemDI | Any | Any | Any | Any | Any | Any | DeliveryType – Delivery type (choice) | Any
Vintage | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Vintage – Building vintage (choice)
Property Fields
Sort Order | 2 | 1 | 5 | 5 | 2 | 8 | 3 | 3 | 3 | 5 | 5 | 4 | 39 | 34 | 11 | 36 | 6 |  | Sort Order – sequential/unique order of validation data records | 5
Source Record (Item from Measure Package requiring Property) | Data Collection Requirements: E-5152 Data Collection Requirements table | Data Collection Requirements: E-5152 Data Collection Requirements table | Data Collection Requirements: E-5152 Data Collection Requirements table | Data Collection Requirements: E-5152 Data Collection Requirements table | Data Collection Requirements: E-5152 Data Collection Requirements table | E-5152 Data Collection Requirements | Program Requirements: Eligible Building Types: This measure is applicable for the following existing building types Eun = Com-Education - University Hsp = Com-Health/Medical - Hospital IPH = Ind-Manufacturing Pharmaceutical MBT = Ind-Manufacturing Biotech | Program Exclusions: Used or rebuilt equipment are not eligible. | Program Requirements: Eligible Products: The HVAC system must be functional/operable and drawing power. | Program Requirements: Eligible Products: This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Program Requirements: Eligible Products: This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Program Requirements: Eligible Products: The low-flow faucet aerator and flow control valve (FCV) must be installed on an existing faucet with a flow rate that complies with the Measure Case Specification. | Data Collection Requirements: E-5152 Data Collection Requirements table | Program Requirements: Eligible Products: This measure includes new commercial steam/convection combination ovens that meet the following requirements based on the ENERGY STAR Program Requirements For Commercial Ovens | Program Requirements: Eligible Products: The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Program Requirements: Eligible Products: Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Measure Case Description: The minimum qualifying efficiency ratings of each measure offering are specified below. | Program Requirements: Eligible Products: This measure requires the installation of a VSD and associated controls on a motor driving a ventilation fan. Eligibility requirements include: • The fan must be ≤ 100 hp. | Source Record – copied text from the measure package to directly connect to the Property Name.
Property Enabled | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes
Property Name | Model | Manufacturer | Serial Number | Serial Number | Equipment ID | RetailPrice | Building Type | New Equipment | Operational | Energy Star Qualified | Energy Star Qualified | Flow Rate | Capacity (kBtuh) | Steam Efficiency | Thermal Efficiency (%) | Full Load Efficiency (kW/ton) | Uniform Energy Factor | Input Rating | Property Name – validation property name that can be chosen from a list of common properties or created as a custom entry. Common properties are preferred to drive consistency across measure packages. | RefNum
Property Label | What is the Model Number of the new convection oven? | What is the Manufacturer of the new dishwasher? | What is the Serial Number of the new water cooled chiller? | What is the Serial Number of the new water cooled chiller? | What is the ID on this Equipment that identifies it to the site? | Retail Price | What is the basic use of the building? | Is the equipment new (not used or rebuilt)? | Is the HVAC system functional/operable and drawing power? | Is the new griddle on the ENERGY STAR Qualified product list? | Is the new griddle on the ENERGY STAR Qualified product list? | What is the Flow Rate of new faucet aerator (gpm)? | What is the Cooling Capacity (kBtu/hr) of the new HVAC unit? | What is the Steam Mode Cooking Efficiency (%) of the new combination oven? | What is the Thermal Efficiency (%) of the new space heating boiler? | What is the Full Load Efficiency (kW/ton) of the new water-cooled chiller? | What is the Uniform Energy Factor (UEF) of the new tankless water heater? | What is the Input Power Rating (hp) of the fan motor? | Property – Label – further description of the name to make the property easier to interpret; sometimes can be modified to a question. | AHRI Reference Number
Data Type | Text Box | Text Box | Text Box | Text Box | Text Box | Number | Drop Down List | Drop Down List | Drop Down List | Drop Down List | QPL | Number | Number | Percentage | Percentage | Number | Number | Number | Property - Installation - Control Type – choice (Date, List, Text, Number, Formula, None)
Choices | n/a | n/a | n/a | n/a | n/a |  | Education – University; Health/Medical – Hospital; Manufacturing – Biotech; Manufacturing – Pharmaceuticals; Other; | Yes;No | Yes;No | Yes;No | Yes;No | n/a | n/a | n/a | n/a | n/a | n/a | n/a | Property – Installation – Values – Custom – choice from List values
Property Description | Photograph of the nameplate of the new convection oven that is being installed that shows the model number. This is typically located... | Photograph of the nameplate of the new dishwasher that is being installed that shows the manufacturer's name. This is typically located... | Photograph of the nameplate of the new water cooled chiller that is being installed that shows the serial number. This is typically located... | Photograph of the nameplate of the new water cooled chiller that is being installed that shows the serial number. This is typically located... | Photograph of the Equipment ID that uniquely identifies it on the site. | (add comment) | Building type from customer NAICS code can be different from application, but justification required (ie, customer affidavit) | The equipment being installed must have been manufactured new - not rebuilt or used. (explain why) | The existing HVAC equipment must be functional and capable of operating, which includes the other primary components of the system such as the compressor and condenser. | The manufacturer and model number of the new griddle that is being installed should be on the ENERGY STAR Qualified product list at the time that the application was submitted. | The manufacturer and model number of the new griddle that is being installed should be on the ENERGY STAR Qualified product list at the time that the application was submitted: https://www.energystar.gov/productfinder/product/certified-commercial-griddles/results | The flow rate after installation must be equal to or lower than the measure case flow rate. | The cooling capacity of the new unit should be documented in the units of kBtu/hr or tons, which can typically be found on the nameplate of the unit. | The Steam Mode Cooking Efficiency (%) of the new combination oven can be found in specification sheets. | The Thermal Efficiency (%) should be listed on the equipment's nameplate or on the equipment's specification sheet. Note that Thermal Efficiency is different than Combustion Efficiency. | The Full Load Efficiency (kW/ton) should be listed on the equipment's nameplate or on the equipment's specification sheet. | The Uniform Energy Factor (UEF) should be listed on the equipment's nameplate or on the equipment's specification sheet. | The input power rate is listed on the nameplate of the fan motor; if this is not accessible, it could be found on equipment specification sheets. | Property Comment – measure specific comment to provide context or specific instructions
Validation Fields
Validation Rule | n/a | n/a | n/a | n/a | n/a |  | Must not be 'Other' | Must be 'Yes' | Must be 'Yes' | Must be 'Yes' | Must be 'Yes' | Must be <= 1.5 AND > 1.2 | Must be 65 <= x < 134 | Must be >= 41% | Must be >= 83% | Must be <= 0.497 | Must be >= 0.81 | Must be ≤ 100 | Validation Rule – logical statement or assertion that describes the passing state
Validation criteria | [6 empty] | Not equal to Other | Equal to Yes | Equal to Yes | Yes | Yes | LTE 1.5 gpm | GTE 65 kBtu/hr and LT 134 kBtu/hr | GTE 38% | GTE 83% | LTE 0.497 kW/ton | GTE 0.81 | LTE 100 hp | Validation Criteria – logical statement of how the correct answer can vary (ie, Equal to, Greater than, etc)
Validation Correct Answer | [6 empty] | Not equal | Equal | Equal | Equal | Equal | LTE | GTE and LT | GTE | GTE | LTE | GTE | LTE | Validation Correct Answer – value that designates the passing criteria
Numeric Type | [5 empty] | US Dollars | [5 empty] | Number | Number | Percentage | Percentage | Number | Number | Number | Numeric Type – number type (currency, number, percent, none)
Min Value | n/a | n/a | n/a | n/a | n/a |  | n/a | n/a | n/a | n/a | n/a | 1.2 | 65 | 41% | 83% | 0 | 0.81 | 0 | Min Value – minimum range of the value allowed
Max Value | n/a | n/a | n/a | n/a | n/a |  | n/a | n/a | n/a | n/a | n/a | 1.5 | 134 | 100% | 100% | 0.497 | 1 | 100 | Max Value – maximum range of the value allowed
Decimal Places | [18 empty] | Decimal Places
Checkpoint | Post-Install Inspection | Post-Install Inspection | QA Checklist | QA Checklist | QA Checklist | Application | QA Checklist | QA Checklist | Pre-Installation | QA Checklist | QA Checklist | QA Checklist | Post-Install Inspection | QA Checklist | Inspections | QA Checklist | QA Checklist | Inspections | Validation Checkpoint – when is data expected to be collected (Application, Inspection, QA Checklist) | EECP
Verification | Photograph of the nameplate showing the model number of the unit. | Photograph the equipment nameplate to capture the manufacturer. | Photograph the equipment nameplate to capture the serial number. | Photograph the equipment nameplate to capture the serial number. | Photograph the equipment identifier that uniquely identifies it at the site. | Trust Implementer response in application | Verify the building type is: - Education – University; - Health/Medical – Hospital; - Manufacturing – Biotech; or - Manufacturing – Pharmaceuticals | Use the submitted invoice or installation report to validate the equipment is new. | A detailed report from the implementer showing the baseline operating performance (tested data before and after) | Use the EnergyStar database and compare the listed manufacturer's make and model in application to the list | Use the EnergyStar database and compare the listed manufacturer's make and model in application to the list | Cross check manufacturer and model number with flow rate | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | Using the submitted manufacturer spec sheet, validate the Steam Mode Cooking Efficiency (%) | Photograph the equipment nameplate to capture the equipment thermal efficiency (%) | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | Use the manufacturer spec sheet to validate the Uniform Energy Factor | Photograph the nameplate of the HVAC Fan motor to capture the power rating, hp (if accessible and safe). | Validation Verification – What data should be used and how should data be used to validate this item | Trust Implementer response in EECP
Pass Criteria | The model number listed in application should match the model number listed on the photograph. | The listed manufacturer in the application should match the photograph. | The listed serial number in the application should match the photograph. | The listed serial number in the application should match the photograph. | The listed Equipment ID in the application should match the photograph. | Trust Implementer response in application | The building type must be: - Education – University; - Health/Medical – Hospital; - Manufacturing – Biotech; or - Manufacturing – Pharmaceuticals | The equipment should be listed as new, not used or rebuilt. | The existing conditions should show before data values indicating the fan was working | The database needs to have the make and model listed in application as being EnergyStar qualified; if not, criteria below must be met (https://www.energystar.gov/productfinder/product/certified-commercial-griddles/results) | The database needs to have the make and model listed in application as being EnergyStar qualified; if not, criteria below must be met (https://www.energystar.gov/productfinder/product/certified-commercial-griddles/results) | The flow rate of the installed unit must match the flow entered in application and be less than or equal to the flowrate required by the measure. | Note the unit difference: application requires tons, while capacity check required kBtu/hr. The listed capacity in application should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (Btu/hr) / 1,000 = kBtu/hr Capacity (tons) * 12 = kBtu/hr | The Steam Mode Cooking Efficiency (%) must be >= 41% | The value on the nameplate should match what is listed in Application | The Full Load Efficiency listed in application should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.497 kW/ton | The Uniform Energy Factor Must be >= 0.81 | Use the nameplate power rating (hp) to validate what is listed in application; the power rating must be <= 100 hp | Pass Criteria – statement of what passing data should look like | Trust Implementer response in EECP AHRI - Boiler, Commercial Link: https://www.ahridirectory.org/NewSearch?programId=30&searchTypeId=3
Alternative Validation Fields | [19 empty] | -
Alternate Checkpoint | QA Checklist | QA Checklist | Application | Application | Application |  | Post-Install Inspection | Application | Post-Install Inspection | Application | Application | Post-Install Inspection | QA Checklist | Application | QA Checklist | Application | Application | QA Checklist | Alternate Validation Checkpoint – when is data expected to be collected; only required if primary validation data is not available | -
Alternate Verification | Use the submitted invoice or installation report to validate the model number is listed. | Use the submitted invoice or installation report to validate the manufacturer is listed. | Trust Implementer response in application | Trust Implementer response in application | Trust Implementer response in application |  | During inspection verify building type | Trust Implementer response in application | Ask the customer if they are able to start the AC unit and observe the equipment (outdoor condenser and indoor vents) | Trust Implementer response in application | Trust Implementer response in application | Using a measuring cup or flow rate measuring device, fill the device for 6 seconds, record the amount of Oz of water in the device; gallons per minute can be calculated as: Measured Oz * 0.078125 = GPM | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | Trust Implementer response in application | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | Trust Implementer response in application | Trust Implementer response in application | Use photographs of the manufacturer spec sheet to validate the power rating (hp) of the fan motor | Alternate Validation Verification – how should data be used to validate this item | -
Alternate Pass Criteria | The model number listed in application should match the model number listed in the invoice or installation report. | The manufacturer listed in system should match the manufacturer listed in the invoice or installation report. | Trust Implementer response in application | Trust Implementer response in application | Trust Implementer response in application |  | The building type must be Education – University; Health/Medical – Hospital; Manufacturing – Biotech; or Manufacturing – Pharmaceuticals | Trust Implementer response in application | Check the HVAC system to see if it is energized and functional (operating without issues) (potentially add a third QA Checklist option) | Trust Implementer response in application | Trust Implementer response in application | The flow rate of the installed unit must match (or be lower than) the flow entered in application and be less than or equal to the flowrate required by the measure. | The listed capacity in application should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (Btu/hr) / 1,000 = kBtuh Capacity (tons) * 12 = kBtu/hr | Trust Implementer response in application | The Thermal Efficiency (%) listed in application should match the value listed in the specification sheet | Trust Implementer response in application | Trust Implementer response in application | The power rating of the fan motor must be <= 100 hp | Alternate Pass Criteria – statement of what passing data should look like
Additional Flags
Purpose Flag (Eligibility / EM&V / Categorization) | EM&V | EM&V | EM&V | EM&V | EM&V | EM&V | Categorization | Eligibility | Eligibility | Eligibility | Eligibility | Eligibility | EM&V | Eligibility | Eligibility | Eligibility | Eligibility | Eligibility | Data Use Category (Eligibility / EM&V) – choice on whether the data is used to determine eligibility (‘Eligibility’) or required as part of a data collection requirement (‘EM&V’) | Eligibility
Check Flag (Required / Recommended) | Required | Required | Required | Recommended | Required | Required | Required | Required | Required | Required | Required | Required | Required | Required | Required | Required | Required | Required | Check (Required / Recommended) – choice on whether data is 'Required’ since it is explicitly documented in the measure package or ‘Recommended’ | Required
Note on B1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Note that "E-5152" up/mid requirement, but any delivery type. Reply: Compare to Column E (SWHC012)
Note on D1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should there be items where the Application is the only check - ie, not also part of inspection process.
Note on E1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should there be items where the Application is the only check - ie, not also part of inspection process.
Note on G1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: We are likely to combine "Property-Installation-Control Type" and "Numeric Type". Concerns.
Note on H1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should Validation Criteria ever overlap with something that is captured in the permutation list?
Note on J1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should there be detail on how to document the answer to an inspection question?
Note on K1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: How should QPLs be integrated now and in the future? - Add a separate field? Reply: Would you need multiple links sometimes?
Note on L1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: How should QPLs be integrated now and in the future? - Add a separate field? Reply: Would you need multiple links sometimes?
Note on M1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Are AR requirements handled differently? Complex example of procedure for checking - could include a video? Reply: Potential rejection from AR may convert to NR.
Note on N1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Formulas: What does the format of the equation need to look like to integrate with PA systems? Can we consider removing "Validation Criteria"? Capacity: Be careful about units - many need several "Capacity" items.
Note on Q1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is there a better way to specify each efficiency level rather than one offering at a time?
Note on R1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is there a better way to specify each efficiency level rather than one offering at a time?
Note on A17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: (comment should provide advice on what the photo should be taken of to capture the model number) Depending on the measure, it should be clear that we are looking for exactly what equipment model we are looking for. For AR or AOE measures we may be wanting base/host equipment model info too.
Note on M19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should the range be from 1.2 to 1.5? Reply: What is the best/right way to represent this that will be understandable?