## Sheet1
Row Labels | Distinct Count of Workpaper ID
- | 1
Is the boiler used for space heating, domestic hot water, pools, or spas? | 1
Min Cooking Efficiency (%) | 1
4-ft LED Tube Type | 1
A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | 1
A map of the pump service area has been submitted? | 1
Additional QM measures (i.e. airflow adjustments) being installed in conjunction with this measure? | 1
After implementation air flow rate? (cfm/ton) | 3
AFUE % | 1
AFUE (%) | 1
AHRI certification number | 1
AHRI Reference Number | 11
All measures related to constant speed screw, constant speed centrifugal, and frictionless chillers are excluded due to the stringency of the tiers specified for the 2020 update of the Database of Energy Efficient Resources (DEER) and equipment availability in the market. | 1
Amount of refrigerant added or removed | 1
Annual Energy Use (kWh/yr) | 1
Annual Fuel Utilization Efficiency, AFUE (%) | 1
Any maintenance or repairs to economizer? If so, what was done? | 1
Are other Quality Maintenance (QM) measures (i.e. airflow adjustments) being installed with this measure? | 1
Are the display cases any of the following: specialty deli cases, custom coolers/freezers, and walk-in boxes with reach-in doors? | 1
Are the display cases served by a remote refrigeration system? | 1
Are the dryers on the site premise? | 1
Are the glass doors being installed on an existing vertical display case? | 1
Are the new motor and controls UL Listed? | 1
Are the refrigeration display case doors new? | 1
Are there any other throttling devices, such as inlet vanes or bypass dampers, and throttling valves still operating? | 1
At least 1-in of insulation added to existing bare commercial or industrial steel or copper pipe? | 1
Automatic Conveyor Broilers Belt Width (in) | 1
Back-up generator size (kW) | 1
base case and measure case pool pumps? (hp) | 1
Base Case Measure Code | 3
Base Case Measure Description | 3
Before implementation condenser over ambient temperature (COAT) ? (degrees) | 3
Before implementation of the measure was an assessment and report created in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations? | 2
Before implementation of the measure was an assessment and report created in accordance with ACCA Standard 43 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations? | 1
Before installation of the measure was the existing backup generator fitted with a circulating block heater or device utilizing similar electro-mechanical system to heat and circulate generator block pre-warming fluid? | 1
Belt Type Installed | 1
Boiler used for space comfort (not domestic or process hot water)? | 1
Building has hot water recirculation system that can be turned OFF for a set period time? | 1
Building infrastructure costs (i.e. panel upgrades or gas installation/upgrades) | 3
Building is a fast food restaurant (RFF)? | 1
Building Type | 23
Building type is existing Agricultural facility (any vintage)? | 1
Building Type is Residential Multifamily? | 1
Building type one of the following: Asm, EPr, ERC, Gro, MLI, RFF, RSD, RtL, RtS, SCn, WRf? | 1
Building Vintage | 3
Building Vintage (construction year) | 1
CA Climate Zone | 20
Capacity (BTU/hr) | 1
Capacity (tons) | 2
Capacity of largest dryer (lbs) | 1
Capacity of largest washing machine (lbs) | 1
Cap-kBtuh | 2
Cap-Tons | 3
Chiller used for space conditioning, not for processes or industrial applications? | 1
Climate Zone | 1
Code Exemption for: Retrofitting < 10% in an enclosed space or <= 50 total per floor or tenant? | 1
Coefficient of Performance (COP) | 2
Combined Energy Efficiency Ratio (CEER) | 1
Combustion Efficiency (%) | 2
Compressor(s) control type | 1
Condenser Manufacturer | 2
Condenser Model | 2
Condenser Serial Number | 3
Contractor license number | 1
Contractor provided load calculations showing new unit is sized correctly for the load? | 2
Conveyer Width (in) | 1
Cooking Energy Rate (kW) | 1
Cooling Capacity (BTU/h) | 1
Cooling Capacity (kBtu/hr) | 3
Cooling Capacity (kBtuh) | 3
Cooling Capacity (tons) | 2
CRI | 2
Crossover duct insulation thermal resistance (R) | 1
Crossover duct location | 1
Customer existing baseline fuel type | 3
Customer has (or plans to have) existing, operational, and VSD compatible fixed speed fan? | 1
Customer has an active natural gas account? | 1
Data to be collected will include manufacturer and model numbers of controllers installed. Controller invoice amount and installation cost will be required to be collected to calibrate cost data. | 1
Date of Construction | 1
Date of installation or major upgrade to refrigeration multiplex system | 1
Design cooling load for connected display cases, walk-in coolers and freezers, cooled storage, and prep areas only (sub-coolers and air conditioning loads ineligible) (tons) | 1
Did both the customer and the installation contractor acknowledge the energy savings setting of the installed measure? | 1
Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | 1
Did equipment and materials meet or exceed all applicable local, state and federal standards? | 1
Did existing fans (not HVAC related) previously have VSD controls? | 1
Did the existing unit have the supply fan in automatic mode or switched OFF during unoccupied periods? | 1
Did the installation contractor follow all manufacturer installation requirements and comply with all applicable standards and regulations including (but not limited to) NEC and the California Title 24 and Title 20 regulations (see Code Requirements).? | 1
Did the installed heater replace an existing pool heater? | 1
Did the installed unit replace a conventional or always-on hand-wrap machine? | 1
Did the installed variable speed drive (VSD) pump replace an existing single- or two-speed pool pump? | 1
Did the Installer follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the circulating block heater to function at optimal energy efficiency? | 1
Did the pipes have existing pipe insulation ? | 1
Did the walk-in cooler or freezer have an existing automatic closer installed? | 1
Dishwasher type | 2
Display case equipped with humidity-sensing controls based on the store dew point temperature? | 1
Disposal method of tube | 2
Do the contractors and technicians that implement the measure meet all certification and training requirements in accordance with program requirements? | 1
Do the installed doors have low/no anti-sweat heat controls in conjunction with the installed controls? | 1
Do the low-temperature case door and frame heaters combined consume more than 50 W/ft of case length? | 1
Do the medium-temp cases have heat in the door (answer No if there is only heat in the door frame)? | 1
Do the retrofit doors have ASH controls installed? | 1
Documentation submitted showing VFD is not for backup pump? | 1
Does the customer already have a smart thermostat or fan delay controller installed? | 1
Does power reduction decrease by at least 2% for every percentage the humidity falls below 55%? | 1
Does premise have central air-cooled direct expansion (DX) cooling and gas heating? | 3
Does the automatic door closer firmly close the door when it is within one inch of full closure? | 1
Does the base design prescribe a pre-heating device other than a circulating block heater? | 1
Does the boiler installation comply with emission limits per air district, if applicable? (Note that Tier 2 hot water heaters are condensing and often require flue modifications to handle the condensate.) | 1
Does the boiler supply hot water to a circulation loop without an intermediary hot water storage tank? | 1
Does the chiller serve space conditioning equipment? | 1
Does the chiller serve space conditioning/comfort equipment? | 1
Does the control system use a Variable Speed Drive (VSD) on the fan motor? | 1
Does the dryer make use of a common dedicated steam system? | 1
Does the EER of the installed unit exceed code by at least 20%? | 1
Does the equipment type match the Measure Case Description (Air Conditioner or Heat Pump) and is not a ductless mini-split air conditioner? | 1
Does the existing dryer use natural gas? | 1
Does the existing refrigeration system have a multiplex compressor system with saturated condensing temperature (SCT) controls at a fixed setpoint? | 1
Does the existing wall furnace or fireplace insert have pilot light controls? | 1
Does the facility utilize natural gas water heating equipment? | 5
Does the facility utilize tankless water heaters? | 2
Does the faucet have an existing aerator installed? | 1
Does the freezer have an ENERGY STAR certification? | 1
Does the ice machine match the measure case equipment type? | 1
Does the installation comply with all applicable regulations, including but not limited to the current California Building Energy Efficiency Standards (Title 24), federal code, and the National Electrical Code® (NEC)? | 1
Does the installation comply with all applicable regulations? | 1
Does the installation comply with all current applicable regulations, code, and standards? | 1
Does the installation include the replacement of multiple-speed or variable speed motors (VSM)? | 1
Does the installed automatic conveyor broiler have a catalyst and an input rate less than 80 kBtu/hr or a dual stage or modulating gas valve with a capability of throttling the input rate below 80 kBtu/hr? | 1
Does the installed case include triple-pane doors with low or no anti-sweat heat or anti-sweat-heat controls? | 1
Does the installed cover have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard)? | 1
Does the installed device meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation? | 1
Does the installed heater have an ON/OFF switch and no pilot light? | 1
Does the installed timer device have seven-day (or better) scheduling capabilities? | 1
Does the installed unit have a remote refrigeration system? | 1
Does the installed unit only provide hot water when there is a hot water draw from the end use? | 1
Does the installed unit only provide hot water when there is a hot water draw from the end use? | 1
Does the installed unit use a mechanical or optical control system? | 1
Does the manufacturer describe the motor as a low-power or high efficiency model? | 1
Does the measure include addition of insulation to hot water and cold-water pipes within the first 3 feet of a storage water heater? | 1
Does the new saturated condensing temperature (SCT) setpoint adjust based on the ambient temperature by controlling condenser fans with variable-speed drives or by staging condenser fans? | 1
Does the nominal capacity of the new VSD pump match the capacity of the pump being replaced? | 1
Does the piping have existing insulation that is damaged or being replaced? | 1
Does the pool cover come with a minimum 5 year warranty? | 1
Does the pump serve a glycol loop? | 1
Does the replacement BFM motor capacity and rated voltage match that of the existing fan motor being replaced? | 1
Does the replacement BFM motor have a warranty of at least two years from date of installation? | 1
Does the shower have a wall-mounted diverter? | 1
Does the split system have a furnace in the AHRI certification that has already received a rebate? | 1
Does the submitted lamp specification sheet list the installed ballast model number showing it to be compatible with the installed lamp? | 1
Does the system include following? 1.An occupancy sensing thermostat 2. An occupancy sensor (wired or wireless) 3. Wiring (if wired) 4. Signal receiver and power pack (if wireless) | 1
Does the tank have existing insulation (in any condition) or evidence of prior insulation being installed ? | 1
Does the unit have a condenser over ambient temperature (COAT) of at least 3 degrees F? | 1
Does the water heater meet all Title 24 and Title 20 testing methods? | 1
Does this fixture/retrofit kit replace a lumen equivalent lamp/fixture of higher wattage? | 1
Does this project meet one of the Code Exemptions: Retrofitting < 10% of luminaires in an enclosed space or retrofitting <= 50 total luminaires per floor or tenant space? | 1
Domestic hot water loop temperature (F) | 1
Domestic hot water served by central system? | 1
Drum Capacity (lbs) | 1
Dual stage economizer: condensate meets sanitary and acidic neutralization of combustion codes? | 1
Duct sealant material | 1
Ductwork installed and tested in accordance with requirements in 2019 Title 24 Section 150.2(b)1D? | 1
Ductwork length > 40-ft been installed and tested in accordance to 2019 Title 24 Section 150.2(b)1D? | 1
During pool operating hours, was the VSD setting “right sized”? | 1
During start-up, system maintains programmed level airflows under both cooling and/or heating? | 1
Economizer efficiency / effectiveness (%) | 1
Economizer manufacturer | 1
Economizer model | 1
EER | 2
Efficacy, Lumens/Watt (LPW) | 1
Efficiency type used for equipment eligibility | 1
Eligible building types include residential single-family, double-wide mobile homes, and in-unit multifamily residences as well as multifamily common area laundry. | 1
End Use | 4
Energy Efficiency Rating (EER) | 1
Energy Efficiency Ratio (EER) | 1
Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | 1
Energy per Bun (W/bun) | 1
ENERGY STAR Certification | 1
ENERGY STAR Qualified | 2
ENERGY STAR Qualified? | 4
Energy Star unique ID | 2
EnergyStar Certification | 1
EnergyStar Connected Product | 1
Equipment Efficiency (EER) | 1
Equipment ID | 18
Equipment type | 1
Evaporator Manufacturer | 2
Evaporator Model | 2
Exhaust hood airflow (cfm) | 1
Existing air conditioning equipment type | 1
Existing ballast manufacturer | 1
Existing ballast model number | 1
Existing domestic hot water system had demand-controlled recirculation pump? | 1
Existing equipment manufacture date | 1
Existing equipment removed and disposed of rather than refurbished and sold? | 1
Existing Equipment Type | 2
Existing Equipment within +/- 5% of the replacement equipment Cooling Capacity (kBtuh)? | 2
Existing Faucet Flow Rate (gpm) | 1
Existing Flow Rate (gpm) | 4
Existing motor was fully functional with no sign of replacement in 12 months from project app. date? | 1
Existing packaged HVAC supply fan motor power (hp) | 1
Existing pump has means to vary the pressure or flow (i.e. throttle valve, control valve, etc.)? | 1
Existing RTU could adjust the changeover setpoint based on the number of thermostat cooling stages? | 1
Existing system can adjust to changeover setpoint based on thermostat stages available for cooling? | 1
Existing system has a constant volume supply fan? | 1
Existing system has operable economizer with high limit set per Title 24 2016 Table 140.4-B? | 1
Existing system is packaged single zone DX cooling w/ gas heat, cooling only, or heat pump? | 1
Existing water heater type | 3
Existing water heater was a storage tank style and disposed of (not retrofitted)? | 1
Facility sector | 1
Fan cfm/watt | 1
Fan flow rate (CFM) | 1
Fan motor type | 1
First Hour Rating (FHR) | 2
Fixture/retrofit kit listing in the Technical Requirements table (V5) on DLC under Classification | 1
Fixture/retrofit kit listing in the Technical Requirements table (V5) on DLC under Primary Use Designations? | 1
Flow Rate of Installed Unit (gpm) | 6
For hot water circulation loops, is there an intermediary hot water storage tank? | 1
For models that require an automatic control system capable of controlling both high and low speeds, was a controller installed? | 1
For NC, select the 'new services' condition | 1
Freezer Type | 1
Fryer Type | 1
Full Load Energy Efficiency (kW/ton) | 1
Full Load Energy Efficiency Rating (EER) | 1
Gas heating equipment type | 1
Gas Input Rating (Btu/hr) | 1
Greenhouse facility specialty | 2
Greenhouse is heated by natural gas (not propane)? | 2
Has a field inspection been performed to verify the condenser and if applicable evaporator make and model? | 1
Has a site Pre-Inspection been completed and documentation uploaded in EECP? | 1
Has all POE documentation been submitted as defined in the workpaper? | 1
Has all Preponderance of Evidence (POE) been presented including: Customer site information, Make/model of pre-existing equipment, Make/model of replacement equipment, Permits and associated documentation, and Pump commissioning information? | 1
Has all Preponderance of Evidence (POE) been included as defined in the workpaper? | 1
Has all Preponderance of Evidence (POE) been submitted as defined by the workpaper? | 2
Has all Preponderance of Evidence (POE) including existing system controls functionality with replacements, reasons for retrofitting to LED, and future plans without incentives been documented and submitted? | 2
Has all the preponderance of evidence required by the measure package been uploaded in EECP? | 2
Has all the preponderance of evidence required by the workpaper been uploaded in EECP? | 2
Has Customer agreed to the QM Service Agreement? | 3
Has only one rebate been applied per spa or wading pool? | 1
Has only one variable-speed pool pump and motor been installed at the residence? | 1
Has photographic evidence or documentation of the test-in and test-out procedures been uploaded? | 1
Has real time monitoring been implemented to ensure proper operation of the system? | 1
Has required Preponderance of Evidence (POE) been submitted in accordance with the workpaper? | 1
Has the contractor performed condenser coil cleaning prior to installation of the pre-cooler system? | 1
Has the customer agreed not to modify and/or alter, in any way, programmed settings on the pump VSD to ensure persistence of the measure savings? | 1
Has the customer agreed to a post installation inspection? | 1
Has the customer confirmed the operation of the replacement equipment on the application form? | 1
Has the customer received less than or equal to the three maximum rebates per property/site for the main filtration pumps (includes pools, spas, and wading pools)? | 1
Has the customer, as part of the incentive application process, acknowledged that the replacement pool pump VSD has been configured to achieve energy savings and agreed to have the pump filtration settings programmed for reduced flow during pool non-operating hours? | 1
Has the existing equipment been properly disposed of and not abandoned in place? | 1
Has the lighting power density increased with a replacement or retrofit of the LED lighting systems in the display case? | 1
Has the manufacturer cut sheet been submitted? | 1
Has the manufacturer specification sheet been submitted to prove the equipment efficiency? | 1
Has this measure been combined with another refrigeration measure? | 1
Have all POE requirements spelled out in the workpaper been included in the program documentation? | 1
Have any improvements been made that would increase system energy use? | 1
Have existing conditions been recorded and measures are were NOT previously installed? | 1
Have POE requirements in the measure package been included in uploaded documentation? | 2
Have the filtration settings been configured to operate outside peak hours, as defined by the utility? | 1
Have the fixtures been delamped? | 2
Heat curtain gas savings rating (%) | 1
Heat Pump Manufacturer | 1
Heat Pump Model | 1
Heat pump water heater storage capacity (gallons) | 1
Heat used to preheat service hot water (not domestic hot water)? | 1
Heating Seasonal Performance Factor (HSPF) | 4
Heating System Capacity (kBtuh) | 1
Heavy Load Cooking Efficiency (%) | 1
Holding cabinet fully insulated (i.e., on all sides) and has solid or transparent doors? | 1
Host equipment type? | 1
Hot water is central, gas-fired, constant-flow, fractional horsepower, uncontrolled recirc pump? | 1
Hours of operation of the hot water system | 1
How much of the pool does the new pool cover encompass? (%) | 1
HP | 1
HPWH First Hour Rating (FHR) | 1
HPWH Manufacturer | 1
HPWH Model | 1
HPWH Storage Capacity (gallons) | 1
HVAC System Cooling Capacity (tons) | 1
HVAC type is a packaged VAV with gas furnace (cPVVG)? | 1
Ice making system type | 1
Idle Energy Rate (Btu/Hr) | 2
Idle Energy Rate (kW) | 2
Idle Energy Rate (watts) | 1
IEER | 2
If customer chose Accelerated Replacement, have written/photographic records disposal been provided? | 1
If humidity is not monitored, ASH controls turn off based on the condensation formed on inner glass? | 1
If installed in a conditioned space, existing space heating fuel type | 1
If not a glycol loop, do the unit energy savings exceed the measure case savings? | 1
If site had electrification measures, have itemized infrastructure costs invoices been submitted? | 1
If site required electric infrastructure upgrades, have itemized invoices with costs been submitted? | 1
If the pool is Olympic sized, is there a storage reel system? | 1
If UL Type A + B Configuration, was the existing ballast removed? | 1
IMC | 1
In the installed insulation required by California Building Energy Efficiency Standards (Title 24) or employee safety laws (Occupational Safety and Health Administration, OSHA)? | 1
Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | 1
Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | 1
Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | 1
Input Capacity (BTU/hr) | 1
Input Rating (btu/hr/gallon of stored water) | 2
Input Rating (btu/hr/gallon) | 1
Input rating (HP) | 1
Input rating (kBtu/hr) | 2
Installation complies with all policies, codes and regulations within the site territory? | 1
Installation contractor | 1
Installation date of existing hood | 1
Installation includes temperature sensor(s) and/or an optic sensor to adjust fan speeds? | 1
Installation is part of a new service defined in Fuel Substitution Technical Guidance for EE? | 1
Installation meets latest NFPA Code 110 for Emergency Power Systems and NEC installation guidelines? | 1
Installed an electronically commutated motor (ECM) or permanent magnet synchronous (PMS) motor/fan? | 1
Installed broiler has an input rate <= 22 kBtu/hr/len-ft with a surface temperature of 600 °F? | 1
Installed in a commercial domestic (or “service”) hot water application in a NonRes facility? | 1
Installed in a NAICS code 31, 31, or 33? | 1
Installed to a functional HVAC unit with cooling/evaporator (dx) coils? | 1
Insulated Holding Cabinet Size (square feet) | 1
Insulation is being installed on bare suction pipes for medium temperature, walk-in coolers | 1
Insulation manufacturer specification sheet submitted with the application? | 1
Insulation material k-value rating | 1
Insulation material type | 1
Integrated Energy Efficiency Ratio (IEER) | 1
Integrated Modified Energy Factor (IMEF) | 1
Integrated Part Load Value (IPLV) | 2
Integrated Part Load Value (kW/ton) | 1
Integrated pilot light controls are capable of using a battery or voltage line to operate? | 1
Integrated Water Factor (IWF) | 1
IR Film only installed on the roof (not on the walls)? | 1
Is a natural gas-fired boiler or water heater supplying hot water to the laundry equipment? | 1
Is a water treatment system used with the evaporative pre-cooler system? | 1
Is an existing, open, multi-deck display case being replaced with a new reach-in unit with doors, electronically commutated motor (ECM) evaporator fan(s), and LED lighting? | 1
Is Equipment Gas or Electric? | 2
Is new equipment/hardware being installed (i.e. not reprogramming an existing controller)? | 1
Is the ballast existing and an electronic instant start type? | 1
Is the base case broiler a similar size or larger than the replacement unit? | 1
Is the baseline air conditioning system equipped with a hardware based built-in delay controller? | 1
Is the building an existing commercial building? | 1
Is the building type: commercial facilities, such as schools, colleges, universities, YMCA/YWCA, public facilities, hotels/motels, health clubs, and spas. This measure is also applicable for multifamily properties, such as homeowner associations and other multifamily complexes? | 1
Is the case temperature above 32F? | 1
Is the case temperature below 32F? | 1
Is the device installed in a health care facility subject to the OSHPD code and regulation/inspection requirements? | 1
Is the equipment a ductless mini-split air conditioner? | 1
Is the equipment new (not used or rebuilt)? | 12
Is the existing belt a cogged V-belt? | 1
Is the existing building considered a Health Care facility as defined by OSHPD? | 1
Is the existing conveyor broiler being replaced by a conveyor broiler similar in size or smaller? | 1
Is the existing faucet served by a natural gas fired water heater in an existing building? | 1
Is the existing unit a low temp coffin with a display width greater than 3 feet? | 1
Is the existing unit a standard efficiency unit of the same configuration and capacity? | 1
Is the existing wall furnace or fireplace insert in working condition (not requiring major repairs)? | 1
Is the facility: • Hospitals (large regional or local) • Emergency rooms • In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals • Doctor offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.) • Clinics and nursing homes | 1
Is the fan controller used for solely optimizing and improving heating efficiency including those for gas furnaces? | 1
Is the fan/blower a designed high-pressure blower (design capacity <= 150 cfm/hp)? | 1
Is the griddle double-sided? | 1
Is the hot water boiler used for space conditioning, industrial (process) end-use applications, pools, or spas? | 1
Is the hot water for the installed commercial-grade PRSV supplied from natural gas water heaters? | 1
Is the HVAC system functional/operable and drawing power? | 1
Is the HVAC type a DX Heat Pump (cDXHP) and the building a refrigerated warehouse (WRf)? | 1
Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | 1
Is the installed equipment a residential-style electric storage water heater? | 1
Is the installed equipment rented or leased? | 1
Is the installed holding cabinet listed on the Food Service Technology Center (FSTC) qualified product list (https://fishnick.com/saveenergy/rebates/)? | 1
Is the installed LFR served by natural gas water heating equipment? | 1
Is the installed product certified by International Association of Plumbing and Mechanical Officials (IAPMO)? | 1
Is the installed smart thermostat in full compliance with the ENERGYSTAR Program Requirements and Product Specification for Connected Thermostats Products Version 1.0 or later? | 1
Is the installed unit a reach-in case that is "1/4" of the total length of the coffin or less? | 1
Is the installed unit an on-demand hand-wrap machine? | 1
Is the insulation for exposed hot-water tanks within seven feet of the floor that are not otherwise guarded in such manner as to prevent contact? | 1
Is the insulation required to prevent burns or is the tank located where burns can be sustained? | 1
Is the insulation R-values of the installed insulation greater than or equal to R-3.2? | 1
Is the insulation R-values of the installed insulation greater than or equal to R-4.3? | 1
Is the lamp listed on the most recent version of the DesignLights Consortium (DLC) list? | 2
Is the LFR labeled as “Vandal Proof” or can not be removed without a proprietary tool, except for dialysis and scrub sink locations? | 1
Is the max flow/capacity of the modulating valve greater than or equal to that of the dryer? | 1
Is the measure a one-for-one pump replacement? | 1
Is the measure an HVAC (evaporator) fan motor with nominal capacity of ½-hp (or less) typically serving HVAC systems with nominal capacities of 3.5 ton (or less)? | 1
Is the measure replacing a shaded pole or permanent split capacitor (PSC) motor with a brushless direct current motor with selectable speed control? | 1
Is the motor installed on a refrigerated display case? | 1
Is the new case length less than or equal to the original case length? | 1
Is the new lighting compatible with the existing lighting controls type (i.e. dimming controls with dimmable LED)? | 1
Is the new motor closely matched to the original motor's speed and shaft output power? | 1
Is the Ozone system installed on a laundry system equipped with a tunnel washer? | 1
Is the ozone transfer into the water via venturi injection or bubble diffusion? | 1
Is the pool heated with natural gas? | 1
Is the pre-existing condition bare suction pipe on a low-temperature, walk-in freezer? | 1
Is the primary target building type for this measure an existing schools/colleges (educational institutions), city (municipal) recreational centers, home owner associations (e.g., condominiums with common pools), private/health clubs, and multifamily residences (apartment buildings)? | 1
Is the pump a mixed flow pump with high volume and low head? | 1
Is the pump is used as a well pump to fill a reservoir or discharging into a canal? | 1
Is the replacement brushless fan motor (BFM) motor and motor controls assembly “UL Listed.”? | 1
Is the return duct in a conditioned space? | 1
Is the setpoint storage temperature range between -70 °C and -80 °C (-94 °F and -112 °F)? | 1
Is the showerhead is installed in tub/shower combination system? | 1
Is the tank that was insulated coupled to gas-fired commercial, industrial, or agriculture equipment that transfers heat to the contained liquid or solution? | 1
Is the TSV certified by applicable standards (e.g., ANSI, ASPE, etc.) ? | 1
Is the unit an air cooled ice maker? | 1
Is the unit being installed in a newly constructed buildings, additions to existing buildings, and alterations to existing buildings? | 1
Is the unit drawing power? | 1
Is the unit operational? | 3
Is the VFD being installed on an existing HVAC supply or return air system | 1
Is the VFD being installed on cooling tower fans? | 1
Is there an existing pool cover in use? | 1
Is this a cook-and-hold retherm equipment? | 1
Is this a Heat Pump clothes dryer? | 1
Is this an electric resistance, passive, or cook-and-hold retherm equipment? | 1
Is this measure being installed on a new construction project? | 1
Is this measure for an HVAC fan? | 1
Itemized invoices submitted with upgrade costs for additional electrification measures? | 3
Kelvin Correlated Color Temperature (CCT) | 3
L70 Lumen Maintenance Hours | 2
L90 Lumen Maintenance Hours | 1
Labor cost for replacement motor | 2
Large-scale remodels are defined as any project involving 50% of the linear feet of refrigerated casework or 32 linear feet of casework replacements, whichever is less. Are the display case replacements part of large-scale store remodels? | 1
Lease term 5-years (not annual renewal) and copy of lease agreement uploaded | 1
LED Tube Type | 1
Length of ductwork replaced (linear feet) | 1
Length of piping in linear feet | 1
List other electrification measures installed | 3
List other electrification measures installed with the heat pump water heater | 1
Location | 4
Lumens | 1
Make | 3
Manufacturer | 93
Manufacturer date of walk-in cooler? | 1
Manufacturer date of walk-in freezer? | 1
Manufacturer specification sheet submitted with the application? | 1
Market Cost | 2
Material cost for replacement motor | 2
Max Daily Potable Water Use Limit (gal/100 lbs. ice) | 1
Max Idle Energy Rate (Btu/h) | 1
Max Idle Energy Rate (Btu/hr) | 2
Max Idle Energy Rate (kW) | 2
Max Idle Energy Rate (W) | 1
Max Idle Energy Rate (W/ft2/hr) | 1
Max Idle Energy Rate (watts/ft3) | 1
Max washing energy (kWh/rack) | 2
Max. Estimated Annual Energy Use (kWh/yr) | 1
Max. Water Consumption (gallons/cycle) | 1
Maximum daily energy consumption(MDEC) (kWh/day/ft3) | 1
Maximum Daily Energy Use (kWh/100 lbs. ice) | 1
Maximum Water Consumption (Gallons per Rack) | 1
Measure combined with evaporative fan controller for walk-in coolers and/or freezers? | 1
Measure installed in conjunction with floating head pressure controls? | 1
Measure installed on a newly constructed, additions or alterations to an existing building? | 1
Measure is installed for wine processing? | 1
Measure Size Category | 9
Min. Cooking Energy Efficiency (%) | 5
Minimum HVAC delivery air flow rate (cfm/ton) | 1
Minimum Warranty | 2
Model | 95
Model Number | 1
Modified Energy Factor J2 (MEF) | 1
Motor Manufacturer | 1
Motor Model | 1
Natural gas must be supplied by a California utility. | 1
New Construction | 2
New Equipment | 10
New Faucet Flow Rate (gpm) | 1
New gravity wall furnace is replacing an existing gravity wall furnace? | 1
Nominal Capacity (tons) | 1
Number of Guest Rooms | 1
OA Reset Control (F) | 1
Only eligible for Single Family Homes, did the customer perform self-installation of the new pump? | 1
Oven Mode Cooking Efficiency (%) | 1
Oven Mode Idle Energy Rate (Btu/hr) | 1
Oven Mode Idle Energy Rate (watts) | 1
Oven Production Capacity (lbs/hr) | 1
Oven Size | 2
PA shall confirm that the customer has a newly purchased smart thermostat. At minimum, the PA shall obtain a copy of the thermostat sales receipt and the PA shall confirm the purchase date is on or after the program start date. | 1
Pan Capacity | 1
Percent OA verified for heating and cooling for each stage as well as ventilation only mode? | 1
Percent of refrigerant added or removed | 1
Photograph of existing heating equipment submitted? | 1
Photograph of open belly return duct submitted? | 1
Photograph showing deterioration, damage, or poor installation of crossover duct submitted? | 1
Photograph(s) of existing cooling and heating equipment submitted? | 3
Pipe Diameter (in) | 1
Post leakage rate (%) | 1
Power Factor | 2
Pre leakage rate (%) | 1
Pre-Existing Conditions: Automated controls type in retrofitted spaces | 1
Pre-Existing Conditions: Fluorescent Lamp Wattage (W) | 2
Pre-Existing Conditions: Number of Ballasts per Fixture | 1
Pre-Existing Conditions: Number of Fixtures Sampled | 2
Pre-Existing Conditions: Number of Lamps per Fixture | 2
Pre-Existing Conditions: Percent of Fixtures Sampled | 1
Pre-Existing Conditions: Total number of fixtures on site | 2
Preheat Energy (Btu/hr) | 1
Preheat Energy (watts) | 1
Preheat Energy Rate (kW) | 1
Preheat Time (mins) | 1
Primarily used for domestic water? | 1
Primary Use Category | 2
Proc-lbs | 1
Product has a warranty >= 5 years | 1
Product qualification method? | 1
Production Capacity (lb/hr) | 1
Production Capacity (units/hr) | 1
Production Per Day (lbs) | 1
Proof of purchase submitted showing Integrated intermittent pilot light in the wall furnace? | 1
Proposed furnace is replacing an existing gas furnace? | 1
Pump annual hours of operation (hr/yr) | 1
Pump horsepower (hp) | 1
Pump type | 1
Purchase date of newly installed thermostat | 1
QM1: Is the HVAC system drawing power? | 1
QM2: For refrigerant charge adjustments, does the unit deliver supply air of at least 350 cfm/ton? | 1
QM3: Does the unit have a condenser over ambient temperature (COAT) of at least 3 degrees F? | 1
QM4: Has a report been submitted meeting ACCA Standard 4 prior to any treatments being applied? | 1
Quantity (sq ft) of heat curtain does not include overlap or exceed sq ft of the floor? | 1
R value (ft2-hr-F/Btu) | 1
Rated equipment capacity (kBtu/hr) | 1
Rated Input (Btuh) | 1
Rated-HP | 1
Refrigerant charge adjustments, unit has been tested to deliver supply air of at least 350 cfm/ton? | 1
Refrigerant successfully applied and meets manufacturer recommended levels | 3
Refrigerant Type | 3
Refrigeration Multiplex System | 1
Refrigeration suction pipe diameter on existing equipment in inches | 1
Replacement duct material | 1
Replacement fixture/retrofit kit on the most recent version of the DLC qualified product list? | 1
Replacement like-for-like (i.e. air conditioner for an air conditioner or heat pump for heat pump)? | 2
Replacement motor efficiency (%) | 1
Replacement motor size (W) | 2
Replacing gas unit with gas unit? | 3
Report been submitted in accordance with ACCA Standard 4 prior to any treatments being applied? | 1
Required NC document(s) submitted as outlined in the measure package? | 1
Retail Price | 13
Retailor or distributor zip code | 2
Return duct insulation thermal resistance (R) | 1
Seasonal Energy Efficiency Ratio (SEER) | 1
Seasonal Energy Efficiency Ratio (SEER) value | 1
SEER | 3
Select the most appropriate building vintage | 1
Select the most appropriate Multiplex compressor system vintage | 1
Serial Number | 21
Site ID | 18
Size ( kBtu/hr) | 1
Size (Btu/hr) | 1
Size (gallons) | 1
Size (kBtu/hr) | 2
Size of Recirculation Pump Motor | 1
Sizing exemption for chillers > 300 tons | 1
Software used to control SRM | 1
Steam boiler input rating (MMBtu/hr) | 1
Steam boiler manufacturer | 1
Steam boiler model | 1
Steam boiler spec sheet submitted? | 1
Steam Mode Cooking Efficiency (%) | 1
Steam Mode Idle Energy Rate (Btu/hr) | 1
Steam Mode Idle Energy Rate (watts) | 1
Steam Pressure (psig) | 1
Steam Production Capacity (lbs/hr) | 1
Sticker Number | 1
Storage Capacity (gallons) | 2
System Efficacy, Lumens/Watt (LPW) as listed on DLC | 1
System Efficacy, Lumens/Watt (LPW) listed on DLC | 1
System is served by chilled water or serves domestic hot water? | 1
System Type | 2
System used for comfort/space cooling, not process or refrigeration loads? | 1
Temperature inside the tank (F) | 1
Test-in Duct Leakage Rate (%) | 1
Test-out Duct Leakage Rate (%) | 1
The greenhouse curtain must be a single layer plastic curtain | 1
The installation address must have a commercial natural gas account. | 1
The IR film must be infrared, anti-condensate, polyethylene plastic with a minimum thickness of six thousandths of an inch. | 1
The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. | 1
The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | 2
The PA shall confirm that the customer has a newly purchased smart thermostat. At minimum, the PA shall obtain a copy of the thermostat sales receipt and the PA shall confirm the purchase date is on or after the program start date. | 1
The PA shall determine customer eligibility prior to rebate payment. Upon request, all data associated with determining eligibility shall be provided to Energy Division of the California Public Utilities Commission (CPUC). All PAs shall extend this requirement to all third-party vendors that assist PAs with determining customer eligibility. To the extent that they are used to determine eligibility, data regarding dates of purchase, location of home, customer HVAC equipment type, pre-installation HVAC energy use, etc. shall be made available. | 1
The program administrator (PA) shall employ QA/QC procedures to ensure that the thermostat is installed in an eligible home and is attached to the type of HVAC equipment that is being incentivized, whether it is for natural gas or electricity savings. | 1
The purchase invoice must be provided as a proof that the wall furnace has been purchased to replace a previously existing unit. Additionally, the customer must agree to a post measure installation inspection. | 1
The submitted product specifications should match the measure description in EECP including the Tier, Size, Venting type, Fuel type, and Voltage (if fuel type is electric) | 1
Thermal Efficiency (%) | 3
Thermal efficiency of installed heater (%) | 1
This equipment must be installed by a qualified HVAC Contractor. Please verify the invoice and/or installation contract that verifies the equipment was installed by a qualified HVAC contractor has been submitted. | 1
This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | 1
This measure is not eligible when there is no natural gas to electricity fuel substitution for heating and/or when the measures include a non-regulated fuel. New construction measures are only eligible under certain conditions listed in the above section. Ground up constructions are not eligible. | 1
Total dryer capacity affected (lbs) | 1
Total Harmonic Distortion | 2
Total hp that can benefit from this measure above the max power rating offered by the measure (>3hp) | 1
Total unit airflow has been verified for at least one of the fan speeds? | 1
Total washing machine capacity (lbs) | 1
Type of fan controller installed? | 1
Type of insulation | 1
Type of insulation for hot water pipes installed | 1
Type of refrigerated display case the motor is being installed on | 1
Type of tank material (steel, fiberglass, etc.) | 1
Uniform Energy Factor | 2
Uniform Energy Factor (UEF) | 5
Unit has multi-speed indoor fan and gas furnace heating? | 1
Unoccupied supply fan operation already set to “Auto” or intermittent? | 1
Usage | 1
VFD installed on an existing constant speed pump motor? | 1
VFD is automated by pressure, fluid temperature, or flow rate feedback? | 1
VFD is installed on a pressurized irrigation system (no flood irrigation)? | 1
VFD is used for flow/pressure control, not for soft start or cavitation? | 1
VFD Manufacturer | 1
VFD Model | 1
Volume (cu. ft.) | 1
Volume less than 7.75 cu. ft. and Height < 36 inches | 1
Volume of freezer in cubic feet? | 1
Volume of reach-in unit (ft3) | 1
VSD controlled by static pressure, airflow, or duct velocity and meets IEEE 519-2014.2 requirements? | 1
VSD Manufacturer | 1
VSD Model | 1
VSD setting percentage during non-operating hours | 1
Wall furnaces that are direct-vent systems that mount on an outside wall are not eligible. | 1
Was a copy of the purchase receipt submitted? | 3
Was a design consultant used for major refrigeration system upgrades as a result of this measure? | 1
Was a High Efficiency Package Terminal Air Conditioner (Non Res) DX Unit installed? | 1
Was a medium-temperature, open, vertical refrigerated display case with a high efficiency evaporator coil installed? | 1
Was a minimum thickness of 1 inch of pipe insulation added to existing bare pipe? | 1
Was a new commercial-grade PRSV with a maximum flow rate = 0.75 gpm installed that replaced an existing PRSV with a maximum flow rate of 1.00 gpm for a spray force of < 5.0 ozf? | 1
Was a new commercial-grade PRSV with a maximum flow rate = 1.07 gpm installed that replaced an existing PRSV with a maximum flow rate of 1.20 gpm for a spray force of > 5.0 ozf and < 8.0 ozf? | 1
Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | 1
Was a pool pump installed in a spa or jacuzzi? | 1
Was a professional installer used to remove and reattach the gas line? | 1
Was add. tech verification of thermostat wiring and number of cooling stages that should be performed to ensure the 1st stage of cooling is dedicated to economizer operation and 2-stage thermostat operation is enabled performed if possible? | 1
Was an undercounter high temperature dishwasher installed (not another dishwasher types such as: conveyor, door-type, flight-type)? | 1
Was entire AHRI-tested ice making system purchased? | 1
Was field documentation of the existing conditions that verify the measure was necessary and that the measure was successfully applied submitted? | 1
Was the automatic door closer installed on the main insulated opaque door(s) of an existing walk-in cooler or freezer? | 1
Was the controller changeover setpoint adjusted appropriately based on the available number of thermostat cooling stages? | 1
Was the customer approached directly by a direct installation implementer? | 2
Was the equipment fully replaced (i.e. not a part swap or motor only replacement)? | 1
Was the existing broiler an automatic conveyor broiler than could maintain a temperature above 600 °F with a tested idle rate greater than 40 kBtu/hr for a belt narrower than 20 inches? | 1
Was the installation of the circulating block heater performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician)? | 1
Was the installation of the measure completed by a utility-approved contractor? | 2
Was the installed equipment new? | 1
Was the installed equipment won as a prize? | 1
Was the installed unit the same style as the existing case? | 1
Was the measure installed in a new construction application? | 1
Was the measure installed in an eligible home and attached to the type of HVAC equipment that is being incentivized? | 1
Was the measure installed on a main filtration pump? | 1
Was the measure installed where recirculation pumps are used or where potential crossover between hot water and cold water may occur? | 1
Was the motor installed to replace a supply fan (not a return fan or outdoor air fan) of a packaged HVAC unit? | 1
Was the pump being replaced disposed of rather than refurbished and/or sold? | 1
Was the VSD pump configured to meet program pump configuration requirements? | 1
Was third-party baseline verification and data gathering in full compliance with the established POE requirements performed? | 1
Was this measure installed on a new faucet that met or exceeded the 2016 California Appliance Efficiency Regulations (Title 20) code requirement of 1.2 gpm flow rate for lavatory faucet and 1.8 gpm flow rate for kitchen faucet? | 1
Water consumption of dishwasher in gallons per rack | 1
Water Consumption Rate (gal/hr) | 1
Water heater fuel type | 1
Water heater is primarily used for domestic hot water, not for space conditioning, pools or spas? | 1
Water heater meet all emissions requirements as outlined by local air quality management districts? | 1
Wattage | 1
Were all health code requirements and inspections passed successfully? | 1
What is area in square footage of the pool area | 1
What is the assumed baseline fuel type? | 1
What is the fixture Color Rendering Index (CRI)? | 1
What type of HVAC system does the customer have? | 1
When was the walk-in installed in the building? | 1
Where is the tank located? | 1
Who was the party that filled out the POE documentation? | 6
Zip Code | 20
Grand Total | 104

## SDG&E Data
Color Control | Workpaper ID | Revision # | WP Name | WP Offering ID | MeasAppType | DeliveryType | System of Record | Sort Order | Source Record (Item from Workpaper requiring Property) | Property Enabled | Property Name | Property - Label | Property - Installation - Control Type | Property - Installation - Values - Custom | Validation criteria | Validation Correct Answer | Numeric Type | Min Value | Max Value | Decimal Places | ValidationRule | Validation Checkpoint | Validation Verification | Pass Criteria | Alternate Validation Checkpoint | Alternate Validation Verification | Alternate Pass Criteria | QC and Notes for CPSS | Finalized Date | Sign Off | Comment | Mgmt. Comment | Property Label Len
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Any | Any | Any | EECP | 0 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 12
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Any | Any | Any | EECP | 0 | Eligible building types include any residential single family, multifamily, and residential double-wide mobile homes. | Yes |  | Building Type | Drop Down List | Residential single family;Multifamily;Double-wide mobile home; | [7 empty] | Inspections | Document the type of residence the unit was installed in (Single Family Home, Multifamily, or Mobile Home) | The building type listed in EECP should match the building type during the inspection | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 13
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Any | Any | Any | EECP | 5 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 5
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Any | Any | Any | EECP | 10 | The product eligibility requirements for the ENERGY STAR and ENERGY STAR Most Efficient tiers are provided below. See Measure Case Description for a full list of refrigerator model specifications. Must be on the ENERGY STAR qualifying list. | Yes |  | ENERGY STAR Certification | Drop Down List | Yes;No |  | Yes |  |  |  |  | Must be Yes | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being EnergyStar certified | The make and model from EECP should be present on the EnergyStar database as being a certified product | Inspections | Photograph the EnergyStar label on the unit | The EnergyStar label should be locatable on the unit or within the nameplate | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 25
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | A | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | B | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | C | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | D | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | E | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | F | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | G | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | H | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | I | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | J | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | K | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | L | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | M | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | N | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | O | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | P | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Q | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | R | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | S | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | T | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | U | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | V | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | W | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | X | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Y | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Z | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AA | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AB | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AC | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AD | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AE | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AF | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AG | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AH | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AI | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AJ | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AK | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AL | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AM | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AN | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AO | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AP | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AQ | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AR | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AS | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AT | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AU | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AV | Any | Any | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AW | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AX | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AY | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AZ | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BA | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BB | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BC | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BD | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BE | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BF | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BG | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BH | Any | Any | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | A | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Volume less than 7.75 cu. ft. and Height < 36 inches | Drop Down List | Yes;No; |  | Maybe just change to Numeric to capture volume, but then would have to add height… |  |  |  |  | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine the Volume (cu. ft.) and Height (in) for the make and model | The Volume (cu. ft.) listed on the EnergyStar database must be less than 7.75 cu. ft. The Height (in) listed on the EnergyStar database must be less than 36 inches | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 52
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | B | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | C | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Volume less than 7.75 cu. ft. and Height < 36 inches | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine the Volume (cu. ft.) and Height (in) for the make and model | The Volume (cu. ft.) listed on the EnergyStar database must be less than 7.75 cu. ft. The Height (in) listed on the EnergyStar database must be less than 36 inches | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 52
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | D | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Volume less than 7.75 cu. ft. and Height < 36 inches | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine the Volume (cu. ft.) and Height (in) for the make and model | The Volume (cu. ft.) listed on the EnergyStar database must be less than 7.75 cu. ft. The Height (in) listed on the EnergyStar database must be less than 36 inches | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 52
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | E | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | F | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | G | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | H | Any | Any | EECP | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Volume less than 7.75 cu. ft. and Height < 36 inches | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine the Volume (cu. ft.) and Height (in) for the make and model | The Volume (cu. ft.) listed on the EnergyStar database must be less than 7.75 cu. ft. The Height (in) listed on the EnergyStar database must be less than 36 inches | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 52
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | I | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | J | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | K | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | L | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | M | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | N | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | O | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | P | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Q | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | R | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | S | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | T | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | U | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | V | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | W | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | X | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Y | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Z | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AA | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AB | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AC | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AD | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AE | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AF | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AG | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AH | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AI | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AJ | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AK | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AL | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AM | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AN | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AO | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AP | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AQ | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AR | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AS | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AT | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AU | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AV | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AW | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AX | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AY | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AZ | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BA | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BB | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BC | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BD | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BE | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BF | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BG | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BH | Any | Any | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | A | Any | Any | QA Checklist | 25 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | C | Any | Any | QA Checklist | 25 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | D | Any | Any | QA Checklist | 25 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | H | Any | Any | QA Checklist | 25 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
0 | SWAP003 | 2 | Clothes Dryer, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 12
0 | SWAP003 | 2 | Clothes Dryer, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 5
0 | SWAP003 | 2 | Clothes Dryer, Residential | Any | Any | Any | EECP | 3 | Eligible building types include any new or existing residential building, including single family, multifamily units, and double-wide mobile homes. | Yes |  | Building Type | Drop Down List | Residential single family;Multifamily;Double-wide mobile home; | [7 empty] | Inspections | Document the type of residence the unit was installed in (Single Family Home, Multifamily, or Mobile Home) | The building type listed in EECP should match the building type during the inspection | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 13
0 | SWAP003 | 2 | Clothes Dryer, Residential | H | Any | Any | EECP | 4 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
0 | SWAP003 | 2 | Clothes Dryer, Residential | I | Any | Any | EECP | 5 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
0 | SWAP003 | 2 | Clothes Dryer, Residential | J | Any | Any | EECP | 6 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
0 | SWAP003 | 2 | Clothes Dryer, Residential | K | Any | Any | EECP | 7 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
0 | SWAP003 | 2 | Clothes Dryer, Residential | L | Any | Any | EECP | 8 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
0 | SWAP003 | 2 | Clothes Dryer, Residential | M | Any | Any | EECP | 9 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
0 | SWAP003 | 2 | Clothes Dryer, Residential | Any | Any | Any | QA Checklist | 10 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) and ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. | Yes |  | The submitted product specifications should match the measure description in EECP including the Tier, Size, Venting type, Fuel type, and Voltage (if fuel type is electric) | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being EnergyStar certified | If the product is deemed certified, verify the product falls within the measure case description (i.e. the Tier, Size, Venting type, Fuel type, and Voltage (if fuel type is electric) should all align between EnergyStar and EECP) | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-08-04 | Kenny Liljestrom |  | Add | 171
1 | SWAP003 | 3 | Clothes Dryer, Residential | Any | Any | Any | EECP | 0 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 12
1 | SWAP003 | 3 | Clothes Dryer, Residential | Any | Any | Any | EECP | 0 | Eligible building types include any new or existing residential building, including single family, multifamily units, and double-wide mobile homes. | Yes |  | Building Type | Drop Down List | Residential single family;Multifamily;Double-wide mobile home; | [7 empty] | Inspections | Document the type of residence the unit was installed in (Single Family Home, Multifamily, or Mobile Home) | The building type listed in EECP should match the building type during the inspection | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 13
1 | SWAP003 | 3 | Clothes Dryer, Residential | Any | Any | Any | EECP | 5 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 5
1 | SWAP003 | 3 | Clothes Dryer, Residential | H | Any | Any | EECP | 10 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; |  | Yes |  |  |  |  | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
1 | SWAP003 | 3 | Clothes Dryer, Residential | I | Any | Any | EECP | 10 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; |  | Yes |  |  |  |  | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
1 | SWAP003 | 3 | Clothes Dryer, Residential | J | Any | Any | EECP | 10 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; |  | Yes |  |  |  |  | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
1 | SWAP003 | 3 | Clothes Dryer, Residential | K | Any | Any | EECP | 10 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; |  | Yes |  |  |  |  | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
1 | SWAP003 | 3 | Clothes Dryer, Residential | L | Any | Any | EECP | 10 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; |  | Yes |  |  |  |  | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
1 | SWAP003 | 3 | Clothes Dryer, Residential | M | Any | Any | EECP | 10 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; |  | Yes |  |  |  |  | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
1 | SWAP003 | 3 | Clothes Dryer, Residential | Any | Any | Any | QA Checklist | 205 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) and ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. | Yes |  | The submitted product specifications should match the measure description in EECP including the Tier, Size, Venting type, Fuel type, and Voltage (if fuel type is electric) | Text Box | [8 empty] | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being EnergyStar certified | If the product is deemed certified, verify the product falls within the measure case description (i.e. the Tier, Size, Venting type, Fuel type, and Voltage (if fuel type is electric) should all align between EnergyStar and EECP) | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-08-04 | Kenny Liljestrom |  | Add | 171
0 | SWAP004 | 2 | Clothes Washer, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 12
0 | SWAP004 | 2 | Clothes Washer, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 5
0 | SWAP004 | 2 | Clothes Washer, Residential | Any | Any | Any | EECP | 3 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | EnergyStar Certification | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being EnergyStar certified | The make and model from EECP should be present on the EnergyStar database as being a certified product | Inspections | Photograph the EnergyStar label on the unit | The EnergyStar label should be locatable on the unit or within the nameplate | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 24
0 | SWAP004 | 2 | Clothes Washer, Residential | Any | Any | Any | EECP | 4 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | EnergyStar Connected Product | Drop Down List | Yes;No | [7 empty] | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being EnergyStar Connected (i.e. capable of reporting energy usage) | The make and model from EECP should be present on the EnergyStar database as being an EnergyStar Connected product | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 28
0 | SWAP004 | 2 | Clothes Washer, Residential | A | Any | Any | EECP | 5 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Volume (cu. ft.) | Numeric Value | [7 empty] | Must be > 2.5 and <= 6.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 2.5 and <= 6.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | A | Any | Any | EECP | 6 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Integrated Modified Energy Factor (IMEF) | Numeric Value | [7 empty] | If 'EnergyStar Connected Product' is Yes then must be >= 2.76 If 'EnergyStar Connected Product' is No then must be >= 2.62 | QA Checklist | Use the EnergyStar database to determine the Integrated Modified Energy Factor (IMEF) of the Washing Machine | The Integrated Modified Energy Factor (IMEF) must be listed on EnergyStar as >= 2.76 If the product is an EnergyStar Connected unit, the Integrated Modified Energy Factor (IMEF) must be >= 2.62 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 40
0 | SWAP004 | 2 | Clothes Washer, Residential | A | Any | Any | EECP | 7 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [7 empty] | Must be <= 3.2 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 3.2 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | B | Any | Any | EECP | 8 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Volume (cu. ft.) | Numeric Value | [7 empty] | Must be > 2.5 and <= 6.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 2.5 and <= 6.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | B | Any | Any | EECP | 9 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Integrated Modified Energy Factor (IMEF) | Numeric Value | [7 empty] | If 'EnergyStar Connected Product' is Yes then must be >= 2.76 If 'EnergyStar Connected Product' is No then must be >= 2.62 | QA Checklist | Use the EnergyStar database to determine the Integrated Modified Energy Factor (IMEF) of the Washing Machine | The Integrated Modified Energy Factor (IMEF) must be listed on EnergyStar as >= 2.76 If the product is an EnergyStar Connected unit, the Integrated Modified Energy Factor (IMEF) must be >= 2.62 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 40
0 | SWAP004 | 2 | Clothes Washer, Residential | B | Any | Any | EECP | 10 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [7 empty] | Must be <= 3.2 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 3.2 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | G | Any | Any | EECP | 11 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Volume (cu. ft.) | Numeric Value | [7 empty] | Must be > 2.5 and <= 6.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 2.5 and <= 6.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | G | Any | Any | EECP | 12 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Integrated Modified Energy Factor (IMEF) | Numeric Value | [7 empty] | If 'EnergyStar Connected Product' is Yes then must be >= 2.06 If 'EnergyStar Connected Product' is No then must be >= 1.96 | QA Checklist | Use the EnergyStar database to determine the Integrated Modified Energy Factor (IMEF) of the Washing Machine | The Integrated Modified Energy Factor (IMEF) must be listed on EnergyStar as >= 2.06 If the product is an EnergyStar Connected unit, the Integrated Modified Energy Factor (IMEF) must be >= 1.96 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 40
0 | SWAP004 | 2 | Clothes Washer, Residential | G | Any | Any | EECP | 13 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [7 empty] | Must be <= 4.3 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 4.3 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | H | Any | Any | EECP | 14 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Volume (cu. ft.) | Numeric Value | [7 empty] | Must be > 2.5 and <= 6.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 2.5 and <= 6.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | H | Any | Any | EECP | 15 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Integrated Modified Energy Factor (IMEF) | Numeric Value | [7 empty] | If 'EnergyStar Connected Product' is Yes then must be >= 2.06 If 'EnergyStar Connected Product' is No then must be >= 1.96 | QA Checklist | Use the EnergyStar database to determine the Integrated Modified Energy Factor (IMEF) of the Washing Machine | The Integrated Modified Energy Factor (IMEF) must be listed on EnergyStar as >= 2.06 If the product is an EnergyStar Connected unit, the Integrated Modified Energy Factor (IMEF) must be >= 1.96 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 40
0 | SWAP004 | 2 | Clothes Washer, Residential | H | Any | Any | EECP | 16 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [7 empty] | Must be <= 4.3 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 4.3 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | C | Any | Any | EECP | 17 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Volume (cu. ft.) | Numeric Value | [7 empty] | Must be > 2.5 and <= 6.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 2.5 and <= 6.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | C | Any | Any | EECP | 18 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Integrated Modified Energy Factor (IMEF) | Numeric Value | [7 empty] | Must be >= 2.92 | QA Checklist | Use the EnergyStar database to determine the Integrated Modified Energy Factor (IMEF) of the Washing Machine | The Integrated Modified Energy Factor (IMEF) must be listed on EnergyStar as >= 2.92 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 40
0 | SWAP004 | 2 | Clothes Washer, Residential | C | Any | Any | EECP | 19 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [7 empty] | Must be <= 3.2 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 3.2 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | D | Any | Any | EECP | 20 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Volume (cu. ft.) | Numeric Value | [7 empty] | Must be > 2.5 and <= 6.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 2.5 and <= 6.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | D | Any | Any | EECP | 21 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Integrated Modified Energy Factor (IMEF) | Numeric Value | [7 empty] | Must be >= 2.92 | QA Checklist | Use the EnergyStar database to determine the Integrated Modified Energy Factor (IMEF) of the Washing Machine | The Integrated Modified Energy Factor (IMEF) must be listed on EnergyStar as >= 2.92 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 40
0 | SWAP004 | 2 | Clothes Washer, Residential | D | Any | Any | EECP | 22 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [7 empty] | Must be <= 3.2 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 3.2 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | I | Any | Any | EECP | 23 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Volume (cu. ft.) | Numeric Value | [7 empty] | Must be > 2.5 and <= 6.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 2.5 and <= 6.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | I | Any | Any | EECP | 24 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Integrated Modified Energy Factor (IMEF) | Numeric Value | [7 empty] | Must be >= 2.92 | QA Checklist | Use the EnergyStar database to determine the Integrated Modified Energy Factor (IMEF) of the Washing Machine | The Integrated Modified Energy Factor (IMEF) must be listed on EnergyStar as >= 2.92 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 40
0 | SWAP004 | 2 | Clothes Washer, Residential | I | Any | Any | EECP | 25 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [7 empty] | Must be <= 3.2 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 3.2 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | J | Any | Any | EECP | 26 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Volume (cu. ft.) | Numeric Value | [7 empty] | Must be > 2.5 and <= 6.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 2.5 and <= 6.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | J | Any | Any | EECP | 27 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Integrated Modified Energy Factor (IMEF) | Numeric Value | [7 empty] | Must be >= 2.92 | QA Checklist | Use the EnergyStar database to determine the Integrated Modified Energy Factor (IMEF) of the Washing Machine | The Integrated Modified Energy Factor (IMEF) must be listed on EnergyStar as >= 2.92 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 40
0 | SWAP004 | 2 | Clothes Washer, Residential | J | Any | Any | EECP | 28 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [7 empty] | Must be <= 3.2 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 3.2 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | E | Any | Any | EECP | 29 | ENERGY STAR Commercial Clothes Washer - Owned – Must be an ENERGY STAR-qualified commercial front-loading model. – The clothes container volume must be > 1.6 and < 8.0 cubic feet. – All models must have MEF J2 ≥ 2.2 and IWF ≤ 4.0 | Yes |  | Volume (cu. ft.) | Numeric Value | [7 empty] | Must be > 1.6 and < 8.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 1.6 and < 8.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | E | Any | Any | EECP | 30 | ENERGY STAR Commercial Clothes Washer - Owned – Must be an ENERGY STAR-qualified commercial front-loading model. – The clothes container volume must be > 1.6 and < 8.0 cubic feet. – All models must have MEF J2 ≥ 2.2 and IWF ≤ 4.0 | Yes |  | Modified Energy Factor J2 (MEF) | Numeric Value | [7 empty] | Must be >= 2.20 | QA Checklist | Use the EnergyStar database to determine the Modified Energy Factor J2 (MEF J2) of the Washing Machine | The Modified Energy Factor J2 (MEF J2) must be listed on EnergyStar as >= 2.20 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 31
0 | SWAP004 | 2 | Clothes Washer, Residential | E | Any | Any | EECP | 31 | ENERGY STAR Commercial Clothes Washer - Owned – Must be an ENERGY STAR-qualified commercial front-loading model. – The clothes container volume must be > 1.6 and < 8.0 cubic feet. – All models must have MEF J2 ≥ 2.2 and IWF ≤ 4.0 | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [7 empty] | Must be <= 4.0 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 4.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | F | Any | Any | EECP | 32 | ENERGY STAR Commercial Clothes Washer – Leased – Must be an ENERGY STAR-qualified commercial front-loading model. – The clothes container volume must be > 1.6 and < 8.0 cubic feet. – All models must have MEF J2 ≥ 2.2 and IWF ≤ 4.0 – Lease Term must be for a minimum term of 5 years and term cannot end prior to five years after the qualified measure is installed. Annual renewal leases do not qualify. | Yes |  | Volume (cu. ft.) | Numeric Value | [7 empty] | Must be > 1.6 and < 8.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 1.6 and < 8.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | F | Any | Any | EECP | 33 | ENERGY STAR Commercial Clothes Washer – Leased – Must be an ENERGY STAR-qualified commercial front-loading model. – The clothes container volume must be > 1.6 and < 8.0 cubic feet. – All models must have MEF J2 ≥ 2.2 and IWF ≤ 4.0 – Lease Term must be for a minimum term of 5 years and term cannot end prior to five years after the qualified measure is installed. Annual renewal leases do not qualify. | Yes |  | Modified Energy Factor J2 (MEF) | Numeric Value | [7 empty] | Must be >= 2.20 | QA Checklist | Use the EnergyStar database to determine the Modified Energy Factor J2 (MEF J2) of the Washing Machine | The Modified Energy Factor J2 (MEF J2) must be listed on EnergyStar as >= 2.20 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 31
0 | SWAP004 | 2 | Clothes Washer, Residential | F | Any | Any | EECP | 34 | ENERGY STAR Commercial Clothes Washer – Leased – Must be an ENERGY STAR-qualified commercial front-loading model. – The clothes container volume must be > 1.6 and < 8.0 cubic feet. – All models must have MEF J2 ≥ 2.2 and IWF ≤ 4.0 – Lease Term must be for a minimum term of 5 years and term cannot end prior to five years after the qualified measure is installed. Annual renewal leases do not qualify. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [7 empty] | Must be <= 4.0 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 4.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | F | Any | Any | EECP | 35 | ENERGY STAR Commercial Clothes Washer – Leased – Must be an ENERGY STAR-qualified commercial front-loading model. – The clothes container volume must be > 1.6 and < 8.0 cubic feet. – All models must have MEF J2 ≥ 2.2 and IWF ≤ 4.0 – Lease Term must be for a minimum term of 5 years and term cannot end prior to five years after the qualified measure is installed. Annual renewal leases do not qualify. | Yes |  | Lease term 5-years (not annual renewal) and copy of lease agreement uploaded | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | Implementer should provide a copy of the lease terms and conditions for review | The lease language must indicate: • A minimum of 5-years continuous • No annual renewal of lease | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 76
0 | SWAP004 | 2 | Clothes Washer, Residential | Any | Any | Any | QA Checklist | 36 | Eligible building types include residential single-family, double-wide mobile homes, and in-unit multifamily residences as well as multifamily common area laundry. | Yes |  | Eligible building types include residential single-family, double-wide mobile homes, and in-unit multifamily residences as well as multifamily common area laundry. | Text Box | [8 empty] | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP | Inspections | Document the type of residence the unit was installed in (Single Family Home, Multifamily, or Mobile Home) | The building type listed in EECP should match the building type during the inspection |  | 2021-08-04 | Kenny Liljestrom |  | Add | 163
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the Ozone equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-09 | Kenny Liljestrom |  | Add | 12
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the Ozone equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-09 | Kenny Liljestrom |  | Add | 5
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any | EECP | 3 | This measure is applicable for hotels/motels, health centers, nursing homes, and correctional facilities. | Yes |  | Building Type | Drop Down List | hotels/motels;health centers;nursing homes;correctional facility;other | [6 empty] | Must not be 'other' | QA Checklist | Use the building type from the EECP enrollment phase to determine if the project is eligible | The building type should only consist of: hotels/motels, health centers, nursing homes, or correctional facility | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 13
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any | EECP | 4 | Eligible ozone laundry products must meet the following requirements: • The washing capacity of each washing machine must be rated at 200 pounds or less. • The customer must have a natural gas-fired boiler or natural gas water heater that supplies hot water to the on-premise laundry (OPL) equipment. • The ozone laundry system(s) must be a new purchased product and installed with a new or existing commercial washing machine(s). • The ozone laundry system(s) must transfer ozone into the water with either the venture injection or bubble diffusion process. | Yes | Capacity | Capacity of largest washing machine (lbs) | Numeric Value | [7 empty] | Must be <= 200 | QA Checklist | Use the manufacturer specification sheets or inspection photos to validate the laundry capacity (lbs) of the largest washing machine connected to the Ozone system; the make and model can be used to locate a manufacturer specification sheet where the laundry capacity (lbs) should be listed | The capacity for EACH washing machine should be <= 200 lbs; the total capacity (combined) of all the washing machines does not have a limitation | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Updated Property label name to be more consistent with workpaper requirement | 2021-06-10 | Kenny Liljestrom |  | Add | 41
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any | EECP | 5 | Eligible ozone laundry products must meet the following requirements: • The washing capacity of each washing machine must be rated at 200 pounds or less. • The customer must have a natural gas-fired boiler or natural gas water heater that supplies hot water to the on-premise laundry (OPL) equipment. • The ozone laundry system(s) must be a new purchased product and installed with a new or existing commercial washing machine(s). • The ozone laundry system(s) must transfer ozone into the water with either the venture injection or bubble diffusion process. | Yes |  | Is a natural gas-fired boiler or water heater supplying hot water to the laundry equipment? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Locate and photograph the hot water heater supplying the on premise laundry washers; photograph the water heater nameplate to capture the make, model, and input rating (Btu/hr) or photograph the yellow gas piping fueling the water heater | Ensure the water heater previously serving or still connected to the washing machine is served by a natural gas fired water heater | QA Checklist | Use the submitted invoice or installation report to validate the make and model number of the on site water heater is listed and use those data to locate a manufacturer specification sheet | The manufacturer specification sheet should indicate the unit is a natural gas fired water heater | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 91
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any | EECP | 6 | - | Yes | LBS | Total washing machine capacity (lbs) | Numeric Value | [8 empty] | QA Checklist | Use the manufacturer specification sheets or inspection photos to validate the laundry capacity (lbs) of all on premise washing machines connected to the Ozone system; the make and model can be used to locate a manufacturer specification sheet where the laundry capacity (lbs) should be listed | The total capacity (combined) of all the washing machines does not have a limitation | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Revise property label to "Total washing machine capacity (lbs)" | 2021-06-10 | Kenny Liljestrom |  | Add | 36
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any | EECP | 7 | Eligible ozone laundry products must meet the following requirements: • The washing capacity of each washing machine must be rated at 200 pounds or less. • The customer must have a natural gas-fired boiler or natural gas water heater that supplies hot water to the on-premise laundry (OPL) equipment. • The ozone laundry system(s) must be a new purchased product and installed with a new or existing commercial washing machine(s). • The ozone laundry system(s) must transfer ozone into the water with either the venture injection or bubble diffusion process. | Yes | Market Cost | Market Cost | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | If this is a legacy property, do not include for this program and possibly remove if not configured for others | 2021-06-10 | Kenny Liljestrom |  | Add | 11
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any | EECP | 8 | - | Yes | Number of Guest Rooms | Number of Guest Rooms | Numeric Value | [8 empty] | Inspections | Ask the customer for the number of guest rooms at the facility | The value in EECP should be within 5% of the total number of guest rooms indicated by the customer | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | If this is a legacy property, do not include for this program and possibly remove if not configured for others | 2021-06-10 | Kenny Liljestrom |  | Add | 21
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any | EECP | 9 | - | Yes | Serial Number | Serial Number | Text Box | [8 empty] | Inspections | Photograph the Ozone equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Collect the equipment invoice for the product and/or installation report with the Ozone equipment serial number | The listed serial number in EECP should match the nameplate | If this is a legacy property, do not include for this program and possibly remove if not configured for others | 2021-06-10 | Kenny Liljestrom |  | Add | 13
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any | EECP | 10 | Eligible ozone laundry products must meet the following requirements: • The washing capacity of each washing machine must be rated at 200 pounds or less. • The customer must have a natural gas-fired boiler or natural gas water heater that supplies hot water to the on-premise laundry (OPL) equipment. • The ozone laundry system(s) must be a new purchased product and installed with a new or existing commercial washing machine(s). • The ozone laundry system(s) must transfer ozone into the water with either the venture injection or bubble diffusion process. | Yes | Size | Proc-lbs | Numeric Value | [7 empty] | Must be <= 200 lbs | QA Checklist | Use the manufacturer specification sheets or inspection photos to validate the laundry capacity (lbs) of all on premise washing machines connected to the Ozone system; the make and model can be used to locate a manufacturer specification sheet where the laundry capacity (lbs) should be listed | The total capacity (combined) of all the washing machines does not have a limitation | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Duplicate property of 'Capacity', possibly remove | 2021-06-10 | Kenny Liljestrom |  | Add | 8
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any | EECP | 11 | Eligible ozone laundry products must meet the following requirements: • The washing capacity of each washing machine must be rated at 200 pounds or less. • The customer must have a natural gas-fired boiler or natural gas water heater that supplies hot water to the on-premise laundry (OPL) equipment. • The ozone laundry system(s) must be a new purchased product and installed with a new or existing commercial washing machine(s). • The ozone laundry system(s) must transfer ozone into the water with either the venture injection or bubble diffusion process. | Yes |  | New Equipment | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Collect the equipment invoice for the product | The invoice should list the equipment as new (i.e. not used, rebuilt. or leased) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 13
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any | EECP | 12 | Eligible ozone laundry products must meet the following requirements: • The washing capacity of each washing machine must be rated at 200 pounds or less. • The customer must have a natural gas-fired boiler or natural gas water heater that supplies hot water to the on-premise laundry (OPL) equipment. • The ozone laundry system(s) must be a new purchased product and installed with a new or existing commercial washing machine(s). • The ozone laundry system(s) must transfer ozone into the water with either the venture injection or bubble diffusion process. | Yes |  | Is the ozone transfer into the water via venturi injection or bubble diffusion? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Ensure specifications indicate what type of injection system is utilized | The ozone system needs to use either a venturi injection or bubble diffusion process to transfer the ozone to the laundry | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 79
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any | EECP | 13 | Laundry systems equipped with tunnel washers are not eligible. | Yes |  | Is the Ozone system installed on a laundry system equipped with a tunnel washer? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | Inspections | Photo of the washing machine | Ensure the washers are not large scale with tunnel washers (like would be found in a commercial laundry service facility) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 80
0 | SWAP006 | 2 | Dishwasher, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 12
0 | SWAP006 | 2 | Dishwasher, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 5
0 | SWAP006 | 2 | Dishwasher, Residential | Any | Any | Any | EECP | 3 | This measure is eligible for all residential building types of any vintage that utilize natural gas water heating equipment. | Yes |  | Water heater fuel type | Drop Down List | Gas;Electric; | [6 empty] | Must be 'Gas' | Inspections | Photograph the domestic water heater nameplate to capture the make and model number, or photograph the yellow pipe gas line going into the water heater | The water heater must use natural gas as the fuel source | QA Checklist | Implementer should provide proof of water heater fuel source in an installation report or proof that a natural gas water heater is used to supply the dishwasher | The water heater must use natural gas as the fuel source | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 22
0 | SWAP006 | 2 | Dishwasher, Residential | Any | Any | Any | EECP | 4 | Compact residential dishwashers and commercial dishwashers are excluded from this measure. | Yes |  | Dishwasher type | Drop Down List | Standard;Compact;Commercial; | [6 empty] | Must be 'Standard' | QA Checklist | Use the EnergyStar database to determine the Type of the Dishwasher | The Type must be listed on EnergyStar as Standard | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 15
0 | SWAP006 | 2 | Dishwasher, Residential | Any | Any | Any | EECP | 5 | The dishwasher must meet ENERGY STAR Program Requirements for Residential Dishwashers (Version 6.0).3 Please note that the offering is more stringent than the ENERGY STAR Most Efficient criteria. | Yes |  | Max. Estimated Annual Energy Use (kWh/yr) | Numeric Value | [7 empty] | Must be <= 199 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) of the Dishwasher | The Annual Energy Use (kWh/yr) must be listed on EnergyStar as <= 199 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 41
0 | SWAP006 | 2 | Dishwasher, Residential | Any | Any | Any | EECP | 6 | The dishwasher must meet ENERGY STAR Program Requirements for Residential Dishwashers (Version 6.0).3 Please note that the offering is more stringent than the ENERGY STAR Most Efficient criteria. | Yes |  | Max. Water Consumption (gallons/cycle) | Numeric Value | [7 empty] | Must be <= 3.5 | QA Checklist | Use the EnergyStar database to determine the Water Use (gallons/cycle) of the Dishwasher | The Water Use (gallons/cycle) must be listed on EnergyStar as <= 3.5 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 38
1 | SWAP006 | 3 | Dishwasher, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 12
1 | SWAP006 | 3 | Dishwasher, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 5
1 | SWAP006 | 3 | Dishwasher, Residential | Any | Any | Any | EECP | 3 | This measure is eligible for all residential building types of any vintage that utilize natural gas water heating equipment. | Yes |  | Water heater fuel type | Drop Down List | Gas;Electric; | [6 empty] | Must be 'Gas' | Inspections | Photograph the domestic water heater nameplate to capture the make and model number, or photograph the yellow pipe gas line going into the water heater | The water heater must use natural gas as the fuel source | QA Checklist | Implementer should provide proof of water heater fuel source in an installation report or proof that a natural gas water heater is used to supply the dishwasher | The water heater must use natural gas as the fuel source | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 22
1 | SWAP006 | 3 | Dishwasher, Residential | Any | Any | Any | EECP | 4 | Compact residential dishwashers and commercial dishwashers are excluded from this measure. | Yes |  | Dishwasher type | Drop Down List | Standard;Compact;Commercial; | [6 empty] | Must be 'Standard' | QA Checklist | Use the EnergyStar database to determine the Type of the Dishwasher | The Type must be listed on EnergyStar as Standard | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 15
1 | SWAP006 | 3 | Dishwasher, Residential | Any | Any | Any | EECP | 5 | The dishwasher must meet ENERGY STAR Program Requirements for Residential Dishwashers (Version 6.0).3 Please note that the offering is more stringent than the ENERGY STAR Most Efficient criteria. | Yes |  | Max. Estimated Annual Energy Use (kWh/yr) | Numeric Value | [7 empty] | Must be <= 199 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) of the Dishwasher | The Annual Energy Use (kWh/yr) must be listed on EnergyStar as <= 199 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 41
1 | SWAP006 | 3 | Dishwasher, Residential | Any | Any | Any | EECP | 6 | The dishwasher must meet ENERGY STAR Program Requirements for Residential Dishwashers (Version 6.0).3 Please note that the offering is more stringent than the ENERGY STAR Most Efficient criteria. | Yes |  | Max. Water Consumption (gallons/cycle) | Numeric Value | [7 empty] | Must be <= 3.5 | QA Checklist | Use the EnergyStar database to determine the Water Use (gallons/cycle) of the Dishwasher | The Water Use (gallons/cycle) must be listed on EnergyStar as <= 3.5 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 38
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed | EECP | 0 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 7
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed | EECP | 5 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 12
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | Any | EECP | 10 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer in EECP should match what is listed in the invoice or installation report |  | 2022-06-10 | Kenny Liljestrom |  | Add | 12
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | Any | EECP | 15 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number in EECP should match what is listed in the invoice or installation report |  | 2022-06-10 | Kenny Liljestrom |  | Add | 5
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed | EECP | 20 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number in EECP should match what is listed in the invoice or installation report |  | 2022-06-10 | Kenny Liljestrom |  |  | 13
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed | EECP | 25 | The following products are not eligible: packaged terminal air conditioners (PTACs), portable air conditioners, room air conditioner models with electric resistance heat as the primary heat source, and dehumidifiers. | Yes | Equipment Type | Equipment type | Drop Down List | Window AC;Through the wall AC;Other; | Not Equal | Other |  |  |  |  | Must not be Other | QA Checklist | Using the make and model, determine the equipment type from the EnergyStar database | The equipment types on EnergyStar should not include any of the following: • packaged terminal air conditioners (PTACs) • portable air conditioners • room air conditioner models with electric resistance heat as the primary heat source • dehumidifiers | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-06-10 | Kenny Liljestrom |  | Add | 14
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed | EECP | 30 | The room air conditioner must meet or exceed the current ENERGY STAR efficiency levels and carry the ENERGY STAR qualification, as per specification in the Measure Case Description. | Yes | Energy Star ID | Energy Star unique ID | Text Box | [8 empty] | QA Checklist | Review the EnergyStar database to check for the make and model of the installed equipment | The equipment in EECP should be locatable on the EnergyStar database as being a certified product and should match the make and model of the equipment | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Can we have this qualify via Energy Star within CPSS and not entered yes/no by the 3P? | 2022-06-10 | Kenny Liljestrom |  | Add | 21
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed | EECP | 35 | E-5152 Data Collection Requirements | Yes | Capacity | Cooling Capacity (BTU/h) | Numeric Value |  |  |  | General | 0 |  | 0 |  | Inspections | Photograph the equipment nameplate to capture the cooling capacity (Btu/hr) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the EnergyStar database to check for the capacity (Btu/hr) of the installed equipment | The equipment in EECP should be locatable on the EnergyStar database as being a certified product and should have a capacity (Btu/hr) that matches EECP |  | 2022-06-10 | Kenny Liljestrom |  |  | 24
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed | EECP | 40 | E-5152 Data Collection Requirements | Yes | CEER | Combined Energy Efficiency Ratio (CEER) | Numeric Value |  |  |  | General | 0 |  | 1 |  | Inspections | Photograph the equipment nameplate to capture the Combined Energy Efficinecy Ratio (CEER) value | The listed CEER value in EECP should match the nameplate | QA Checklist | Review the EnergyStar database to check for the Combined Energy Efficinecy Ratio (CEER) value of the installed equipment | The equipment in EECP should be locatable on the EnergyStar database as being a certified product and should have a CEER value that matches EECP |  | 2022-06-10 | Kenny Liljestrom |  |  | 39
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed | EECP | 190 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value |  |  |  | General |  |  | 0 |  | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 8
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed | EECP | 195 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 15
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the modulating valve nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-05 | Kenny Liljestrom |  | Add | 12
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the modulating valve nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-05 | Kenny Liljestrom |  | Add | 5
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any | EECP | 3 | This measure is applicable for all new and existing commercial or multifamily buildings of all vintages. For the commercial sector, this measure will apply to the following building types: general commercial, hotels, motels, small retail, and nursing homes. | Yes |  | Building type | Drop Down List | Multifamily;General commercial;Hotel;Motel;Small retail;Nursing home; | [7 empty] | Inspections | Document the type of building the unit was installed in (Multifamily, General commercial, Hotel, Motel, Small retail, or Nursing home) | The building type listed in EECP should match the building type during the inspection | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 13
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any | EECP | 4 | A professional installer will be required for all installations of this product as the inlet natural gas line will have to be removed and reattached during installation. | Yes |  | Was a professional installer used to remove and reattach the gas line? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Request the name of the installer for the gas valve and or contractor license number | Use the installer or contractor license number to determine if the installer is qualified using the Contractor License Board verification website (https://www.cslb.ca.gov/OnlineServices/CheckLicenseII/checklicense.aspx) | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 70
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any | EECP | 5 | All applicants must have their dryers on site | Yes | Dryer OnSite | Are the dryers on the site premise? | Drop Down List | Yes;No | [6 empty] | Must be Yes | Inspections | Determine if the dryers are on the site premise for the applicant or at a remote site | The dryers need to be on the same premise as the customers address | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-08-05 | Kenny Liljestrom |  | Add | 35
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any | EECP | 6 | A dryer that makes use of a common or dedicated steam system is not eligible. | Yes |  | Does the dryer make use of a common dedicated steam system? | Drop Down List | Yes;No | [6 empty] | Must be No | Inspections | Ask the customer if there is a dedicated steam system onsite to serve the laundry facility; Some dryers are capable of using both steam and natural gas | Document the customers response, there should be no steam serving the dryers | QA Checklist | Use the make and model number of the dryers to determine if that unit is capable of operating with steam; If the dryer is capable of using steam, request via an installation report whether or not the dryer is served by a dedicated steam system | The unit should not be able to operate with steam, but if it can, there should be no steam system onsite or at the least not serving the laundry dryers | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 59
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any | EECP | 7 | The natural gas dryer must not be modified by any technology that would reduce the natural gas consumption beyond the manufacturer specifications. | Yes |  | Is the max flow/capacity of the modulating valve greater than or equal to that of the dryer? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 92
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any | EECP | 8 | This measure is not eligible for dryers with a capacity greater than 200 lbs or less than 20 lbs. For capacities outside of this range, a custom measure type is recommended. | Yes |  | Capacity of largest dryer (lbs) | Numeric Value | [7 empty] | Must be > 20 and <= 200 | Inspections | Photograph the nameplate on the dryer | Sometimes the capacity is listed on the nameplate of the dryer; if not listed, supply the make and model information to the processor to verify the capacity of the dryer | QA Checklist | Use either the make and model of the dryer to locate the specification sheet and determine the capacity of the unit; or request via an installation report photographs of the dryer nameplate and/or the dryer specification sheet to validate the capacity of the largest dryer | Using either method, determine if the dryer has a maximum capacity (lbs) of > 20 lbs and <= 200 lbs | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 31
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any | EECP | 9 | This measure is not eligible for dryers with a capacity greater than 200 lbs or less than 20 lbs. For capacities outside of this range, a custom measure type is recommended. | Yes |  | Total dryer capacity affected (lbs) | Numeric Value | [8 empty] | Inspections | Photograph the nameplates of all the dryers with gas modulating valves | Sometimes the capacity is listed on the nameplate of the dryer; if not listed, supply the make and model information to the processor to verify the capacity of the dryers | QA Checklist | Use either the make and model of the dryer to locate the specification sheet and determine the capacity of the unit; or request via an installation report photographs of the dryer nameplate and/or the dryer specification sheet to validate the capacity of the largest dryer | There are no pass or fail criteria for the property just good information to collect | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 35
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any | QA Checklist | 10 | Natural gas must be supplied by a California utility. | Yes |  | Natural gas must be supplied by a California utility. | Text Box | [8 empty] | QA Checklist | Use EECP to determine if the customer purchases natural gas from SDG&E | The customer must be an active account holder and purchase natural gas from SDG&E | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 53
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any | EECP | 11 |  | Yes | Natural Gas | Does the existing dryer use natural gas? | Drop Down List | Yes;No | [7 empty] | - | - | - | - | - | - | Engineering request to expire | 2022-01-24 | Kenny Liljestrom |  |  | 40
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any | EECP | 12 |  | Yes | Size | Drum Capacity (lbs) | Numeric Value | [8 empty] | - | - | - | - | - | - | Engineering request to expire | 2022-01-24 | Kenny Liljestrom |  |  | 19
0 | SWBE001 | 2 | Greenhouse Heat Curtain | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 12
0 | SWBE001 | 2 | Greenhouse Heat Curtain | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 5
0 | SWBE001 | 2 | Greenhouse Heat Curtain | Any | Any | Any | EECP | 3 | This measure is applicable for agricultural or commercial greenhouse of any vintage for the primary purpose of the production of nursery products, horticultural specialties, or ornamental products | Yes |  | Greenhouse facility specialty | Text Box | [8 empty] | Inspections | Make note of the type of agriculture taking place at the facility | The description in EECP should match the agriculture type of the facility | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 29
0 | SWBE001 | 2 | Greenhouse Heat Curtain | Any | Any | Any | QA Checklist | 4 | Eligible products must meet the following requirements: Must be a single-layer interior curtain installed for heat retention. Must be installed in a gas-heated greenhouse facility. The facility must be a greenhouse with the primary purpose of agricultural use. The heat curtain must be a new curtain installed where none previously existed or a new curtain that is replacing an existing curtain that is no longer functional. The heat curtain must be installed above the conditioned area where the gas heat source provides hot air to plant and seed species. The heat curtain must have a natural gas savings rating that meets or exceeds 40%. The heat curtain must have a warranty/product life of five years. The installation must allow the curtain to be automatically or manually moved into place. | Yes |  | The greenhouse curtain must be a single layer plastic curtain | None | [8 empty] | Inspections | Inspect the greenhouse curtain to check for the number of layers of plastic | The curtain should contain only a single layer of material (i.e. not double and triple stacked curtains | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 61
0 | SWBE001 | 2 | Greenhouse Heat Curtain | Any | Any | Any | EECP | 5 | Eligible products must meet the following requirements: Must be a single-layer interior curtain installed for heat retention. Must be installed in a gas-heated greenhouse facility. The facility must be a greenhouse with the primary purpose of agricultural use. The heat curtain must be a new curtain installed where none previously existed or a new curtain that is replacing an existing curtain that is no longer functional. The heat curtain must be installed above the conditioned area where the gas heat source provides hot air to plant and seed species. The heat curtain must have a natural gas savings rating that meets or exceeds 40%. The heat curtain must have a warranty/product life of five years. The installation must allow the curtain to be automatically or manually moved into place. | Yes |  | Greenhouse is heated by natural gas (not propane)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | Inspect the gas lines going to the greenhouse heaters | The heaters should be fueled by natural gas; there should not be propane tanks connected to the gas lines fueling the heaters | QA Checklist | Check the customer usage data or history to determine if the facility uses natural gas | The facility must consume natural gas to qualify for this measure |  | 2022-02-28 | Kenny Liljestrom |  |  | 50
0 | SWBE001 | 2 | Greenhouse Heat Curtain | Any | Any | Any | EECP | 6 | Eligible products must meet the following requirements: Must be a single-layer interior curtain installed for heat retention. Must be installed in a gas-heated greenhouse facility. The facility must be a greenhouse with the primary purpose of agricultural use. The heat curtain must be a new curtain installed where none previously existed or a new curtain that is replacing an existing curtain that is no longer functional. The heat curtain must be installed above the conditioned area where the gas heat source provides hot air to plant and seed species. The heat curtain must have a natural gas savings rating that meets or exceeds 40%. The heat curtain must have a warranty/product life of five years. The installation must allow the curtain to be automatically or manually moved into place. | Yes |  | Heat curtain gas savings rating (%) | Numeric Value | [7 empty] | Must be >= 40% | QA Checklist | Review the submitted specification sheet and determine the gas or energy savings rating (%) of the product installed | The energy or gas savings rating must be >= 40% as indicated in the specification sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 35
0 | SWBE001 | 2 | Greenhouse Heat Curtain | Any | Any | Any | QA Checklist | 7 | Eligible products must meet the following requirements: Must be a single-layer interior curtain installed for heat retention. Must be installed in a gas-heated greenhouse facility. The facility must be a greenhouse with the primary purpose of agricultural use. The heat curtain must be a new curtain installed where none previously existed or a new curtain that is replacing an existing curtain that is no longer functional. The heat curtain must be installed above the conditioned area where the gas heat source provides hot air to plant and seed species. The heat curtain must have a natural gas savings rating that meets or exceeds 40%. The heat curtain must have a warranty/product life of five years. The installation must allow the curtain to be automatically or manually moved into place. | Yes |  | Product has a warranty >= 5 years | None | [8 empty] | QA Checklist | Review the manufacturer specification sheet to find the warranty information | The product should be covered by at minimum a 5-year warranty | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 33
0 | SWBE001 | 2 | Greenhouse Heat Curtain | Any | Any | Any | EECP | 8 | The square footage of the new heat curtain cannot exceed the square footage of the greenhouse floor. Additionally, any overhang and overlap of curtain material cannot be included in the square footage calculation. | Yes |  | Quantity (sq ft) of heat curtain does not include overlap or exceed sq ft of the floor? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | Inspect the installed heat curtain | The curtain should not be draped over support structures, nor should the estimated square footage (quantity in EECP) be greater than the floor area of the greenhouse; best estimates are sufficient for the square footage determination | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 87
1 | SWBE002 | 2 | Greenhouse Infrared Film | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 12
1 | SWBE002 | 2 | Greenhouse Infrared Film | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 5
1 | SWBE002 | 2 | Greenhouse Infrared Film | Any | Any | Any | EECP | 3 | This measure is applicable for agricultural or commercial greenhouse of any vintage for the primary purpose of the production of nursery products, horticultural specialties, or ornamental products | Yes |  | Greenhouse facility specialty | Text Box | [8 empty] | Inspections | Make note of the type of agriculture taking place at the facility | The description in EECP should match the agriculture type of the facility | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 29
1 | SWBE002 | 2 | Greenhouse Infrared Film | Any | Any | Any | EECP | 4 | The installation of infrared (IR) film must meet the following requirements: The IR film must be installed in a gas-heated greenhouse facility. The heating equipment type (building HVAC) must be specified in the implementation of the measure. The facility must be a greenhouse with the primary purpose of agricultural use. The film must be infrared, anti-condensate, polyethylene plastic with a minimum thickness of six thousandths of an inch. The IR film shall not be installed on the walls of the greenhouse. | Yes |  | Greenhouse is heated by natural gas (not propane)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | Inspect the gas lines going to the greenhouse heaters | The heaters should be fueled by natural gas; there should not be propane tanks connected to the gas lines fueling the heaters | QA Checklist | Check the customer usage data or history to determine if the facility uses natural gas | The facility must consume natural gas to qualify for this measure |  | 2022-02-28 | Kenny Liljestrom |  |  | 50
1 | SWBE002 | 2 | Greenhouse Infrared Film | Any | Any | Any | EECP | 5 | The installation of infrared (IR) film must meet the following requirements: The IR film must be installed in a gas-heated greenhouse facility. The heating equipment type (building HVAC) must be specified in the implementation of the measure. The facility must be a greenhouse with the primary purpose of agricultural use. The film must be infrared, anti-condensate, polyethylene plastic with a minimum thickness of six thousandths of an inch. The IR film shall not be installed on the walls of the greenhouse. | Yes |  | Gas heating equipment type | Drop Down List | aGF;aRH; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-28 | Kenny Liljestrom |  |  | 26
1 | SWBE002 | 2 | Greenhouse Infrared Film | Any | Any | Any | QA Checklist | 6 | The installation of infrared (IR) film must meet the following requirements: The IR film must be installed in a gas-heated greenhouse facility. The heating equipment type (building HVAC) must be specified in the implementation of the measure. The facility must be a greenhouse with the primary purpose of agricultural use. The film must be infrared, anti-condensate, polyethylene plastic with a minimum thickness of six thousandths of an inch. The IR film shall not be installed on the walls of the greenhouse. | Yes |  | The IR film must be infrared, anti-condensate, polyethylene plastic with a minimum thickness of six thousandths of an inch. | None | [8 empty] | QA Checklist | Use the submitted manufacturer specification sheet to ensure the item qualifies based on the following criteria: infrared, anti-condensate, polyethylene plastic with a minimum thickness of six thousandths of an inch | The IR Film must meet these criteria to qualify: - It must be infrared type film - the film must be anti-condensate - the film must be made of polyethylene plastic - the film thickness must be >= 6/1000 (0.006-inches) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 123
1 | SWBE002 | 2 | Greenhouse Infrared Film | Any | Any | Any | EECP | 7 | The installation of infrared (IR) film must meet the following requirements: The IR film must be installed in a gas-heated greenhouse facility. The heating equipment type (building HVAC) must be specified in the implementation of the measure. The facility must be a greenhouse with the primary purpose of agricultural use. The film must be infrared, anti-condensate, polyethylene plastic with a minimum thickness of six thousandths of an inch. The IR film shall not be installed on the walls of the greenhouse. | Yes |  | IR Film only installed on the roof (not on the walls)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | Inspect the IR film installation to check the walls and roof | The IR film is only allowed to be installed on the roof to qualify; if IR film is on the walls, the claimed quantity in EECP should align with, using your best estimates, to the square footage of the roof alone | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 54
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the Anti-Sweat Heater Control box nameplate to capture the manufacturer; the box may be located on the interior of the case or walk-in near the junction box | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-10 | Kenny Liljestrom |  | Add | 12
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the Anti-Sweat Heater Control box nameplate to capture the model number; the box may be located on the interior of the case or walk-in near the junction box | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-10 | Kenny Liljestrom |  | Add | 5
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | Any | Any | Any | EECP | 3 | The program should collect and verify the vintage of the building and the refrigeration multiplex system. | Yes | Date of Construction | Date of Construction | Date | [8 empty] | QA Checklist | There is no pass or fail criteria for this property, it is recommended for data collection purposes | There is no pass or fail criteria for this property, it is recommended for data collection purposes | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | This would be in the property information on the application | 2021-06-10 | Kenny Liljestrom |  | Add | 20
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | Any | Any | Any | EECP | 4 | The program should collect and verify the vintage of the building and the refrigeration multiplex system. The offerings are ineligible for multiplex systems majorly upgraded or installed after July 1, 2014 since the Title-24 code mandates the floating controls since July 1, 2014. | Yes | Date of Installation | Date of installation or major upgrade to refrigeration multiplex system | Date | [7 empty] | Must be before 7/1/2014 | Inspections | Photograph the of refrigeration system (chiller) nameplate to capture the serial number and, more preferrable, the date of manufacture | Validate the serial number or date of manufacture is consistent with installations dates listed in EECP | QA Checklist | The implementer can verify this information by providing the serial number or construction date of the refrigeration system | The serial number can be cross referenced with the manufacturer or online lookup tables if not provided directly on the nameplate of the system; the system must be older than 7/1/2014 to qualify |  | 2021-06-10 | Kenny Liljestrom |  | Add | 71
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | A | Any | Any | EECP | 5 | The unit energy savings (UES) of anti-sweat heater (ASH) controls are based upon the installation of controllers on existing ASHs on low-temperature (case temperature below 32 °F) and medium-temperature case temperature (at or above 32 °F) display cases. | Yes | Temp Below 32F | Is the case temperature below 32F? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Check case temperatures with thermometers installed in the cases or with a handheld thermocouple | The case temperature should be below 32F (or a freezer) | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Can be removed; data in measure description | 2021-06-10 | Kenny Liljestrom |  | Add | 34
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | B | Any | Any | EECP | 6 | The unit energy savings (UES) of anti-sweat heater (ASH) controls are based upon the installation of controllers on existing ASHs on low-temperature (case temperature below 32 °F) and medium-temperature case temperature (at or above 32 °F) display cases. | Yes |  | Is the case temperature above 32F? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Check case temperatures with thermometers installed in the cases or with a handheld thermocouple | The case temperature should be above 32F (or a refrigerator) | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Can be removed; data in measure description | 2021-08-03 | Kenny Liljestrom |  | Add | 34
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | Any | Any | Any | EECP | 7 | To qualify, the display case must be equipped with humidity-sensing controls that reduce the amount of power supplied to the heaters as the store dew point (DP) temperature decreases.. | Yes | Humidity Sensing Controls | Display case equipped with humidity-sensing controls based on the store dew point temperature? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Update property label so it makes sense | 2021-06-10 | Kenny Liljestrom |  | Add | 94
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | Any | Any | Any | EECP | 8 | Typically, power reduction occurs when relative humidity levels reach 55% and lower. Power reduction should decrease by at least 2% for every percentage the humidity falls below 55%. | Yes | Power Reduction | Does power reduction decrease by at least 2% for every percentage the humidity falls below 55%? | Drop Down List | Yes;No; | [7 empty] | QA Checklist | Using the manufacturer spec sheet, identify the controls summary information to check for power reduction based on humidity decrease; if not, the following criteria must be met | The controls must decrease power by 2% for every humidity percentage decrease below 55%; if not, the following criteria must be met | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Validation criteria needs to be updated | 2021-06-10 | Kenny Liljestrom |  | Add | 95
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | Any | Any | Any | EECP | 9 | Equivalent technologies that can reduce or turn off ASHs based on the amount of condensation formed on the inner glass pane may also qualify. | Yes |  | If humidity is not monitored, ASH controls turn off based on the condensation formed on inner glass? | Drop Down List | Yes;No;N/A; | [6 empty] | If Power Reduction is 'No' then Must be 'Yes' | QA Checklist | Using the manufacturer spec sheet, identify the controls summary information to check for shut off controls based on condensation formed on the inner glass | If the above criteria passed, disregard the measure property; the manufacturer spec sheet should list the controls as having the ability to shut off the anti-sweat heating elements based on the amount of condensation formed on the glass door | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-03 | Kenny Liljestrom |  | Add | 100
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | B | Any | Any | EECP | 10 | This measure cannot be used in conjunction with the new refrigeration display case with doors. This measure cannot be used in conjunction with the special doors with low/no anti-sweat heat on low-temperature display case. | Yes | Doors Anti Sweat Heat Controls | Do the installed doors have low/no anti-sweat heat controls in conjunction with the installed controls? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-06-10 | Kenny Liljestrom |  | Add | 103
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | Any | Any | Any | EECP | 11 | This measure cannot be used in conjunction with the new refrigeration display case with doors. | Yes | Display Case Doors New | Are the refrigeration display case doors new? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | Inspections | Photos of case doors, look for anything indicating doors are not new | The doors must not looked like they have been replaced within the last couple months | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 45
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the Anti-Sweat Heater Control box nameplate to capture the manufacturer; the box may be located on the interior of the case or walk-in near the junction box | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-06 | Kenny Liljestrom | Effective Date 1/1/2022 | Add | 12
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the Anti-Sweat Heater Control box nameplate to capture the model number; the box may be located on the interior of the case or walk-in near the junction box | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-06 | Kenny Liljestrom | Effective Date 1/1/2022 | Add | 5
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any | QA Checklist | 3 | The program should collect and verify the vintage of the building and the refrigeration multiplex system. | No | Date of Construction | Date of Construction | Date | [8 empty] | EECP | There is no pass or fail criteria for this property, it is recommended for data collection purposes | There is no pass or fail criteria for this property, it is recommended for data collection purposes | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-08-06 | Kenny Liljestrom | Property removed from EECP, put on QA Checklist instead since this data is captured at the enrollment level | Add | 20
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any | QA Checklist | 4 | The program should collect and verify the vintage of the building and the refrigeration multiplex system. | Yes | Date of Construction | Date of Construction | Date | [8 empty] | QA Checklist | There is no pass or fail criteria for this property, it is recommended for data collection purposes | There is no pass or fail criteria for this property, it is recommended for data collection purposes | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Updated property source to QA Checklist from EECP; Building vintage is captured at the enrollment level | 2022-01-04 | Kenny Liljestrom |  |  | 20
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any | EECP | 5 | The program should collect and verify the vintage of the building and the refrigeration multiplex system. The offerings are ineligible for multiplex systems majorly upgraded or installed after July 1, 2014 since the Title-24 code mandates the floating controls since July 1, 2014. | Yes | Date of Installation | Date of installation or major upgrade to refrigeration multiplex system | Date | [7 empty] | Must be before 7/1/2014 | Inspections | Photograph the of refrigeration system (chiller) nameplate to capture the serial number and, more preferrable, the date of manufacture | Validate the serial number or date of manufacture is consistent with installations dates listed in EECP | QA Checklist | The implementer can verify this information by providing the serial number or construction date of the refrigeration system | The serial number can be cross referenced with the manufacturer or online lookup tables if not provided directly on the nameplate of the system; the system must be older than 7/1/2014 to qualify |  | 2021-08-06 | Kenny Liljestrom | Effective Date 1/1/2022 | Add | 71
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any | EECP | 6 | To qualify, the display case must be equipped with humidity-sensing controls that reduce the amount of power supplied to the heaters as the store dew point (DP) temperature decreases.. | Yes | Humidity Sensing Controls | Display case equipped with humidity-sensing controls based on the store dew point temperature? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Update property label so it makes sense | 2021-08-06 | Kenny Liljestrom | Effective Date 1/1/2022 | Add | 94
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any | EECP | 7 | Typically, power reduction occurs when relative humidity levels reach 55% and lower. Power reduction should decrease by at least 2% for every percentage the humidity falls below 55%. | Yes | Power Reduction | Does power reduction decrease by at least 2% for every percentage the humidity falls below 55%? | Drop Down List | Yes;No; | [7 empty] | QA Checklist | Using the manufacturer spec sheet, identify the controls summary information to check for power reduction based on humidity decrease; if not, the following criteria must be met | The controls must decrease power by 2% for every humidity percentage decrease below 55%; if not, the following criteria must be met | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Validation criteria needs to be updated | 2021-08-06 | Kenny Liljestrom | Effective Date 1/1/2022 | Add | 95
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any | EECP | 8 | Equivalent technologies that can reduce or turn off ASHs based on the amount of condensation formed on the inner glass pane may also qualify. | Yes | ASH Controls | If humidity is not monitored, ASH controls turn off based on the condensation formed on inner glass? | Drop Down List | Yes;No;N/A; | [6 empty] | If Power Reduction is 'No' then Must be 'Yes' | QA Checklist | Using the manufacturer spec sheet, identify the controls summary information to check for shut off controls based on condensation formed on the inner glass | If the above criteria passed, disregard the measure property; the manufacturer spec sheet should list the controls as having the ability to shut off the anti-sweat heating elements based on the amount of condensation formed on the glass door | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom | Effective Date 1/1/2022 | Add | 100
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | B | Any | Any | EECP | 9 | This measure cannot be used in conjunction with the new refrigeration display case with doors. This measure cannot be used in conjunction with the special doors with low/no anti-sweat heat on low-temperature display case. | No | Doors Anti Sweat Heat Controls | Do the installed doors have low/no anti-sweat heat controls in conjunction with the installed controls? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-08-06 | Kenny Liljestrom | Property updated to QA checklist in order to place a level of trust with the implementers since this is difficult to near impossible to verify | Add | 103
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | B | Any | Any | QA Checklist | 9 | This measure cannot be used in conjunction with the new refrigeration display case with doors. This measure cannot be used in conjunction with the special doors with low/no anti-sweat heat on low-temperature display case. | Yes | Doors Anti Sweat Heat Controls | Do the installed doors have low/no anti-sweat heat controls in conjunction with the installed controls? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-08-06 | Kenny Liljestrom | Effective Date 1/1/2022 | Add | 103
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any | EECP | 11 | This measure cannot be used in conjunction with the new refrigeration display case with doors. | Yes | Display Case Doors New | Are the refrigeration display case doors new? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | Inspections | Photos of case doors, look for anything indicating doors are not new | The doors must not looked like they have been replaced within the last couple months | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom | Effective Date 1/1/2022 | Add | 45
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any | EECP | 12 | This measure cannot be used in conjunction with the new refrigeration display case with doors. | Yes | Temp Below 32F | Is the case temperature below 32F? | Drop Down List | Yes;No | [7 empty] | - | - | - | - | - | - | Engineering request to expire | 2022-01-24 | Kenny Liljestrom |  |  | 34
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-03 | Kenny Liljestrom |  | Add | 12
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-03 | Kenny Liljestrom |  | Add | 5
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any | EECP | 3 | Preponderance of evidence (POE) must be documented including: Customer/site information, specifications of existing equipment, proof the existing fan motor is still operating as intended, existing fan motor nameplate data with manufacturer date to confirm RUL, Replacement Motor nameplate information, if the equipment was replaced as a direct result of recommendations provided by the PA. | Yes | POE Docs | Has all the preponderance of evidence required by the workpaper been uploaded in EECP? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Check EECP for any POE related documents | Preponderance of evidence (POE) must be documented including: • Customer/site information, specifications of existing equipment • proof the existing fan motor is still operating as intended • existing fan motor nameplate data with manufacturer date to confirm RUL • Replacement Motor nameplate information • if the equipment was replaced as a direct result of recommendations provided by the PA | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 86
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any | EECP | 4 | This measure cannot be used in conjunction with the following measures: SWAP011 Vending and Beverage Merchandise Controller SWCR002 Low-Temperature Display Case Doors With No Anti-Sweat Heaters SWCR018 Reach-In Refrigerator or Freezer, Commercial SWCR019 Low-Temperature Coffin To Reach-In Display Case Conversion SWCR021 Medium or Low-Temperature Display Case With Doors SWCR020 Medium-Temperature Open Display Case Retrofit | Yes |  | Has this measure been combined with another refrigeration measure? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | QA Checklist | Check the enrollment package or installation report for any other refrigeration measures | This measure cannot be used in conjunction with the following measures: SWAP011 Vending and Beverage Merchandise Controller SWCR002 Low-Temperature Display Case Doors With No Anti-Sweat Heaters SWCR018 Reach-In Refrigerator or Freezer, Commercial SWCR019 Low-Temperature Coffin To Reach-In Display Case Conversion SWCR021 Medium or Low-Temperature Display Case With Doors SWCR020 Medium-Temperature Open Display Case Retrofit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 66
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any | EECP | 5 | This measure is applicable in conditioned spaces in any existing commercial building type of any vintage. | Yes |  | Is the building an existing commercial building? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | While on site, indicate whether or not the building is new (built within the last year) or existing | The building needs to be existing | QA Checklist | Use EECP to check for the service length of the site address | The site address should have at least one-year of continued service form SDG&E | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 48
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any | QA Checklist | 6 | The motor is installed as an evaporator fan motor in a refrigerated display case | Yes |  | Is the motor installed on a refrigerated display case? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | Observe the equipment where the motor was installed | The equipment was installed on a refrigerated display case | QA Checklist | Photographs of the motor and display case can be used to show what the motor was installed in | The motor must be installed in a refrigerated display case | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 54
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any | EECP | 7 | Program implementers are encouraged to collect data on motor products installed under the rebate program, such as the type of display case receiving a new motor, motor size, motor cost, and labor cost. | Yes | Fridge Type | Type of refrigerated display case the motor is being installed on | Drop Down List | Open Vertical;Vertical with Doors;Horizontal;Horizontal with Doors;Coffin;Island;Counter;Other; | [7 empty] | Inspections | Observe the case type where the motor is installed; There are several case types including Open Vertical; Vertical with Doors; Horizontal; Horizontal with Doors; Coffin; Island; Counter; Other; | The case type must match the type listed in EECP | QA Checklist | Use the installation report to identify the case type the motor was installed in | There are no validation criteria other than trying to match the type of case to what is listed in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 65
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any | QA Checklist | 8 | The installed motor is a permanent magnet electronically commutated motor (ECM) or permanent magnet synchronous AC (PMS) motor/fan. | Yes |  | Installed an electronically commutated motor (ECM) or permanent magnet synchronous (PMS) motor/fan? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice, installation report, or manufacturer spec sheet to validate the motor type is listed | The motor type listed in EECP should match what is listed in the invoice, installation report, or manufacturer spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 99
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any | EECP | 9 | The motor must be described as a low‐power or high efficiency model by the manufacturer | Yes | Motor Model | Does the manufacturer describe the motor as a low-power or high efficiency model? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted manufacturer spec sheet to validate if the motor is described as a low‐power or high efficiency model by the manufacturer | The motor must be described as a low‐power or high efficiency model by the manufacturer | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 81
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any | EECP | 10 | The new motor is the available product most closely matched to the original motor's speed and shaft output power (equivalent size) | Yes | Match Output power | Is the new motor closely matched to the original motor's speed and shaft output power? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-10 | Kenny Liljestrom |  | Add | 86
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any | EECP | 11 | Program implementers are encouraged to collect data on motor products installed under the rebate program, such as the type of display case receiving a new motor, motor size, motor cost, and labor cost. | Yes | Motor Size | Replacement motor size (W) | Numeric Value | [8 empty] | QA Checklist | Use the submitted manufacturer spec sheet to validate the motor power (W) | The value in EECP should match what is listed in the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 26
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any | EECP | 12 | Due to limited quantitative results in studies pertaining to refrigerated display cases on the market spread of motor efficiency within rather than across motor types (and motor size classes), program implementers are also encouraged to collect data on motor type and motor efficiency ratings that could be used in future programs to specify a high‐efficiency level for each motor type. | Yes | Motor Efficiency | Replacement motor efficiency (%) | Numeric Value | [8 empty] | QA Checklist | Use the submitted manufacturer spec sheet to validate the motor efficiency (%) | The value in EECP should match what is listed in the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 32
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any | EECP | 13 | Program implementers are encouraged to collect data on motor products installed under the rebate program, such as the type of display case receiving a new motor, motor size, motor cost, and labor cost. | Yes | Material Cost | Material cost for replacement motor | Numeric Value | [8 empty] | QA Checklist | Use the submitted invoice to identify the material cost for the motor | The value in EECP should match what is listed in the invoice | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 35
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any | EECP | 14 | Program implementers are encouraged to collect data on motor products installed under the rebate program, such as the type of display case receiving a new motor, motor size, motor cost, and labor cost. | Yes | Labor Cost | Labor cost for replacement motor | Numeric Value | [8 empty] | QA Checklist | Use the submitted invoice to identify the labor cost for the motor | The value in EECP should match what is listed in the invoice | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 32
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 12
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 5
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any | EECP | 3 | Preponderance of evidence (POE) must be documented including: Customer/site information, specifications of existing equipment, proof the existing fan motor is still operating as intended, existing fan motor nameplate data with manufacturer date to confirm RUL, Replacement Motor nameplate information, if the equipment was replaced as a direct result of recommendations provided by the PA. | Yes | POE Docs | Has all the preponderance of evidence required by the workpaper been uploaded in EECP? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Check EECP for any POE related documents | Preponderance of evidence (POE) must be documented including: • Customer/site information, specifications of existing equipment • proof the existing fan motor is still operating as intended • existing fan motor nameplate data with manufacturer date to confirm RUL • Replacement Motor nameplate information, if the equipment was replaced as a direct result of recommendations provided by the PA | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 86
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any | EECP | 4 | Pre-inspection of existing equipment is required. | Yes | Site Pre-Inspection | Has a site Pre-Inspection been completed and documentation uploaded in EECP? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | Check EECP documents for any pre-inspection reports | There must be a pre-inspection for this measure to qualify | QA Checklist | Check EECP documents for any pre-inspection reports | There must be a pre-inspection for this measure to qualify |  | 2021-06-10 | Kenny Liljestrom |  | Add | 76
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any | EECP | 5 | The existing motor system must be fully functional with no signs of replacement in the 12 months following the project application date. | Yes |  | Existing motor was fully functional with no sign of replacement in 12 months from project app. date? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-04-12 | Kenny Liljestrom |  | Add | 100
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any | EECP | 7 | This measure is applicable in any existing commercial building type 2008 and older. This is based on the assumption that walk-in equipment is at least as new as the building. | Yes | Date Installed | When was the walk-in installed in the building? | Date | [7 empty] | Must be before 1/1/2009 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Property validation needs to be configured | 2021-08-06 | Kenny Liljestrom |  | Add | 47
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any | QA Checklist | 8 | This measure cannot be used in conjunction with the evaporative fan controller for walk-in coolers and freezers. | Yes |  | Measure combined with evaporative fan controller for walk-in coolers and/or freezers? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | QA Checklist | Using the measure report and EECP double dip, check previously installed measures at the location | The measure listing should not include evaporative fan controllers for the walk-in cooler or freezer | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-04-12 | Kenny Liljestrom | System of record updated from EECP to QA Checklist per request of Programs team who indicated the property could be cheked via double-dip report | Add | 85
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any | EECP | 9 | The measure excludes motors greater than ½ horsepower. | Yes | Motor Size | Replacement motor size (W) | Numeric Value | [7 empty] | Must be <= 373 | QA Checklist | Use the installation report or manufacturer spec sheet to validate the power (W) of the replacement motor is listed | The Power (W) listed in EECP should match the manufacturer spec sheet and be <= 373 W | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property validation needs to be configured | 2021-06-10 | Kenny Liljestrom |  | Add | 26
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any | EECP | 10 | The highest quality data collection would include associated motor sizes (nominal W) and a table of material and labor costs for each size of motor being installed. | Yes | CFM | Fan flow rate (CFM) | Numeric Value | [8 empty] | QA Checklist | Use the installation report or manufacturer spec sheet to validate the flow rate (cfm) of the replacement motor is listed | The Flow Rate (cfm) listed in EECP should match the manufacturer spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 19
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any | EECP | 11 | To improve quality of cost-effectiveness calculations, programs implementing this measure should collect data on actual costs for materials and labor. The highest quality data collection would include associated motor sizes (nominal W) and a table of material and labor costs for each size of motor being installed. | Yes | Material Cost | Material cost for replacement motor | Numeric Value | [8 empty] | QA Checklist | Use the submitted invoice to verify the material cost of the equipment | The cost listed in EECP should match the submitted invoice | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 35
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any | EECP | 12 | To improve quality of cost-effectiveness calculations, programs implementing this measure should collect data on actual costs for materials and labor. The highest quality data collection would include associated motor sizes (nominal W) and a table of material and labor costs for each size of motor being installed. | Yes | Labor Cost | Labor cost for replacement motor | Numeric Value | [8 empty] | QA Checklist | Use the submitted invoice to verify the labor cost of the equipment | The cost listed in EECP should match the submitted invoice | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 32
0 | SWCR005 | 1 | Auto Closer For Refrigerated Storage Door | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | If accessible, photograph the controller nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-12 | Kenny Liljestrom |  | Add | 12
0 | SWCR005 | 1 | Auto Closer For Refrigerated Storage Door | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | If accessible, photograph the controller nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-12 | Kenny Liljestrom |  | Add | 5
0 | SWCR005 | 1 | Auto Closer For Refrigerated Storage Door | A | Any | Any | EECP | 3 | The automatic closer must be installed on a walk-in cooler or freezer that was manufactured before January 1, 2009. | Yes | Date of Manufacture | Manufacturer date of walk-in cooler? | Date | [7 empty] | Must be before 1/1/2009 | QA Checklist | The installation report should list the manufacture date of the Walk-In Cooler | The walk-in must be installed prior to 1/1/2009 to be eligible | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-12 | Kenny Liljestrom |  | Add | 36
0 | SWCR005 | 1 | Auto Closer For Refrigerated Storage Door | B | Any | Any | EECP | 4 | The automatic closer must be installed on a walk-in cooler or freezer that was manufactured before January 1, 2009. | Yes | Date of Manufacture | Manufacturer date of walk-in freezer? | Date | [7 empty] | Must be before 1/1/2009 | QA Checklist | The installation report should list the manufacture date of the Walk-In Freezer | The walk-in must be installed prior to 1/1/2009 to be eligible | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-12 | Kenny Liljestrom |  | Add | 37
0 | SWCR005 | 1 | Auto Closer For Refrigerated Storage Door | Any | Any | Any | EECP | 5 | The measure case is specified as the installation of an automatic door closer on a walk-in cooler or a walk-in freezer door that was not previously equipped with one. | Yes | Existing Auto Close | Did the walk-in cooler or freezer have an existing automatic closer installed? | Drop Down List | Yes;No | [6 empty] | Must be 'No'' | QA Checklist | The installation report should indicate whether or not the walk-in had any existing controls for the door closer; photographs of existing conditions can also verify the existence of any controls | There should not be any previous controls installed on the walk-in door | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWCR005 | 1 | Auto Closer For Refrigerated Storage Door | Any | Any | Any | EECP | 6 | The automatic door closer must be installed on the main insulated opaque door(s) of an existing walk-in cooler or freezer. | Yes | Location of Install | Was the automatic door closer installed on the main insulated opaque door(s) of an existing walk-in cooler or freezer? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Locate the main entry door for the walk-in | The door must be opaque (not glass or see through) and act as the main entry door for the walk-in cooler or freezer | QA Checklist | Photographs of the proposed conditions showing the controller installed on a main entry door (large opaque door, not see through, used to access the walk-in) | The photographs should show the doors as being opaque and in a location that would indicate it is the main entry door for the walk-in |  | 2021-08-12 | Kenny Liljestrom |  | Add | 118
0 | SWCR005 | 1 | Auto Closer For Refrigerated Storage Door | Any | Any | Any | EECP | 7 | The automatic door closer must firmly close the door when it is within one inch of full closure. | Yes | Firm Close | Does the automatic door closer firmly close the door when it is within one inch of full closure? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Open the door to the walk-in to test the functionality of the auto closer | When the door is closing observe the auto closure and note if the door shuts firmly when closed to about 1-inch of full closure | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-12 | Kenny Liljestrom |  | Add | 96
1 | SWCR005 | 2 | Auto Closer For Refrigerated Storage Door | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | If accessible, photograph the controller nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-11 | Kenny Liljestrom |  |  | 12
1 | SWCR005 | 2 | Auto Closer For Refrigerated Storage Door | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | If accessible, photograph the controller nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-11 | Kenny Liljestrom |  |  | 5
1 | SWCR005 | 2 | Auto Closer For Refrigerated Storage Door | A | Any | Any | EECP | 3 | The automatic closer must be installed on a walk-in cooler or freezer that was manufactured before January 1, 2009. | Yes | Date of Manufacture | Manufacturer date of walk-in cooler? | Date | [7 empty] | Must be before 1/1/2009 | QA Checklist | The installation report should list the manufacture date of the Walk-In Cooler | The walk-in must be installed prior to 1/1/2009 to be eligible | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-11 | Kenny Liljestrom |  |  | 36
1 | SWCR005 | 2 | Auto Closer For Refrigerated Storage Door | B | Any | Any | EECP | 4 | The automatic closer must be installed on a walk-in cooler or freezer that was manufactured before January 1, 2009. | Yes | Date of Manufacture | Manufacturer date of walk-in freezer? | Date | [7 empty] | Must be before 1/1/2009 | QA Checklist | The installation report should list the manufacture date of the Walk-In Freezer | The walk-in must be installed prior to 1/1/2009 to be eligible | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-11 | Kenny Liljestrom |  |  | 37
1 | SWCR005 | 2 | Auto Closer For Refrigerated Storage Door | Any | Any | Any | EECP | 5 | The measure case is specified as the installation of an automatic door closer on a walk-in cooler or a walk-in freezer door that was not previously equipped with one. | Yes | Existing Auto Close | Did the walk-in cooler or freezer have an existing automatic closer installed? | Drop Down List | Yes;No | [6 empty] | Must be 'No'' | QA Checklist | The installation report should indicate whether or not the walk-in had any existing controls for the door closer; photographs of existing conditions can also verify the existence of any controls | There should not be any previous controls installed on the walk-in door | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-11 | Kenny Liljestrom |  |  | 78
1 | SWCR005 | 2 | Auto Closer For Refrigerated Storage Door | Any | Any | Any | EECP | 6 | The automatic door closer must be installed on the main insulated opaque door(s) of an existing walk-in cooler or freezer. | Yes | Location of Install | Was the automatic door closer installed on the main insulated opaque door(s) of an existing walk-in cooler or freezer? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Locate the main entry door for the walk-in | The door must be opaque (not glass or see through) and act as the main entry door for the walk-in cooler or freezer | QA Checklist | Photographs of the proposed conditions showing the controller installed on a main entry door (large opaque door, not see through, used to access the walk-in) | The photographs should show the doors as being opaque and in a location that would indicate it is the main entry door for the walk-in |  | 2021-11-11 | Kenny Liljestrom |  |  | 118
1 | SWCR005 | 2 | Auto Closer For Refrigerated Storage Door | Any | Any | Any | EECP | 7 | The automatic door closer must firmly close the door when it is within one inch of full closure. | Yes | Firm Close | Does the automatic door closer firmly close the door when it is within one inch of full closure? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Open the door to the walk-in to test the functionality of the auto closer | When the door is closing observe the auto closure and note if the door shuts firmly when closed to about 1-inch of full closure | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-11 | Kenny Liljestrom |  |  | 96
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 12
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 5
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 3 | - | Yes | Model Number | Model Number | Text Box | [8 empty] | - | - | - | - | - | - | request to retire property | 2021-06-10 | Kenny Liljestrom |  | Add | 12
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 3 | This measure is applicable to any existing non-residential building type in commercial sector, and the vintage categories listed below: Prior to 1978 (represented by typical year “1975”) 1978 through 1992 (“1985”) 1993 through 2001 (“1996”) 2002 through 2005 (“2003”) 2006 through 2009 (“2007”) 2010 through 2013 (“2011”) In addition, the following installations are ineligible: New construction installations | Yes | Building vintage | Select the most appropriate building vintage | Drop Down List | Prior to 1978;1978 - 1992;1993 - 2001;2002 - 2005;2006 - 2009;2010 - 2013;2014 - Present; | [6 empty] | Must not be '2014 - Present' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload Can be configured at the enrollment level | 2021-08-06 | Kenny Liljestrom |  | Add | 44
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 4 | - | Yes | Building vintage | Building Vintage | Text Box | [8 empty] | - | - | - | - | - | - | Legacy property should be removed, replaced by above property | 2021-06-10 | Kenny Liljestrom |  | Add | 16
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 4 | This measure is applicable to any existing non-residential building type in commercial sector, and the vintage categories listed below: Prior to 1978 (represented by typical year “1975”) 1978 through 1992 (“1985”) 1993 through 2001 (“1996”) 2002 through 2005 (“2003”) 2006 through 2009 (“2007”) 2010 through 2013 (“2011”) The program should collect and verify the vintage of the building and the refrigeration multiplex system. The offerings are ineligible for multiplex systems majorly upgraded or installed after July 1, 2014 since the Title-24 code mandates the floating controls since July 1, 2014. | Yes | Multiplex System Vintage | Select the most appropriate Multiplex compressor system vintage | Drop Down List | Prior to 1978;1978 - 1992;1993 - 2001;2002 - 2005;2006 - 2009;2010 - 2013;2014 - Present; | [6 empty] | Must not be '2014 - Present' | Inspections | Photograph the nameplate of the refrigeration system; the nameplate may be difficult to locate on the multiplex systems because most are custom made, start by looking at the compressor then the entire system to try and locate a nameplate; you will want to capture the serial number or date of manufacture | The value listed in EECP should match and be identifiable on the equipment nameplate; you may need to use a serial number lookup table online or pass the information to the processing team for them to review and approve this measure property; The equipment must not have been constructed between 2014 and the present year | QA Checklist | Using photographs of the multiplex nameplate, try to identify the equipment age via the serial number or date of manufacture (if listed) | The equipment must not have been constructed between 2014 and the present year |  | 2021-06-10 | Kenny Liljestrom |  | Add | 63
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 5 | - | Yes | Refrigeration multiplex system | Refrigeration Multiplex System | Text Box | [8 empty] | - | - | - | - | - | - | Legacy property should be removed, replaced by 'Multiplex System Vintage' | 2021-06-10 | Kenny Liljestrom |  | Add | 30
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | QA Checklist | 5 | Products cannot be used in conjunction with measures that already incorporate floating head pressure controls. | Yes |  | Measure installed in conjunction with floating head pressure controls? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | QA Checklist | Use the submitted installation report or EECP Double Dip to check for measures installed at the site | This measure cannot be used in conjunction with floating head pressure controls | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 70
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | QA Checklist | 6 | In addition, the following installations are ineligible: Projects that only reprogram a controller; new hardware must be installed. | Yes |  | Is new equipment/hardware being installed (i.e. not reprogramming an existing controller)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to check if the equipment being installed is brand new | The equipment needs to be new (not used or rebuilt) | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 90
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 7 | The controls only apply to refrigeration systems having multiplex compressor systems with existing control of the SCT at a fixed setpoint. The controls are added to float head pressure down to a lower pressure when conditions permit (i.e., changes control from fixed setpoint to floating setpoint). | Yes | Setpoint Controls | Does the existing refrigeration system have a multiplex compressor system with saturated condensing temperature (SCT) controls at a fixed setpoint? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the installation report to check for a demonstration or proof the existing system uses a fixed setpoint to control the condensing temperature | The existing system must operate with fixed saturation setpoint controls | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Should be used to replace 'Refrigeration multiplex system' | 2021-06-10 | Kenny Liljestrom |  | Add | 147
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 8 | The new SCT setpoint must follow the ambient temperature by controlling condenser fans with variable-speed drives or by staging condenser fans. | Yes | Setpoint Adjust | Does the new saturated condensing temperature (SCT) setpoint adjust based on the ambient temperature by controlling condenser fans with variable-speed drives or by staging condenser fans? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Review the installation report or manufacturer spec sheet to check for how the SCT is controlled | The installation report or manufacturer spec sheet must indicate the new SCT setpoint follows the ambient temperature by controlling condenser fans with variable-speed drives or by staging condenser fans | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 187
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 9 | In addition, the following installations are ineligible: Any improvements that will increase system energy use. | Yes |  | Have any improvements been made that would increase system energy use? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 70
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 10 | Additionally, the calculation of the design cooling load (tons) is to be based on connected display cases, walk-in coolers and freezers, cooled storage, and prep areas only. Sub-cooler loads and air conditioning loads are ineligible for consideration. | Yes | Design tons | Design cooling load for connected display cases, walk-in coolers and freezers, cooled storage, and prep areas only (sub-coolers and air conditioning loads ineligible) (tons) | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-10 | Kenny Liljestrom |  | Add | 173
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Kenny Liljestrom |  |  | 12
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Kenny Liljestrom |  |  | 5
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 3 | This measure is applicable to any existing non-residential building type in commercial sector, and the vintage categories listed below: Prior to 1978 (represented by typical year “1975”) 1978 through 1992 (“1985”) 1993 through 2001 (“1996”) 2002 through 2005 (“2003”) 2006 through 2009 (“2007”) 2010 through 2013 (“2011”) In addition, the following installations are ineligible: New construction installations | No |  | Select the most appropriate building vintage | Drop Down List | Prior to 1978;1978 - 1992;1993 - 2001;2002 - 2005;2006 - 2009;2010 - 2013;2014 - Present; | [6 empty] | Must not be '2014 - Present' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-01-07 | Kenny Liljestrom | Property removed, new construction installations not eligible to be configured at enrollment level |  | 44
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 3 | This measure is applicable to any existing non-residential building type in commercial sector, and the vintage categories listed below: Prior to 1978 (represented by typical year “1975”) 1978 through 1992 (“1985”) 1993 through 2001 (“1996”) 2002 through 2005 (“2003”) 2006 through 2009 (“2007”) 2010 through 2013 (“2011”) In addition, the following installations are ineligible: New construction installations | Yes |  | Building vintage | None | [7 empty] | Construction year must be < current year (new construction not eligible) | - | - | - | - | - | - | This property to be configured at the enrollment level | 2022-01-07 | Kenny Liljestrom |  |  | 16
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 4 | This measure is applicable to any existing non-residential building type in commercial sector, and the vintage categories listed below: Prior to 1978 (represented by typical year “1975”) 1978 through 1992 (“1985”) 1993 through 2001 (“1996”) 2002 through 2005 (“2003”) 2006 through 2009 (“2007”) 2010 through 2013 (“2011”) The program should collect and verify the vintage of the building and the refrigeration multiplex system. The offerings are ineligible for multiplex systems majorly upgraded or installed after July 1, 2014 since the Title-24 code mandates the floating controls since July 1, 2014. | Yes | Multiplex System Vintage | Select the most appropriate Multiplex compressor system vintage | Drop Down List | Prior to 1978;1978 - 1992;1993 - 2001;2002 - 2005;2006 - 2009;2010 - 2013;2014 - Present; | [6 empty] | Must not be '2014 - Present' | Inspections | Photograph the nameplate of the refrigeration system; the nameplate may be difficult to locate on the multiplex systems because most are custom made, start by looking at the compressor then the entire system to try and locate a nameplate; you will want to capture the serial number or date of manufacture | The value listed in EECP should match and be identifiable on the equipment nameplate; you may need to use a serial number lookup table online or pass the information to the processing team for them to review and approve this measure property; The equipment must not have been constructed between 2014 and the present year | QA Checklist | Using photographs of the multiplex nameplate, try to identify the equipment age via the serial number or date of manufacture (if listed) | The equipment must not have been constructed between 2014 and the present year |  | 8/19/2021 | Kenny Liljestrom |  |  | 63
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | QA Checklist | 5 | Products cannot be used in conjunction with measures that already incorporate floating head pressure controls. | Yes |  | Measure installed in conjunction with floating head pressure controls? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | QA Checklist | Use the submitted installation report or EECP Double Dip to check for measures installed at the site | This measure cannot be counted towards other measures like installing a new chiller at the site; check the EECP double dip report to check for claims of a new chiller being installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 8/19/2021 | Kenny Liljestrom |  |  | 70
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 6 | In addition, the following installations are ineligible: Projects that only reprogram a controller; new hardware must be installed. | Yes |  | Is new equipment/hardware being installed (i.e. not reprogramming an existing controller)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to check if the equipment being installed is brand new | The equipment needs to be new (not used or rebuilt) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 8/19/2021 | Kenny Liljestrom |  |  | 90
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 7 | The controls only apply to refrigeration systems having multiplex compressor systems with existing control of the SCT at a fixed setpoint. The controls are added to float head pressure down to a lower pressure when conditions permit (i.e., changes control from fixed setpoint to floating setpoint). | Yes | Setpoint Controls | Does the existing refrigeration system have a multiplex compressor system with saturated condensing temperature (SCT) controls at a fixed setpoint? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the installation report to check for a demonstration or proof the existing system uses a fixed setpoint to control the condensing temperature | The existing system must operate with fixed saturation setpoint controls | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Kenny Liljestrom |  |  | 147
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 8 | The new SCT setpoint must follow the ambient temperature by controlling condenser fans with variable-speed drives or by staging condenser fans. | Yes | Setpoint Adjust | Does the new saturated condensing temperature (SCT) setpoint adjust based on the ambient temperature by controlling condenser fans with variable-speed drives or by staging condenser fans? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Review the installation report or manufacturer spec sheet to check for how the SCT is controlled | The installation report or manufacturer spec sheet must indicate the new SCT setpoint follows the ambient temperature by controlling condenser fans with variable-speed drives or by staging condenser fans | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Kenny Liljestrom |  |  | 187
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | - | 9 | In addition, the following installations are ineligible: Any improvements that will increase system energy use. | No |  | Have any improvements been made that would increase system energy use? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-01-07 | Kenny Liljestrom | Worked with Program Ops to justify removal of property. Since the multiplex system vintage is being captured, capactiy expansion will result in disqualification and added energy use in unlikely. |  | 70
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any | EECP | 10 | Additionally, the calculation of the design cooling load (tons) is to be based on connected display cases, walk-in coolers and freezers, cooled storage, and prep areas only. Sub-cooler loads and air conditioning loads are ineligible for consideration. | Yes | Design tons | Design cooling load for connected display cases, walk-in coolers and freezers, cooled storage, and prep areas only (sub-coolers and air conditioning loads ineligible) (tons) | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 8/19/2021 | Kenny Liljestrom |  |  | 173
0 | SWCR010 | 1 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 12
0 | SWCR010 | 1 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 5
0 | SWCR010 | 1 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any | EECP | 3 | Measure Description | Yes | Insulation on Bare Suction Pipes | Insulation is being installed on bare suction pipes for medium temperature, walk-in coolers | Drop Down List | [7 empty] | Must be Yes | - | - | - | - | - | - | Request to remove property, in measure description | 2021-08-10 | Kenny Liljestrom |  | Add | 91
0 | SWCR010 | 1 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any | EECP | 4 | The eligibility requirements are as follows: • The refrigeration suction pipe on existing equipment must be no more than 1-5/8 inches in diameter. • This measure is applicable to bare suction pipes insulated with closed-cell nitrite rubber or equivalent with at least ¾-inch for medium-temperature and 1-inch for low-temperature systems. • Insulation R-values must be greater than or equal to R-3.2 for medium-temperature cooler pipes. • Insulation R-values must be greater than or equal to R-4.3 low-temperature freezer pipes. | Yes | Size | Refrigeration suction pipe diameter on existing equipment in inches | Numeric Value | [7 empty] | Must be <= 1-5/8 inches | QA Checklist | Use the manufacturer specification sheet or installation report to determine the thickness of the insulation | The insulation thickness should be greater than 1-5/8" and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 67
0 | SWCR010 | 1 | Bare Suction Pipe Insulation, Commercial | A | Any | Any | EECP | 5 | The eligibility requirements are as follows: • The refrigeration suction pipe on existing equipment must be no more than 1-5/8 inches in diameter. • This measure is applicable to bare suction pipes insulated with closed-cell nitrite rubber or equivalent with at least ¾-inch for medium-temperature and 1-inch for low-temperature systems. • Insulation R-values must be greater than or equal to R-3.2 for medium-temperature cooler pipes. • Insulation R-values must be greater than or equal to R-4.3 low-temperature freezer pipes. | Yes | R-value Installed Greater | Is the insulation R-values of the installed insulation greater than or equal to R-3.2? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Use the manufacturer specification sheet or installation report to determine the insulation R-Value | The insulation R-Value should be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 86
0 | SWCR010 | 1 | Bare Suction Pipe Insulation, Commercial | B | Any | Any | EECP | 6 | The eligibility requirements are as follows: • The refrigeration suction pipe on existing equipment must be no more than 1-5/8 inches in diameter. • This measure is applicable to bare suction pipes insulated with closed-cell nitrite rubber or equivalent with at least ¾-inch for medium-temperature and 1-inch for low-temperature systems. • Insulation R-values must be greater than or equal to R-3.2 for medium-temperature cooler pipes. • Insulation R-values must be greater than or equal to R-4.3 low-temperature freezer pipes. | Yes | R-value Installed Greater | Is the insulation R-values of the installed insulation greater than or equal to R-4.3? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Use the manufacturer specification sheet or installation report to determine the insulation R-Value | The insulation R-Value should be >= 4.3 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 86
1 | SWCR010 | 2 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 12
1 | SWCR010 | 2 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 5
1 | SWCR010 | 2 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any | EECP | 3 | Measure Description | No | Insulation on Bare Suction Pipes | Insulation is being installed on bare suction pipes for medium temperature, walk-in coolers | Drop Down List | [7 empty] | Must be Yes | - | - | - | - | - | - | Request to remove property, in measure description | 2021-08-10 | Kenny Liljestrom |  | Add | 91
1 | SWCR010 | 2 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any | EECP | 3 | Measure Description | No | PreExisting Bare Suction Pipe | Is the pre-existing condition bare suction pipe on a low-temperature, walk-in freezer? | Drop Down List | [7 empty] | Must be Yes | - | - | - | - | - | - | Request to remove property, in measure description | 2021-08-10 | Kenny Liljestrom |  |  | 86
1 | SWCR010 | 2 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any | EECP | 4 | The eligibility requirements are as follows: • The refrigeration suction pipe on existing equipment must be no more than 1-5/8 inches in diameter. • This measure is applicable to bare suction pipes insulated with closed-cell nitrite rubber or equivalent with at least ¾-inch for medium-temperature and 1-inch for low-temperature systems. • Insulation R-values must be greater than or equal to R-3.2 for medium-temperature cooler pipes. • Insulation R-values must be greater than or equal to R-4.3 low-temperature freezer pipes. | Yes | Size | Refrigeration suction pipe diameter on existing equipment in inches | Numeric Value | [7 empty] | Must be <= 1-5/8 inches | QA Checklist | Use the manufacturer specification sheet or installation report to determine the thickness of the insulation | The insulation thickness should be greater than 1-5/8" and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 67
1 | SWCR010 | 2 | Bare Suction Pipe Insulation, Commercial | A | Any | Any | EECP | 5 | The eligibility requirements are as follows: • The refrigeration suction pipe on existing equipment must be no more than 1-5/8 inches in diameter. • This measure is applicable to bare suction pipes insulated with closed-cell nitrite rubber or equivalent with at least ¾-inch for medium-temperature and 1-inch for low-temperature systems. • Insulation R-values must be greater than or equal to R-3.2 for medium-temperature cooler pipes. • Insulation R-values must be greater than or equal to R-4.3 low-temperature freezer pipes. | Yes | R-value Installed Greater | Is the insulation R-values of the installed insulation greater than or equal to R-3.2? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Use the manufacturer specification sheet or installation report to determine the insulation R-Value | The insulation R-Value should be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 86
1 | SWCR010 | 2 | Bare Suction Pipe Insulation, Commercial | B | Any | Any | EECP | 6 | The eligibility requirements are as follows: • The refrigeration suction pipe on existing equipment must be no more than 1-5/8 inches in diameter. • This measure is applicable to bare suction pipes insulated with closed-cell nitrite rubber or equivalent with at least ¾-inch for medium-temperature and 1-inch for low-temperature systems. • Insulation R-values must be greater than or equal to R-3.2 for medium-temperature cooler pipes. • Insulation R-values must be greater than or equal to R-4.3 low-temperature freezer pipes. | Yes | R-value Installed Greater | Is the insulation R-values of the installed insulation greater than or equal to R-4.3? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Use the manufacturer specification sheet or installation report to determine the insulation R-Value | The insulation R-Value should be >= 4.3 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 86
0 | SWCR015 | 1 | Medium-Temperature Case Doors | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 12
0 | SWCR015 | 1 | Medium-Temperature Case Doors | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 5
0 | SWCR015 | 1 | Medium-Temperature Case Doors | Any | Any | Any | EECP | 3 | The retrofit of glass doors, or glass doors with LED lights, for a medium-temperature, open-vertical, refrigerated display case must be added to an existing open-vertical, medium temp display case. The complete removal of the existing display case and replacing it with a new case with glass doors is not eligible | Yes |  | Are the glass doors being installed on an existing vertical display case? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | Photograph and observe the display case and determine the case type (vertical, horizontal, coffin, etc.) | To qualify, the display case with the retrofitted doors must be a vertical display case | QA Checklist | Check EECP for photographs of the display cases; or check the invoice and determine if the entire case was replaced | The photograph should show glass doors on the display case; or the invoice should only show costs for the doors and hardware, not an entire case replacement | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 73
0 | SWCR015 | 1 | Medium-Temperature Case Doors | Any | Any | Any | QA Checklist | 4 | In addition to retrofitting the doors and door frames, the measure may require changes to the refrigeration system serving the affected display case(s). These changes may include but are not limited to: replacing the expansion valve and/or evaporator pressure regulating valve, adjusting the evaporator temperature/pressure set point, resizing refrigeration piping, replacing the flood back valve on the condenser, resizing the coil/piping on applicable heat reclaim systems, and replacing or removing compressors. These potential changes stem from the significant reduction in the overall refrigeration load. Due to the complexity in determining which system alterations will be required at a site to maintain optimum system performance, a refrigeration contractor with design experience should be consulted before proceeding with the retrofit. | Yes |  | Was a design consultant used for major refrigeration system upgrades as a result of this measure? | Drop Down List | Yes;No;N/A; | [6 empty] | Must be 'Yes' or 'N/A' | QA Checklist | Review submitted invoice to determine if the Medium Case doors are being purchased with a new case | The doors must be listed on the invoice not in conjunction with a new/replacement case; The tmeasure requires the doors to be a standalone measure not a case replacement | - | - | - |  | 2022-04-12 | Kenny Liljestrom | System of record updated from EECP to QA Checklist per request of Programs team who indicated the property could be cheked via invoice. | Add | 97
0 | SWCR015 | 1 | Medium-Temperature Case Doors | Any | Any | Any | EECP | 5 | Anti-sweat heat (ASH) may not be present in the glass doors or door mounting. (Two out of three manufacturers stated that their products did not contain ASH in the door or mullion. Thus, it was decided to specifically prohibit door and frame heat, as it does not appear necessary in medium-temperature applications.) | No | Doors Anti Sweat Heat Controls | Do the retrofit doors have ASH controls installed? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | QA Checklist | Use the submitted manufacturer spec sheet to determine whether the retrofit doors have Anti-Sweat Heater (ASH) controls installed | The retrofit doors must NOT have ASH controls already installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-04-12 | Kenny Liljestrom | Measure property removed, the measure package does not say this is an absolute requirement, it just suggests a design consultant be used. Worked with programs team to remove property. | Add | 50
0 | SWCR015 | 1 | Medium-Temperature Case Doors | B | Any | Any | EECP | 6 | Total lighting power in the measure case may not exceed total lighting power in the base case (Several manufacturers interviewed stated that most retrofits include a switch to more efficient LED case lighting, but not an overall increase in lighting power density.) | Yes | Power Density | Has the lighting power density increased with a replacement or retrofit of the LED lighting systems in the display case? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-10 | Kenny Liljestrom |  | Add | 120
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 12
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 5
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any | QA Checklist | 3 | Eligible Building Types This measure is applicable for the following existing building types: Education – University, Health/Medical – Hospital, Manufacturing – Biotech, and Manufacturing – Pharmaceuticals. | Yes | Building Type | Building Type | Drop Down List | Education – University;Health/Medical – Hospital;Manufacturing – Biotech;Manufacturing – Pharmaceuticals;Other; | [6 empty] | Must not be 'Other' | QA Checklist | Verify the building type is Education – University; Health/Medical – Hospital; Manufacturing – Biotech; or Manufacturing – Pharmaceuticals | The building type must be Education – University; Health/Medical – Hospital; Manufacturing – Biotech; or Manufacturing – Pharmaceuticals | Inspections | During inspection verify building type | The building type must be Education – University; Health/Medical – Hospital; Manufacturing – Biotech; or Manufacturing – Pharmaceuticals |  | 8/19/2021 | Keith Valenzuela |  | Add | 13
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any | QA Checklist | 4 | Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | Freezer Type | Freezer Type | Drop Down List | Upright;Coffin;Other; | [6 empty] | Must be 'Upright' | QA Checklist | Use the make and model number listed on the invoice/EECP and verify freezer type. | The freezer type must be "Upright" | Inspections | During inspection verify freezer type | The freezer type must be "Upright" |  | 8/19/2021 | Keith Valenzuela |  | Add | 12
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any | EECP | 5 | Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | Setpoint storage temperature range | Is the setpoint storage temperature range between -70 °C and -80 °C (-94 °F and -112 °F)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | During inspection verify freezer temperature | Freezer temperature must be between -70 °C and -80 °C (-94 °F and -112 °F)? | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 89
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any | QA Checklist | 6 | Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | ENERGY STAR Qualified? | Does the freezer have an ENERGY STAR certification? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the make and model number listed on the invoice/EECP and cross check the EnergyStar database to determine if the product is listed as EnergyStar qualified | The listed make and model in EECP should be included in the EnergyStar database | - | None | None |  | 8/19/2021 | Keith Valenzuela |  | Add | 51
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any | QA Checklist | 7 | Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | Daily Energy Use | Maximum daily energy consumption(MDEC) (kWh/day/ft3) | Numeric Value | [7 empty] | If "Does the freezer have an ENERGY STAR verification?" is 'No' then <= 0.55 | QA Checklist | Use the make and model number listed on the invoice/EECP and verify freezer energy use (kWh/day/ft3) | Freezer energy use must be <= 0.55 kWh/day/ft3 | - | None | None |  | 8/19/2021 | Keith Valenzuela |  | Add | 52
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | A | Any | Any | EECP | 8 | Refrig-Freezer-High Efficiency Ultra-Low Temperature (ULT, -80 °C) Freezers, 15 to <24 ft3 | Yes | Freezer Volume (ft^3) | Volume of freezer in cubic feet? | Numeric Value | [7 empty] | >= 15 and < 24 | QA Checklist | Use the make and model number listed on the invoice/EECP and verify freezer volume. | Freezer volume must be >= 15 cubic feet and < 24 cubic feet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 32
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | B | Any | Any | EECP | 9 | Refrig-Freezer-High Efficiency Ultra-Low Temperature (ULT, -80 °C) Freezers, 24 to 29 ft3 | Yes | Freezer Volume (ft^3) | Volume of freezer in cubic feet? | Numeric value | [7 empty] | 24 ≤ and ≤ 29 | QA Checklist | Use the make and model number listed on the invoice/EECP and verify freezer volume. | Freezer volume must be 24 cubic feet ≤ and ≤ 29 cubic feet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 32
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 12
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 5
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any | QA Checklist | 3 | Eligible Building Types This measure is applicable for the following existing building types: Education – University, Health/Medical – Hospital, Manufacturing – Biotech, and Manufacturing – Pharmaceuticals. | Yes | Building Type | Building Type | Drop Down List | Education – University;Health/Medical – Hospital;Manufacturing – Biotech;Manufacturing – Pharmaceuticals;Other; | [6 empty] | Must not be 'Other' | QA Checklist | Verify the building type is Education – University; Health/Medical – Hospital; Manufacturing – Biotech; or Manufacturing – Pharmaceuticals | The building type must be Education – University; Health/Medical – Hospital; Manufacturing – Biotech; or Manufacturing – Pharmaceuticals | Inspections | During inspection verify building type | The building type must be Education – University; Health/Medical – Hospital; Manufacturing – Biotech; or Manufacturing – Pharmaceuticals |  | 8/19/2021 | Keith Valenzuela |  | Add | 13
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any | QA Checklist | 4 | Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | Freezer Type | Freezer Type | Drop Down List | Upright;Coffin;Other; | [6 empty] | Must be 'Upright' | QA Checklist | Use the make and model number listed on the invoice/EECP and verify freezer type. | The freezer type must be "Upright" | Inspections | During inspection verify freezer type | The freezer type must be "Upright" |  | 8/19/2021 | Keith Valenzuela |  | Add | 12
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any | EECP | 5 | Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | Setpoint storage temperature range | Is the setpoint storage temperature range between -70 °C and -80 °C (-94 °F and -112 °F)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | During inspection verify freezer temperature | Freezer temperature must be between -70 °C and -80 °C (-94 °F and -112 °F)? | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 89
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any | QA Checklist | 6 | Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | ENERGY STAR Qualified? | Does the freezer have an ENERGY STAR certification? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the make and model number listed on the invoice/EECP and cross check the EnergyStar database to determine if the product is listed as EnergyStar qualified | The listed make and model in EECP should be included in the EnergyStar database | - | None | None |  | 8/19/2021 | Keith Valenzuela |  | Add | 51
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any | QA Checklist | 7 | Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | Daily Energy Use | Maximum daily energy consumption(MDEC) (kWh/day/ft3) | Numeric Value | [7 empty] | If "Does the freezer have an ENERGY STAR verification?" is 'No' then <= 0.55 | QA Checklist | Use the make and model number listed on the invoice/EECP and verify freezer energy use (kWh/day/ft3) | Freezer energy use must be <= 0.55 kWh/day/ft3 | - | None | None |  | 8/19/2021 | Keith Valenzuela |  | Add | 52
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | A | Any | Any | EECP | 8 | Refrig-Freezer-High Efficiency Ultra-Low Temperature (ULT, -80 °C) Freezers, 15 to <24 ft3 | Yes | Freezer Volume (ft^3) | Volume of freezer in cubic feet? | Numeric Value | [7 empty] | >= 15 and < 24 | QA Checklist | Use the make and model number listed on the invoice/EECP and verify freezer volume. | Freezer volume must be >= 15 cubic feet and < 24 cubic feet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 32
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | B | Any | Any | EECP | 9 | Refrig-Freezer-High Efficiency Ultra-Low Temperature (ULT, -80 °C) Freezers, 24 to 29 ft3 | Yes | Freezer Volume (ft^3) | Volume of freezer in cubic feet? | Numeric value | [7 empty] | 24 ≤ and ≤ 29 | QA Checklist | Use the make and model number listed on the invoice/EECP and verify freezer volume. | Freezer volume must be 24 cubic feet ≤ and ≤ 29 cubic feet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 32
1 | SWCR018 | 2 | Reach-In Refrigerator or Freezer, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-09 | Kenny Liljestrom |  | Add | 12
1 | SWCR018 | 2 | Reach-In Refrigerator or Freezer, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-09 | Kenny Liljestrom |  | Add | 5
1 | SWCR018 | 2 | Reach-In Refrigerator or Freezer, Commercial | Any | Any | Any | EECP | 3 | No requirement listed | Yes |  | New Equipment | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Collect the equipment invoice for the product | The invoice should list the equipment as new (i.e. not used, rebuilt. or leased) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 13
1 | SWCR018 | 2 | Reach-In Refrigerator or Freezer, Commercial | Any | Any | Any | EECP | 4 | Eligible products include ENERGY STAR®-qualified commercial reach-in refrigerators and freezers that replace a standard efficiency unit of the same configuration and capacity. | Yes | Energy Star Qualified | ENERGY STAR Qualified? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the make and model number listed on the invoice/EECP and cross check the EnergyStar database to determine if the product is listed as EnergyStar qualified | The listed make and model in EECP should be included in the EnergyStar database | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-09 | Kenny Liljestrom |  | Add | 22
1 | SWCR018 | 2 | Reach-In Refrigerator or Freezer, Commercial | Any | Any | Any | EECP | 5 | Good to have | Yes |  | Volume of reach-in unit (ft3) | Numeric Value | [8 empty] | QA Checklist | Use the EnergyStar database to capture the volume of the specified equipment | The EnergyStar database value for the volume should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 29
1 | SWCR018 | 2 | Reach-In Refrigerator or Freezer, Commercial | Any | Any | Any | EECP | 6 | Units with remote refrigeration systems do not qualify and used or rebuilt equipment is not eligible. | Yes | Remote Refrigeration System | Does the installed unit have a remote refrigeration system? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-09 | Kenny Liljestrom |  | Add | 59
1 | SWCR018 | 2 | Reach-In Refrigerator or Freezer, Commercial | Any | Any | Any | EECP | 7 | Eligible products include ENERGY STAR®-qualified commercial reach-in refrigerators and freezers that replace a standard efficiency unit of the same configuration and capacity. | Yes | New Same as Existing | Is the existing unit a standard efficiency unit of the same configuration and capacity? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-09 | Kenny Liljestrom |  | Add | 87
0 | SWCR019 | 1 | Low-Temperature Coffin to Reach-in Display Case Conversion | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 12
0 | SWCR019 | 1 | Low-Temperature Coffin to Reach-in Display Case Conversion | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 5
0 | SWCR019 | 1 | Low-Temperature Coffin to Reach-in Display Case Conversion | Any | Any | Any | EECP | 3 | Equipment must be new | Yes | New Equipment | New Equipment | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 13
0 | SWCR019 | 1 | Low-Temperature Coffin to Reach-in Display Case Conversion | Any | Any | Any | EECP | 4 | All coffin replacements with a reach-in display case must meet the specifications in the Measure Case Description. The measure is applicable to replace any existing coffin that is less than or equal to code: • If the display width is less than or equal to 3 feet, the coffin must be replaced by a reach-in case that is ⅟4 of the total length of the coffins or less. • If the display width is greater than 3 feet, the coffin must be replaced by a reach-in case that is ⅓ of the total length of the coffin or less. | Yes | Existing Unit Width | Is the existing unit a low temp coffin with a display width greater than 3 feet? | Drop Down List | Yes;No | [6 empty] | Must be Yes | Inspections | Check the length of the newly installed case, you can do this by estimating, no need for actual measurements | The case needs to be greater than 3-feet in length | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 80
0 | SWCR019 | 1 | Low-Temperature Coffin to Reach-in Display Case Conversion | Any | Any | Any | EECP | 5 | All coffin replacements with a reach-in display case must meet the specifications in the Measure Case Description. The measure is applicable to replace any existing coffin that is less than or equal to code: • If the display width is less than or equal to 3 feet, the coffin must be replaced by a reach-in case that is ⅟4 of the total length of the coffins or less. • If the display width is greater than 3 feet, the coffin must be replaced by a reach-in case that is ⅓ of the total length of the coffin or less. | Yes | Existing Unit Length | Is the installed unit a reach-in case that is "1/4" of the total length of the coffin or less? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-10 | Kenny Liljestrom |  | Add | 94
0 | SWCR019 | 1 | Low-Temperature Coffin to Reach-in Display Case Conversion | Any | Any | Any | EECP | 6 | The replacement case must include triple-pane doors with low or no anti-sweat heat or anti-sweat-heat controls. | Yes | Doors Anti Sweat Heat Controls | Does the installed case include triple-pane doors with low or no anti-sweat heat or anti-sweat-heat controls? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-10 | Kenny Liljestrom |  | Add | 109
1 | SWCR020 | 1 | Medium-Temperature Open Display Case Retrofit | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 12
1 | SWCR020 | 1 | Medium-Temperature Open Display Case Retrofit | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 5
1 | SWCR020 | 1 | Medium-Temperature Open Display Case Retrofit | Any | Any | Any | EECP | 3 | - | Yes | New Equipment | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property can be removed | 2021-08-04 | Kenny Liljestrom |  | Add | 43
1 | SWCR020 | 1 | Medium-Temperature Open Display Case Retrofit | Any | Any | Any | EECP | 4 | The medium-temperature display case must meet or exceed specifications and efficiency requirements in the Measure Case Description and Code Requirements through the use of a high efficiency evaporator coil. | Yes | Evaporator Coil | Was a medium-temperature, open, vertical refrigerated display case with a high efficiency evaporator coil installed? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-08-04 | Kenny Liljestrom |  | Add | 116
1 | SWCR020 | 1 | Medium-Temperature Open Display Case Retrofit | Any | Any | Any | EECP | 5 | The new display case must replace an existing medium-temperature, open, vertical refrigerated display case of the same style | Yes | New Same as Existing | Was the installed unit the same style as the existing case? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-08-04 | Kenny Liljestrom |  | Add | 60
1 | SWCR020 | 1 | Medium-Temperature Open Display Case Retrofit | Any | Any | Any | EECP | 6 | The manufacturer spec sheet for the new display case must be submitted to the Program for review to confirm eligibility. | Yes | Manufacturer Cut Sheet Submitted | Manufacturer specification sheet submitted with the application? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | Review the EECP documentation and look for the manufacturer spec sheet | A spec sheet must be submitted for this measure to qualify | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-04 | Kenny Liljestrom |  | Add | 64
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-09 | Kenny Liljestrom |  | Add | 12
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-09 | Kenny Liljestrom |  | Add | 5
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any | EECP | 3 | This measure is applicable for supermarkets and grocery stores with stand-alone and/or multiplex compressor racks that provide refrigeration to remote display cases and walk-in coolers/freezers. This measure is applicable to supermarkets and grocery stores with both medium-temperature and low-temperature open multi-deck refrigeration cases. Must replace an existing, open, multi-deck display case with a new reach-in unit with doors, electronically commutated motor (ECM) evaporator fan(s), and LED lighting. | Yes | Display Case Replace | Is an existing, open, multi-deck display case being replaced with a new reach-in unit with doors, electronically commutated motor (ECM) evaporator fan(s), and LED lighting? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | Use the submitted manufacturer spec sheet to validate the display case specifications | the case must consist of: Reach-In type with doors, electronically commutated motor (ECM) evaporator fan(s), and LED lighting | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-09 | Kenny Liljestrom |  | Add | 172
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any | EECP | 4 | Refurbished cases are not eligible unless compliant with the 2012 Federal Efficiency Standards (see Code Requirements). | Yes |  | New Equipment | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | Collect the equipment invoice for the product | The invoice should list the equipment as new (i.e. not used, rebuilt. or leased) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 13
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | A | Any | Any | EECP | 5 | Medium-temperature cases must have no heat in the door. Heat is allowed in the frames of medium temperature cases. | Yes |  | Do the medium-temp cases have heat in the door (answer No if there is only heat in the door frame)? | Drop Down List | Yes;No; | [6 empty] | Must be No | QA Checklist | Use the submitted manufacturer spec sheet to validate if the display case already has heaters or Anti-Sweat Heaters (ASH) controls installed | The display case must NOT have ASH controls installed; heaters in the frame of the case are ok | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 99
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | B | Any | Any | EECP | 6 | Low-temperature case door and frame heaters combined may not consume more than 50 W/ft of case length. | Yes | Doorframe Measurement | Do the low-temperature case door and frame heaters combined consume more than 50 W/ft of case length? | Drop Down List | Yes;No; | [6 empty] | Must be No | QA Checklist | Use the submitted manufacturer spec sheet to validate the energy consumed per linear foot of the case | The energy per linear foot of the display case must be <= 50 W/ft; to calculate this value, take the input energy or total power (W) and divide by the length of the case (ft), this value should be <= 50 W/ft | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-09 | Kenny Liljestrom |  | Add | 101
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any | EECP | 7 | The new case length must be less than or equal to the original case length. | Yes | New Case Length | Is the new case length less than or equal to the original case length? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-09 | Kenny Liljestrom |  | Add | 70
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any | EECP | 8 | This measure is only for display cases served by a remote refrigeration system. | Yes | Remote Refrigeration System | Are the display cases served by a remote refrigeration system? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-09 | Kenny Liljestrom |  | Add | 62
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any | EECP | 9 | Specialty deli cases, custom coolers/freezers, and walk-in boxes with reach-in doors are not eligible. | Yes | Category | Are the display cases any of the following: specialty deli cases, custom coolers/freezers, and walk-in boxes with reach-in doors? | Drop Down List | Yes;No; | [6 empty] | Must be No | QA Checklist | Using the submitted manufacturer spec sheet, check the case type (vertical, horizontal, deli coffin, etc.) | The case type must not be any of the following case types: specialty deli cases, custom coolers/freezers, and walk-in boxes with reach-in doors | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-09 | Kenny Liljestrom |  | Add | 129
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any | EECP | 10 | Display case replacements that are part of large-scale store remodels and any new construction projects should be revised to be custom measures. Large-scale remodels are defined as any project involving 50% of the linear feet of refrigerated casework or 32 linear feet of casework replacements, whichever is less. | Yes | Large Scale Remodel | Large-scale remodels are defined as any project involving 50% of the linear feet of refrigerated casework or 32 linear feet of casework replacements, whichever is less. Are the display case replacements part of large-scale store remodels? | Drop Down List | Yes;No; | [6 empty] | Must be No | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-09 | Kenny Liljestrom |  | Add | 238
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any | EECP | 11 | Salvage, disposal or photographic records of replaced equipment should be part of program application requirements when early replacement or open-to-closed case conversion savings are being utilized to ensure the correct baseline is assumed for these measures. | Yes |  | If customer chose Accelerated Replacement, have written/photographic records disposal been provided? | Drop Down List | Yes;No;N/A; | [6 empty] | Must be Yes or N/A | QA Checklist | Review the EECP submitted files and check for photographic evidence or records indicating the disposal of the existing cases | The display cases need to be properly disposed of with photographic or documented evidence | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 100
1 | SWFS001 | 2 | Convection Oven, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-07 | Kenny Liljestrom |  | Add | 12
1 | SWFS001 | 2 | Convection Oven, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-07 | Kenny Liljestrom |  | Add | 5
1 | SWFS001 | 2 | Convection Oven, Commercial | Any | Any | Any | EECP | 3 | All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. * Half-size gas convection ovens are excluded from ENERGY STAR. | Yes | Energy Star Qualified | ENERGY STAR Qualified? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | Use the make and model number listed on the invoice/EECP and cross check the EnergyStar database to determine if the product is listed as EnergyStar qualified | The listed make and model in EECP should be included in the EnergyStar database | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Needs to be updated to a per measure basis. The requirement says it can be CEC certified as well. | 2021-06-10 | Kenny Liljestrom |  | Add | 22
1 | SWFS001 | 2 | Convection Oven, Commercial | Any | Any | Any | EECP | 3 | Used or rebuilt equipment is not eligible. Half-size gas convection is not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 43
1 | SWFS001 | 2 | Convection Oven, Commercial | A | Any | Any | EECP | 4 | All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. * Half-size gas convection ovens are excluded from ENERGY STAR. | Yes |  | Product qualification method? | Drop Down List | CEC ;EnergyStar;Other; | [6 empty] | Must not be Other | QA Checklist | Use the make and model number listed on the invoice/EECP and cross check the EnergyStar database to determine if the product is listed as EnergyStar qualified | The listed make and model in EECP should be included in the EnergyStar database | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Use to replace 'Energy Star Qualified' | 2021-06-07 | Kenny Liljestrom |  | Add | 29
1 | SWFS001 | 2 | Convection Oven, Commercial | B | Any | Any | EECP | 5 | Measure Description | Yes | Size | Oven Size | Drop Down List | Full;Half | [6 empty] | Must be 'Full' | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the equipment is size (half or full size) | The equipment should be listed as being a full-size | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property needs to be reconfigured in EECP. It is currently configured as 'Half' | 2021-06-10 | Kenny Liljestrom |  | Add | 9
1 | SWFS001 | 2 | Convection Oven, Commercial | A | Any | Any | EECP | 5 | Measure Description | Yes |  | Oven Size | Drop Down List | Full;Half | [6 empty] | Must be 'Half' | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the equipment is size (half or full size) | The equipment should be listed as being a half-size | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 9
1 | SWFS001 | 2 | Convection Oven, Commercial | C | Any | Any | EECP | 5 | Measure Description | Yes |  | Oven Size | Drop Down List | Full;Half | [6 empty] | Must be 'Half' | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the equipment is size (half or full size) | The equipment should be listed as being a half-size | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 9
1 | SWFS001 | 2 | Convection Oven, Commercial | D | Any | Any | EECP | 5 | Measure Description | Yes |  | Oven Size | Drop Down List | Full;Half | [6 empty] | Must be 'Full' | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the equipment is size (half or full size) | The equipment should be listed as being a full-size | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 9
1 | SWFS001 | 2 | Convection Oven, Commercial | A | Any | Any | EECP | 6 | Energy Efficiency Requirements of Commercial Convection Ovens Table | Yes |  | Min Cooking Efficiency (%) | Numeric Value | [7 empty] | If Energy Star Qualified = 'EnergyStar' must be >=71% | QA Checklist | If the product is not listed as being EnergyStar qualified, use the submitted installation report or manufacturer spec sheet to validate the equipment minimum cooking efficiency (%) | The cooking efficiency needs to be >= 71% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 27
1 | SWFS001 | 2 | Convection Oven, Commercial | A | Any | Any | EECP | 7 | All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. | Yes |  | Max Idle Energy Rate (kW) | Numeric Value | [7 empty] | If 'Energy Star Qualified" is 'No' then make active Must be <= 1.0 | QA Checklist | If the product is not listed as being EnergyStar qualified, use the submitted installation report or manufacturer spec sheet to validate the equipment Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 1.0 kW | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 25
1 | SWFS001 | 2 | Convection Oven, Commercial | B | Any | Any | EECP | 8 | Energy Efficiency Requirements of Commercial Convection Ovens Table | Yes | EFFICIENCY | Min Cooking Efficiency (%) | Numeric Value | [7 empty] | If Energy Star Qualified = 'EnergyStar' Must be >=71% | QA Checklist | If the product is not listed as being EnergyStar qualified, use the submitted installation report or manufacturer spec sheet to validate the equipment minimum cooking efficiency (%) | The cooking efficiency needs to be >= 71% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 27
1 | SWFS001 | 2 | Convection Oven, Commercial | B | Any | Any | EECP | 10 | All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [7 empty] | If 'Energy Star Qualified" is 'No' then make active Must be <= 1.6 | QA Checklist | If the product is not listed as being EnergyStar qualified, use the submitted installation report or manufacturer spec sheet to validate the equipment Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 1.6 kW | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 25
1 | SWFS001 | 2 | Convection Oven, Commercial | D | Any | Any | EECP | 16 | All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. | Yes |  | Min. Cooking Energy Efficiency (%) | Numeric Value | [7 empty] | If 'Energy Star Qualified" is 'No' then make active Must be >= 46% | QA Checklist | If the product is not listed as being EnergyStar qualified, use the submitted installation report or manufacturer spec sheet to validate the equipment minimum cooking efficiency (%) | The cooking efficiency needs to be >= 46% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 34
1 | SWFS001 | 2 | Convection Oven, Commercial | D | Any | Any | EECP | 17 | Energy Efficiency Requirements of Commercial Convection Ovens Table | Yes |  | Idle Energy Rate (Btu/Hr) | Numeric Value | [7 empty] | If Energy Star Qualified = 'EnergyStar' Must be <= 12000 | QA Checklist | If the product is not listed as being EnergyStar qualified, use the submitted installation report or manufacturer spec sheet to validate the equipment Idle Energy Rate (Btu/hr) | The idle energy rate must be <= 12,000 Btu/hr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 25
1 | SWFS001 | 2 | Convection Oven, Commercial | B | Any | Any | EECP | 18 | All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. * Half-size gas convection ovens are excluded from ENERGY STAR. | Yes |  | Product qualification method? | Drop Down List | CEC ;EnergyStar;Other; | [6 empty] | Must not be Other | QA Checklist | Use the make and model number listed on the invoice/EECP and cross check the EnergyStar database to determine if the product is listed as EnergyStar qualified | The listed make and model in EECP should be included in the EnergyStar database | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Use to replace 'Energy Star Qualified' | 2021-06-07 | Kenny Liljestrom |  | Add | 29
1 | SWFS001 | 2 | Convection Oven, Commercial | C | Any | Any | EECP | 19 | All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. * Half-size gas convection ovens are excluded from ENERGY STAR. | Yes |  | Product qualification method? | Drop Down List | CEC ;EnergyStar;Other; | [6 empty] | Must be 'CEC' | QA Checklist | Use the make and model number listed on the invoice/EECP and cross check the EnergyStar database to determine if the product is listed as EnergyStar qualified | The listed make and model in EECP should be included in the EnergyStar database | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Use to replace 'Energy Star Qualified' | 2021-06-07 | Kenny Liljestrom |  | Add | 29
1 | SWFS001 | 2 | Convection Oven, Commercial | D | Any | Any | EECP | 20 | All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. * Half-size gas convection ovens are excluded from ENERGY STAR. | Yes |  | Product qualification method? | Drop Down List | CEC ;EnergyStar;Other; | [6 empty] | Must not be Other | QA Checklist | Use the make and model number listed on the invoice/EECP and cross check the EnergyStar database to determine if the product is listed as EnergyStar qualified | The listed make and model in EECP should be included in the EnergyStar database | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Use to replace 'Energy Star Qualified' | 2021-06-07 | Kenny Liljestrom |  | Add | 29
0 | SWFS002 | 1 | Door-Type Dishwasher, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-11 | Kenny Liljestrom |  | Add | 12
0 | SWFS002 | 1 | Door-Type Dishwasher, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-11 | Kenny Liljestrom |  | Add | 5
0 | SWFS002 | 1 | Door-Type Dishwasher, Commercial | Any | Any | Any | EECP | 3 | Used or rebuilt equipment and other dishwasher types (conveyor, under-counter, flight-type) are not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 43
0 | SWFS002 | 1 | Door-Type Dishwasher, Commercial | A | Any | Any | EECP | 4 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Water Consumption | Water consumption of dishwasher in gallons per rack | Numeric Value | [7 empty] | Must be <=0.76 | QA Checklist | Using the submitted manufacturer spec sheet validate the water consumption per pack (gallons/rack) | The water consumption must be <= 0.76 gallons/rack | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 51
0 | SWFS002 | 1 | Door-Type Dishwasher, Commercial | B | Any | Any | EECP | 5 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Water Consumption | Water consumption of dishwasher in gallons per rack | Numeric Value | [7 empty] | Must be <=1.0 | QA Checklist | Using the submitted manufacturer spec sheet validate the water consumption per pack (gallons/rack) | The water consumption must be <= 1.0 gallons/rack | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 51
0 | SWFS002 | 1 | Door-Type Dishwasher, Commercial | A | Any | Any | EECP | 6 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <=0.70 | QA Checklist | Using the submitted manufacturer spec sheet validate the Idle Energy Rate (kW) | The Idle Energy Rate must be <= 0.70 kW | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 21
0 | SWFS002 | 1 | Door-Type Dishwasher, Commercial | B | Any | Any | EECP | 7 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <=0.60 | QA Checklist | Using the submitted manufacturer spec sheet validate the Idle Energy Rate (kW) | The Idle Energy Rate must be <= 0.60 kW | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 21
0 | SWFS002 | 1 | Door-Type Dishwasher, Commercial | Any | Any | Any | EECP | 8 | Used or rebuilt equipment and other dishwasher types (conveyor, under-counter, flight-type) are not eligible. | Yes |  | Dishwasher Type | Drop Down List | Door Dishwasher;Conveyor Dishwasher;Under-Counter Dishwasher;Flight Dishwasher; | [6 empty] | Must be 'Door Dishwasher' | QA Checklist | Using the submitted manufacturer spec sheet validate the equipment type | The dishwasher must be listed as being a Door Dishwasher type (not Conveyor Dishwasher, Under-Counter Dishwasher, or Flight Dishwasher) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 15
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 12
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 5
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | Any | Any | Any | QA Checklist | 3 | Used or rebuilt equipment and other dishwasher types (conveyor, under-counter, flight-type) are not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property pending MGMT approval | 2021-09-09 | Kenny Liljestrom |  | Add | 43
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | A | Any | Any | EECP | 4 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Water Consumption | Water consumption of dishwasher in gallons per rack | Numeric Value | [7 empty] | Must be <=0.76 | QA Checklist | Using the submitted manufacturer spec sheet validate the water consumption per pack (gallons/rack) | The water consumption must be <= 0.76 gallons/rack | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property pending MGMT approval | 2021-09-09 | Kenny Liljestrom |  | Add | 51
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | B | Any | Any | EECP | 5 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Water Consumption | Water consumption of dishwasher in gallons per rack | Numeric Value | [7 empty] | Must be <=1.0 | QA Checklist | Using the submitted manufacturer spec sheet validate the water consumption per pack (gallons/rack) | The water consumption must be <= 1.0 gallons/rack | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 51
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | A | Any | Any | EECP | 6 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes |  | Max washing energy (kWh/rack) | Numeric Value | [7 empty] | Must be <= 0.35 | QA Checklist | Using the submitted manufacturer spec sheet validate the water consumption per pack (gallons/rack) | The water consumption must be <= 0.76 gallons/rack | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-09-09 | Kenny Liljestrom |  | Add | 29
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | B | Any | Any | EECP | 7 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes |  | Max washing energy (kWh/rack) | Numeric Value | [7 empty] | Must be <= 0.15 | QA Checklist | Using the submitted manufacturer spec sheet validate the water consumption per pack (gallons/rack) | The water consumption must be <= 1.0 gallons/rack | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-09-09 | Kenny Liljestrom |  | Add | 29
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | A | Any | Any | EECP | 8 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <=0.55 | QA Checklist | Using the submitted manufacturer spec sheet validate the Idle Energy Rate (kW) | The Idle Energy Rate must be <= 0.55 kW | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Validation rule updated for measure package revision | 2021-09-09 | Kenny Liljestrom |  | Add | 21
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | B | Any | Any | EECP | 9 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <=0.30 | QA Checklist | Using the submitted manufacturer spec sheet validate the Idle Energy Rate (kW) | The Idle Energy Rate must be <= 0.30 kW | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Validation rule updated for measure package revision | 2021-09-09 | Kenny Liljestrom |  | Add | 21
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | Any | Any | Any | QA Checklist | 10 | Used or rebuilt equipment and other dishwasher types (conveyor, under-counter, flight-type) are not eligible. | Yes |  | Dishwasher Type | Drop Down List | Door Dishwasher;Conveyor Dishwasher;Under-Counter Dishwasher;Flight Dishwasher; | [6 empty] | Must be 'Door Dishwasher' | QA Checklist | Using the submitted manufacturer spec sheet validate the equipment type | The dishwasher must be listed as being a Door Dishwasher type (not Conveyor Dishwasher, Under-Counter Dishwasher, or Flight Dishwasher) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property pending MGMT approval | 2021-09-09 | Kenny Liljestrom |  | Add | 15
0 | SWFS003 | 1 | Combination Oven, Commercial | Any | Any | Any | EECP | 1 | Manufacturer | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-07 | Kenny Liljestrom |  | Add | 12
0 | SWFS003 | 1 | Combination Oven, Commercial | Any | Any | Any | EECP | 2 | Model | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-07 | Kenny Liljestrom |  | Add | 5
0 | SWFS003 | 1 | Combination Oven, Commercial | Any | Any | Any | EECP | 3 | Used or rebuilt equipment is not eligible. | Yes |  | New Equipment | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Collect the equipment invoice for the product | The invoice should list the equipment as new (i.e. not used, rebuilt. or leased) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 13
0 | SWFS003 | 1 | Combination Oven, Commercial | A | Any | Any | EECP | 4 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Production Capacity | Oven Production Capacity (lbs/hr) | Numeric Value | [7 empty] | Must be >= 100 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Production Capacity (lbs/hr) | The Oven Production Capacity (lbs/hr) Must be >= 100 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | A | Any | Any | EECP | 5 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Preheat Energy (watts) | Numeric Value | [7 empty] | Must be <= 1500 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Preheat Energy (watts) | The Preheat Energy (watts) Must be <= 1500 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 22
0 | SWFS003 | 1 | Combination Oven, Commercial | A | Any | Any | EECP | 6 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Idle Energy Rate | Oven Mode Idle Energy Rate (watts) | Numeric Value | [7 empty] | Must be <= 2000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Idle Energy Rate (watts) | The Oven Mode Idle Energy Rate (watts) Must be <= 2000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | A | Any | Any | EECP | 7 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Efficiency | Oven Mode Cooking Efficiency (%) | Numeric Value | [7 empty] | Must be >= 70% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Cooking Efficiency (%) | The Oven Mode Cooking Efficiency (%) Must be >= 70% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 32
0 | SWFS003 | 1 | Combination Oven, Commercial | A | Any | Any | EECP | 8 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Production Capacity | Steam Production Capacity (lbs/hr) | Numeric Value | [7 empty] | Must be >= 120 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Production Capacity (lbs/hr) | The Steam Production Capacity (lbs/hr) Must be >= 120 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | A | Any | Any | EECP | 9 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Idle Energy Rate | Steam Mode Idle Energy Rate (watts) | Numeric Value | [7 empty] | Must be <= 5000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Idle Energy Rate (watts) | The Steam Mode Idle Energy Rate (watts) Must be <= 5000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 35
0 | SWFS003 | 1 | Combination Oven, Commercial | A | Any | Any | EECP | 10 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Efficiency | Steam Mode Cooking Efficiency (%) | Numeric Value | [7 empty] | Must be >= 50% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Cooking Efficiency (%) | The Steam Mode Cooking Efficiency (%) Must be >= 50% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | A | Any | Any | EECP | 11 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Water Consumption Rate (gal/hr) | Numeric Value | [7 empty] | Must be <= 20 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Water Consumption Rate (gal/hr) | The Water Consumption Rate (gal/hr) Must be <= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 31
0 | SWFS003 | 1 | Combination Oven, Commercial | B | Any | Any | EECP | 12 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Production Capacity | Oven Production Capacity (lbs/hr) | Numeric Value | [7 empty] | Must be >= 125 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Production Capacity (lbs/hr) | The Oven Production Capacity (lbs/hr) Must be >= 125 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | B | Any | Any | EECP | 13 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Preheat Energy (watts) | Numeric Value | [7 empty] | Must be <= 2000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Preheat Energy (watts) | The Preheat Energy (watts) Must be <= 2000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 22
0 | SWFS003 | 1 | Combination Oven, Commercial | B | Any | Any | EECP | 14 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Idle Energy Rate | Oven Mode Idle Energy Rate (watts) | Numeric Value | [7 empty] | Must be <= 2500 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Idle Energy Rate (watts) | The Oven Mode Idle Energy Rate (watts) Must be <= 2500 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | B | Any | Any | EECP | 15 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Efficiency | Oven Mode Cooking Efficiency (%) | Numeric Value | [7 empty] | Must be >= 70% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Cooking Efficiency (%) | The Oven Mode Cooking Efficiency (%) Must be >= 70% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Configured as 71%, needs to be updated to 70% | 2021-06-07 | Kenny Liljestrom |  | Add | 32
0 | SWFS003 | 1 | Combination Oven, Commercial | B | Any | Any | EECP | 16 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Production Capacity | Steam Production Capacity (lbs/hr) | Numeric Value | [7 empty] | Must be >= 200 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Production Capacity (lbs/hr) | The Steam Production Capacity (lbs/hr) Must be >= 200 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | B | Any | Any | EECP | 17 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Idle Energy Rate | Steam Mode Idle Energy Rate (watts) | Numeric Value | [7 empty] | Must be <= 6000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Idle Energy Rate (watts) | The Steam Mode Idle Energy Rate (watts) Must be <= 6000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 35
0 | SWFS003 | 1 | Combination Oven, Commercial | B | Any | Any | EECP | 18 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Efficiency | Steam Mode Cooking Efficiency (%) | Numeric Value | [7 empty] | Must be >= 50% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Cooking Efficiency (%) | The Steam Mode Cooking Efficiency (%) Must be >= 50% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Configured as 51%, needs to be updated to 50% | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | B | Any | Any | EECP | 19 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Water Consumption Rate (gal/hr) | Numeric Value | [7 empty] | Must be <= 25 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Water Consumption Rate (gal/hr) | The Water Consumption Rate (gal/hr) Must be <= 25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 31
0 | SWFS003 | 1 | Combination Oven, Commercial | C | Any | Any | EECP | 20 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Production Capacity | Oven Production Capacity (lbs/hr) | Numeric Value | [7 empty] | Must be >= 325 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Production Capacity (lbs/hr) | The Oven Production Capacity (lbs/hr) Must be >= 325 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | C | Any | Any | EECP | 21 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Preheat Energy (watts) | Numeric Value | [7 empty] | Must be <= 3000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Preheat Energy (watts) | The Preheat Energy (watts) Must be <= 3000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 22
0 | SWFS003 | 1 | Combination Oven, Commercial | C | Any | Any | EECP | 22 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Idle Energy Rate | Oven Mode Idle Energy Rate (watts) | Numeric Value | [7 empty] | Must be <= 4000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Idle Energy Rate (watts) | The Oven Mode Idle Energy Rate (watts) Must be <= 4000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | C | Any | Any | EECP | 23 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Efficiency | Oven Mode Cooking Efficiency (%) | Numeric Value | [7 empty] | Must be >= 70% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Cooking Efficiency (%) | The Oven Mode Cooking Efficiency (%) Must be >= 70% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 32
0 | SWFS003 | 1 | Combination Oven, Commercial | C | Any | Any | EECP | 24 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Production Capacity | Steam Production Capacity (lbs/hr) | Numeric Value | [7 empty] | Must be >= 400 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Production Capacity (lbs/hr) | The Steam Production Capacity (lbs/hr) Must be >= 400 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | C | Any | Any | EECP | 25 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Idle Energy Rate | Steam Mode Idle Energy Rate (watts) | Numeric Value | [7 empty] | Must be <= 9000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Idle Energy Rate (watts) | The Steam Mode Idle Energy Rate (watts) Must be <= 9000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 35
0 | SWFS003 | 1 | Combination Oven, Commercial | C | Any | Any | EECP | 26 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Efficiency | Steam Mode Cooking Efficiency (%) | Numeric Value | [7 empty] | Must be >= 50% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Cooking Efficiency (%) | The Steam Mode Cooking Efficiency (%) Must be >= 50% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | C | Any | Any | EECP | 27 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Water Consumption Rate (gal/hr) | Numeric Value | [7 empty] | Must be <= 30 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Water Consumption Rate (gal/hr) | The Water Consumption Rate (gal/hr) Must be <= 30 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 31
0 | SWFS003 | 1 | Combination Oven, Commercial | D | Any | Any | EECP | 28 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Production Capacity | Oven Production Capacity (lbs/hr) | Numeric Value | [7 empty] | Must be >= 100 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Production Capacity (lbs/hr) | The Oven Production Capacity (lbs/hr) Must be >= 100 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | D | Any | Any | EECP | 29 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Preheat Energy (Btu/hr) | Numeric Value | [7 empty] | Must be <= 13000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Preheat Energy (Btu/hr) | The Preheat Energy (Btu/hr) Must be <= 13000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 23
0 | SWFS003 | 1 | Combination Oven, Commercial | D | Any | Any | EECP | 30 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Idle Energy Rate | Oven Mode Idle Energy Rate (Btu/hr) | Numeric Value | [7 empty] | Must be <= 8000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Idle Energy Rate (Btu/hr) | The Oven Mode Idle Energy Rate (Btu/hr) Must be <= 8000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 35
0 | SWFS003 | 1 | Combination Oven, Commercial | D | Any | Any | EECP | 31 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Efficiency | Oven Mode Cooking Efficiency (%) | Numeric Value | [7 empty] | Must be >= 44% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Cooking Efficiency (%) | The Oven Mode Cooking Efficiency (%) Must be >= 44% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 32
0 | SWFS003 | 1 | Combination Oven, Commercial | D | Any | Any | EECP | 32 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Production Capacity | Steam Production Capacity (lbs/hr) | Numeric Value | [7 empty] | Must be >= 120 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Production Capacity (lbs/hr) | The Steam Production Capacity (lbs/hr) Must be >= 120 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | D | Any | Any | EECP | 33 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Idle Energy Rate | Steam Mode Idle Energy Rate (Btu/hr) | Numeric Value | [7 empty] | Must be <= 15000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Idle Energy Rate (Btu/hr) | The Steam Mode Idle Energy Rate (Btu/hr) Must be <= 15000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 36
0 | SWFS003 | 1 | Combination Oven, Commercial | D | Any | Any | EECP | 34 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Efficiency | Steam Mode Cooking Efficiency (%) | Numeric Value | [7 empty] | Must be >= 38% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Cooking Efficiency (%) | The Steam Mode Cooking Efficiency (%) Must be >= 38% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | D | Any | Any | EECP | 35 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Water Consumption Rate (gal/hr) | Numeric Value | [7 empty] | Must be <= 18 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Water Consumption Rate (gal/hr) | The Water Consumption Rate (gal/hr) Must be <= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 31
0 | SWFS003 | 1 | Combination Oven, Commercial | E | Any | Any | EECP | 36 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Production Capacity | Oven Production Capacity (lbs/hr) | Numeric Value | [7 empty] | Must be >= 125 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Production Capacity (lbs/hr) | The Oven Production Capacity (lbs/hr) Must be >= 125 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | E | Any | Any | EECP | 37 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Preheat Energy (Btu/hr) | Numeric Value | [7 empty] | Must be <= 16000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Preheat Energy (Btu/hr) | The Preheat Energy (Btu/hr) Must be <= 16000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 23
0 | SWFS003 | 1 | Combination Oven, Commercial | E | Any | Any | EECP | 38 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Idle Energy Rate | Oven Mode Idle Energy Rate (Btu/hr) | Numeric Value | [7 empty] | Must be <= 10000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Idle Energy Rate (Btu/hr) | The Oven Mode Idle Energy Rate (Btu/hr) Must be <= 10000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 35
0 | SWFS003 | 1 | Combination Oven, Commercial | E | Any | Any | EECP | 39 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Efficiency | Oven Mode Cooking Efficiency (%) | Numeric Value | [7 empty] | Must be >= 44% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Cooking Efficiency (%) | The Oven Mode Cooking Efficiency (%) Must be >= 44% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 32
0 | SWFS003 | 1 | Combination Oven, Commercial | E | Any | Any | EECP | 40 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Production Capacity | Steam Production Capacity (lbs/hr) | Numeric Value | [7 empty] | Must be >= 200 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Production Capacity (lbs/hr) | The Steam Production Capacity (lbs/hr) Must be >= 200 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | E | Any | Any | EECP | 41 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Idle Energy Rate | Steam Mode Idle Energy Rate (Btu/hr) | Numeric Value | [7 empty] | Must be <= 18000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Idle Energy Rate (Btu/hr) | The Steam Mode Idle Energy Rate (Btu/hr) Must be <= 18000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 36
0 | SWFS003 | 1 | Combination Oven, Commercial | E | Any | Any | EECP | 42 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Efficiency | Steam Mode Cooking Efficiency (%) | Numeric Value | [7 empty] | Must be >= 38% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Cooking Efficiency (%) | The Steam Mode Cooking Efficiency (%) Must be >= 38% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | E | Any | Any | EECP | 43 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Water Consumption Rate (gal/hr) | Numeric Value | [7 empty] | Must be <= 30 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Water Consumption Rate (gal/hr) | The Water Consumption Rate (gal/hr) Must be <= 30 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 31
0 | SWFS003 | 1 | Combination Oven, Commercial | F | Any | Any | EECP | 44 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Production Capacity | Oven Production Capacity (lbs/hr) | Numeric Value | [7 empty] | Must be >= 325 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Production Capacity (lbs/hr) | The Oven Production Capacity (lbs/hr) Must be >= 325 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | F | Any | Any | EECP | 45 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Preheat Energy (Btu/hr) | Numeric Value | [7 empty] | Must be <= 24000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Preheat Energy (Btu/hr) | The Preheat Energy (Btu/hr) Must be <= 24000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 23
0 | SWFS003 | 1 | Combination Oven, Commercial | F | Any | Any | EECP | 46 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Idle Energy Rate | Oven Mode Idle Energy Rate (Btu/hr) | Numeric Value | [7 empty] | Must be <= 16000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Idle Energy Rate (Btu/hr) | The Oven Mode Idle Energy Rate (Btu/hr) Must be <= 16000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 35
0 | SWFS003 | 1 | Combination Oven, Commercial | F | Any | Any | EECP | 47 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Efficiency | Oven Mode Cooking Efficiency (%) | Numeric Value | [7 empty] | Must be >= 44% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Cooking Efficiency (%) | The Oven Mode Cooking Efficiency (%) Must be >= 44% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 32
0 | SWFS003 | 1 | Combination Oven, Commercial | F | Any | Any | EECP | 48 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Production Capacity | Steam Production Capacity (lbs/hr) | Numeric Value | [7 empty] | Must be >= 400 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Production Capacity (lbs/hr) | The Steam Production Capacity (lbs/hr) Must be >= 400 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | F | Any | Any | EECP | 49 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Idle Energy Rate | Steam Mode Idle Energy Rate (Btu/hr) | Numeric Value | [7 empty] | Must be <= 28000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Idle Energy Rate (Btu/hr) | The Steam Mode Idle Energy Rate (Btu/hr) Must be <= 28000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 36
0 | SWFS003 | 1 | Combination Oven, Commercial | F | Any | Any | EECP | 50 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Efficiency | Steam Mode Cooking Efficiency (%) | Numeric Value | [7 empty] | Must be >= 38% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Cooking Efficiency (%) | The Steam Mode Cooking Efficiency (%) Must be >= 38% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | F | Any | Any | EECP | 51 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Water Consumption Rate (gal/hr) | Numeric Value | [7 empty] | Must be <= 60 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Water Consumption Rate (gal/hr) | The Water Consumption Rate (gal/hr) Must be <= 60 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 31
1 | SWFS004 | 1 | Griddle, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-11 | Kenny Liljestrom |  | Add | 12
1 | SWFS004 | 1 | Griddle, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-11 | Kenny Liljestrom |  | Add | 5
1 | SWFS004 | 1 | Griddle, Commercial | Any | Any | Any | EECP | 3 | Double-sided griddles and used or rebuilt equipment are not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
1 | SWFS004 | 1 | Griddle, Commercial | Any | Any | Any | EECP | 4 | Double-sided griddles and used or rebuilt equipment are not eligible. | Yes |  | Is the griddle double-sided? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | QA Checklist | Cross check make and model number with EnergyStar database or specification sheet | The unit must not be listed as being 'Double Sided' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 28
1 | SWFS004 | 1 | Griddle, Commercial | Any | Any | Any | EECP | 5 | This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | Energy Star Qualified | ENERGY STAR Qualified? | Drop Down List | Yes;No | [7 empty] | QA Checklist | Use the EnergyStar database and compare the listed make and model in EECP to the list | The database needs to have the make and model listed in EECP as being EnergyStar qualified; if not, criteria below must be met | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 22
1 | SWFS004 | 1 | Griddle, Commercial | A | Any | Any | EECP | 6 | This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | Size | Production Capacity (lb/hr) | Numeric Value | [7 empty] | If 'Energy Star Qualified' is 'No' then Must be >=49 | QA Checklist | Use the manufacturer specification sheet to capture the production capacity of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be >= 49 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 27
1 | SWFS004 | 1 | Griddle, Commercial | A | Any | Any | EECP | 7 | This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (W/ft2/hr) | Numeric Value | [7 empty] | If 'Energy Star Qualified' is 'No' then Must be <= 293 | QA Checklist | Use the manufacturer specification sheet to capture the maximum idle energy rate (W/ft2-hr) of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be <= 293 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 31
1 | SWFS004 | 1 | Griddle, Commercial | A | Any | Any | EECP | 8 | This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | EFFICIENCY | Min. Cooking Energy Efficiency (%) | Numeric Value | [7 empty] | If 'Energy Star Qualified' is 'No' then Must be >= 75% | QA Checklist | Use the manufacturer specification sheet to capture the minimum cooking efficiency (%) of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be >= 75% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 34
1 | SWFS004 | 1 | Griddle, Commercial | B | Any | Any | EECP | 9 | This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | Size | Production Capacity (lb/hr) | Numeric Value | [7 empty] | If 'Energy Star Qualified' is 'No' then Must be >=49.2 | QA Checklist | Use the manufacturer specification sheet to capture the production capacity (lb/hr) of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be >= 49.2 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 27
1 | SWFS004 | 1 | Griddle, Commercial | B | Any | Any | EECP | 10 | This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (Btu/hr) | Numeric Value | [7 empty] | If 'Energy Star Qualified' is 'No' then Must be <= 2068 | QA Checklist | Use the manufacturer specification sheet to capture the maximum idle energy rate (Btu/hr) of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be <= 2068 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 29
1 | SWFS004 | 1 | Griddle, Commercial | B | Any | Any | EECP | 11 | This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | EFFICIENCY | Min. Cooking Energy Efficiency (%) | Numeric Value | [7 empty] | If 'Energy Star Qualified' is 'No' then Must be >= 46% | QA Checklist | Use the manufacturer specification sheet to capture the minimum cooking efficiency (%) of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be >= 46% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 34
0 | SWFS005 | 2 | Steamer, Commercial | Any | Any | Any | EECP | 1 | Manufacturer | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-07 | Kenny Liljestrom |  | Add | 12
0 | SWFS005 | 2 | Steamer, Commercial | Any | Any | Any | EECP | 2 | Model | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-07 | Kenny Liljestrom |  | Add | 5
0 | SWFS005 | 2 | Steamer, Commercial | Any | Any | Any | EECP | 3 | Measure Description | Yes |  | Is Equipment Gas or Electric? | Drop Down List | Gas;Electric; | [7 empty] | - | - | - | - | - | - | Not configured in original upload | 2021-06-07 | Kenny Liljestrom | Removed, measure description clarifies what is being installed | Add | 30
0 | SWFS005 | 2 | Steamer, Commercial | Any | Any | Any | EECP | 4 | Used or rebuilt equipment is not eligible. | Yes |  | New Equipment | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Collect the equipment invoice for the product | The invoice should list the equipment as new (i.e. not used, rebuilt. or leased) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 13
0 | SWFS005 | 2 | Steamer, Commercial | Any | Any | Any | EECP | 5 | New commercial steam cookers must meet the ENERGY STAR Program Requirements for Commercial Steam Cookers, Version 1.2 or the specification in the Measure Case Description. | Yes | Energy Star Qualified | ENERGY STAR Qualified | Drop Down List | Yes;No; | [7 empty] | QA Checklist | Use the EnergyStar database and compare the listed make and model in EECP to the list | The database needs to have the make and model listed in EECP as being EnergyStar qualified; if not, criteria below must be met | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 21
0 | SWFS005 | 2 | Steamer, Commercial | Any | Any | Any | EECP | 6 | New commercial steam cookers must meet the ENERGY STAR Program Requirements for Commercial Steam Cookers, Version 1.2 or the specification in the Measure Case Description. | Yes | Size | Pan Capacity | Drop Down List | 3 Pan;4 Pan;5 Pan;6+ Pan; | [7 empty] | QA Checklist | Use the manufacturer specification sheet to capture the number of pans of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be 3, 4, 5, or 6 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 12
0 | SWFS005 | 2 | Steamer, Commercial | A | Any | Any | EECP | 7 | New commercial steam cookers must meet the ENERGY STAR Program Requirements for Commercial Steam Cookers, Version 1.2 or the specification in the Measure Case Description. | Yes | EFFICIENCY | Min. Cooking Energy Efficiency (%) | Numeric Value | [7 empty] | If 'Energy Star Qualified' is No then make active Must be >=50% | QA Checklist | If the product is not ENERGYSTAR listed, use the manufacturer specification sheet to capture the minimum cooking efficiency (%) of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be >= 50% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS005 | 2 | Steamer, Commercial | A | Any | Any | EECP | 8 | New commercial steam cookers must meet the ENERGY STAR Program Requirements for Commercial Steam Cookers, Version 1.2 or the specification in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (W) | Numeric Value | [7 empty] | If 'Pan Capacity' is '3 Pan' then Must be <= 800 If 'Pan Capacity' is '4 Pan' then Must be <= 530 If 'Pan Capacity' is '5 Pan' then Must be <= 670 If 'Pan Capacity' is '6+ Pan' then Must be <= 800 | QA Checklist | If the product is not ENERGYSTAR listed, use the manufacturer specification sheet to capture the max idle energy rate (W) of the unit | If 'Pan Capacity' is '3 Pan' then must be <= 800 W If 'Pan Capacity' is '4 Pan' then must be <= 530 W If 'Pan Capacity' is '5 Pan' then must be <= 670 W If 'Pan Capacity' is '6+ Pan' then must be <= 800 W | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 24
0 | SWFS005 | 2 | Steamer, Commercial | B | Any | Any | EECP | 9 | New commercial steam cookers must meet the ENERGY STAR Program Requirements for Commercial Steam Cookers, Version 1.2 or the specification in the Measure Case Description. | Yes | EFFICIENCY | Min. Cooking Energy Efficiency (%) | Numeric Value | [7 empty] | If 'Energy Star Qualified' is No Must be >=38% | QA Checklist | If the product is not ENERGYSTAR listed, use the manufacturer specification sheet to capture the minimum cooking efficiency (%) of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be >= 38% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS005 | 2 | Steamer, Commercial | B | Any | Any | EECP | 10 | New commercial steam cookers must meet the ENERGY STAR Program Requirements for Commercial Steam Cookers, Version 1.2 or the specification in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (Btu/hr) | Numeric Value | [7 empty] | If 'Pan Capacity' is '3 Pan' then Must be <= 6250 If 'Pan Capacity' is '4 Pan' then Must be <= 8350 If 'Pan Capacity' is '5 Pan' then Must be <= 10400 If 'Pan Capacity' is '6+ Pan' then Must be <= 12500 | QA Checklist | If the product is not ENERGYSTAR listed, use the manufacturer specification sheet to capture the max idle energy rate (W) of the unit | If 'Pan Capacity' is '3 Pan' then Must be <= 6250 Btu/hr If 'Pan Capacity' is '4 Pan' then Must be <= 8350 Btu/hr If 'Pan Capacity' is '5 Pan' then Must be <= 10400 Btu/hr If 'Pan Capacity' is '6+ Pan' then Must be <= 12500 Btu/hr | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 29
1 | SWFS006 | 1 | Ice Machine, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate of the top section of the ice machine showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
1 | SWFS006 | 1 | Ice Machine, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate of the top section of the ice machine showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
1 | SWFS006 | 1 | Ice Machine, Commercial | Any | Any | Any | EECP | 3 | Measure Description | Yes |  | Does the ice machine match the measure case equipment type? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | - | - | - | - | - | - | Not configured in original upload | 2021-05-28 | Kenny Liljestrom | Removed, measure description clarifies what is being installed | Add | 59
1 | SWFS006 | 1 | Ice Machine, Commercial | Any | Any | Any | EECP | 4 | Water-cooled ice machines and used or rebuilt equipment are not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | Any | Any | Any | EECP | 5 | Program qualifying ice machines are defined by equipment type and daily ice harvest rate. The efficiency specifications must meet the requirements listed in the Measure Case Description for batch and continuous machines, per the ENERGY STAR V3.0 Program Requirements for Automatic Commercial Ice Makers. | Yes |  | ENERGY STAR Qualified | Drop Down List | Yes;No; | [6 empty] | If 'No', make available Harvest Rate and Energy Use | QA Checklist | Use the EnergyStar database and compare the listed make and model in EECP to the list | The database needs to have the make and model listed in EECP as being EnergyStar qualified; if not, criteria below must be met | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 21
1 | SWFS006 | 1 | Ice Machine, Commercial | Any | Any | Any | EECP | 6 | The entire AHRI-tested ice making system must be purchased. Remote machines must be purchased with qualifying remote condenser or remote condenser/compressor unit. | Yes | Entire AHRI System Purchased | Was entire AHRI-tested ice making system purchased? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 51
1 | SWFS006 | 1 | Ice Machine, Commercial | Any | Any | Any | EECP | 7 | Only air-cooled machines (self-contained, icemaker heads, or remote condensing) are eligible. Water-cooled ice machines and used or rebuilt equipment are not eligible. | Yes | Air Cooled Unit | Is the unit an air cooled ice maker? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | Using the submitted manufacturer spec sheet validate if the unit is air-cooled or water cooled | The unit must be listed as being air cooled | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 36
1 | SWFS006 | 1 | Ice Machine, Commercial | Any | Any | Any | EECP | 8 | Required for defining Energy Use | Yes | Ice Machine Production Type | Ice making system type | Drop Down List | Batch;Continuous; | [7 empty] | QA Checklist | Using the submitted manufacturer spec sheet validate the ice system making type (batch or continuous) | There are no validation criteria for this property | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 22
1 | SWFS006 | 1 | Ice Machine, Commercial | A | Any | Any | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [7 empty] | Must be < 110 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be < 110 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | B | Any | Any | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [7 empty] | Must be >= 110 and < 200 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be >= 110 and < 200 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | C | Any | Any | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [7 empty] | Must be >= 200 and < 4000 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be >= 200 and < 4000 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | D | Any | Any | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [7 empty] | Must be < 300 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be < 300 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | E | Any | Any | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [7 empty] | Must be >= 300 and < 800 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be >= 300 and < 800 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | F | Any | Any | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [7 empty] | Must be >= 800 and < 1500 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be >= 800 and < 1500 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | G | Any | Any | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [7 empty] | Must be >= 1500 and < 4000 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be >= 1500 and < 4000 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | H | Any | Any | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [7 empty] | Must be < 987 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be < 987 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | I | Any | Any | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [7 empty] | Must be >= 988 and < 4000 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be >= 988 and < 4000 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | A | Any | Any | EECP | 10 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [7 empty] | If System Type is 'Batch' must be <= 12.57 - 0.0399 x Production per Day | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | If System Type is 'Batch' must be <= 12.57 - 0.0399 x Production per Day | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | B | Any | Any | EECP | 11 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [7 empty] | If System Type is 'Batch' must be <=10.56 - 0.0215 x Production per Day | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | The Maximum Daily Energy Use (kWh/100 lbs. ice) If System Type is 'Batch' must be <=10.56 - 0.0215 x Production per Day | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | C | Any | Any | EECP | 12 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [7 empty] | If System Type is 'Batch' and Production per Day is >= 200 and <= 4000 then must be <= 6.25 'If System Type is 'Continuous' and Production per Day is >= 200 and <= 700 then must be <= 8.24 - 0.005429 x Production per Day 'If System Type is 'Continuous' and Production per Day is >= 700 and <= 4000 then must be <= 4.44 | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | The Maximum Daily Energy Use (kWh/100 lbs. ice) If System Type is 'Batch' and Production per Day is >= 200 and <= 4000 then must be <= 6.25 'If System Type is 'Continuous' and Production per Day is >= 200 and <= 700 then must be <= 8.24 - 0.005429 x Production per Day 'If System Type is 'Continuous' and Production per Day is >= 700 and <= 4000 then must be <= 4.44 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | D | Any | Any | EECP | 13 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [7 empty] | If System Type is 'Batch' then must be <= 9.20 - 0.01134 x Production per Day 'If System Type is 'Continuous' then must be <= 7.90 - 0.005409 x Production per Day | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | The Maximum Daily Energy Use (kWh/100 lbs. ice) If System Type is 'Batch' then must be <= 9.20 - 0.01134 x Production per Day 'If System Type is 'Continuous' then must be <= 7.90 - 0.005409 x Production per Day | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | E | Any | Any | EECP | 14 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [7 empty] | If System Type is 'Batch' then must be <= 6.49-0.0023 x Production per Day 'If System Type is 'Continuous' and Production per Day < 310 then must be <= 7.90-0.005409 x Production per Day 'If System Type is 'Continuous' and Production per Day >= 310 then must be <= 7.08-0.002752 x Production per Day | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | The Maximum Daily Energy Use (kWh/100 lbs. ice) If System Type is 'Batch' then must be <= 6.49-0.0023 x Production per Day 'If System Type is 'Continuous' and Production per Day < 310 then must be <= 7.90-0.005409 x Production per Day 'If System Type is 'Continuous' and Production per Day >= 310 then must be <= 7.08-0.002752 x Production per Day | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | F | Any | Any | EECP | 15 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [7 empty] | If System Type is 'Batch' then must be <=5.11-0.00058 x Production per Day 'If System Type is 'Continuous' and Production per Day < 820 then must be <= 7.08-0.002752 x Production per Day 'If System Type is 'Continuous' and Production per Day >= 820 then must be <= 4.82 | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | The Maximum Daily Energy Use (kWh/100 lbs. ice) If System Type is 'Batch' then must be <=5.11-0.00058 x Production per Day 'If System Type is 'Continuous' and Production per Day < 820 then must be <= 7.08-0.002752 x Production per Day 'If System Type is 'Continuous' and Production per Day >= 820 then must be <= 4.82 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | G | Any | Any | EECP | 16 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [7 empty] | If System Type is 'Batch' then must be <= 4.24 'If System Type is 'Continuous' then must be <= 4.82 | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | The Maximum Daily Energy Use (kWh/100 lbs. ice) If System Type is 'Batch' then must be <= 4.24 'If System Type is 'Continuous' then must be <= 4.82 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | H | Any | Any | EECP | 17 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [7 empty] | If System Type is 'Batch' then must be <= 7.17-0.00308 x Production per Day 'If System Type is 'Continuous' and Production per Day < 800 then must be <= 7.76-0.00464 x Production per Day 'If System Type is 'Continuous' and Production per Day >= 800 then must be <= 4.05 | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | The Maximum Daily Energy Use (kWh/100 lbs. ice) If System Type is 'Batch' then must be <= 7.17-0.00308 x Production per Day 'If System Type is 'Continuous' and Production per Day < 800 then must be <= 7.76-0.00464 x Production per Day 'If System Type is 'Continuous' and Production per Day >= 800 then must be <= 4.05 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | I | Any | Any | EECP | 18 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [7 empty] | If System Type is 'Batch' then must be <= 4.13 'If System Type is 'Continuous' then must be <= 4.05 | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | The Maximum Daily Energy Use (kWh/100 lbs. ice) If System Type is 'Batch' then must be <= 4.13 'If System Type is 'Continuous' then must be <= 4.05 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | A | Any | Any | EECP | 19 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [7 empty] | If 'System Type' is Batch then <=25 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=25 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
1 | SWFS006 | 1 | Ice Machine, Commercial | B | Any | Any | EECP | 20 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [7 empty] | If 'System Type' is Batch then <=25 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=25 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
1 | SWFS006 | 1 | Ice Machine, Commercial | C | Any | Any | EECP | 21 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [7 empty] | If 'System Type' is Batch then <=25 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=25 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
1 | SWFS006 | 1 | Ice Machine, Commercial | D | Any | Any | EECP | 22 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [7 empty] | If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
1 | SWFS006 | 1 | Ice Machine, Commercial | E | Any | Any | EECP | 23 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [7 empty] | If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
1 | SWFS006 | 1 | Ice Machine, Commercial | F | Any | Any | EECP | 24 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [7 empty] | If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
1 | SWFS006 | 1 | Ice Machine, Commercial | G | Any | Any | EECP | 25 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [7 empty] | If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
1 | SWFS006 | 1 | Ice Machine, Commercial | H | Any | Any | EECP | 26 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [7 empty] | If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
1 | SWFS006 | 1 | Ice Machine, Commercial | I | Any | Any | EECP | 27 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [7 empty] | If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | Any | Any | Any | EECP | 3 | Any cabinets considered in this measure must have an electric resistance heating element, passive holding cabinets with no heating elements are not eligible. | Yes | Gas_Electric | Is Equipment Gas or Electric? | Drop Down List | Gas;Electric | [6 empty] | Must be Electric | QA Checklist | Using the submitted manufacturer spec sheet validate the fuel source type (electric or gas) | The equipment must be electric | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 29
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | Any | Any | Any | EECP | 4 | Used or rebuilt equipment are not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | A | Any | Any | EECP | 5 | Qualifying cabinets must not exceed the maximum idle energy rate of 25 W/ft3 for full-size cabinets and 35 W/ft3 for half-size cabinets, in accordance with the American Society for Testing and Materials (ASTM) Standard Test Method for the Performance of Hot Food Holding Cabinets (F2140). | Yes | Idle Energy Rate | Max Idle Energy Rate (watts/ft3) | Numeric Value | [7 empty] | Must be <= 25 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Idle Energy Rate (watts/ft3) | The Max Idle Energy Rate (watts/ft3) Must be <= 25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 32
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | B | Any | Any | EECP | 6 | Qualifying cabinets must not exceed the maximum idle energy rate of 25 W/ft3 for full-size cabinets and 35 W/ft3 for half-size cabinets, in accordance with the American Society for Testing and Materials (ASTM) Standard Test Method for the Performance of Hot Food Holding Cabinets (F2140). | Yes | Idle Energy Rate | Max Idle Energy Rate (watts/ft3) | Numeric Value | [7 empty] | Must be <= 35 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Idle Energy Rate (watts/ft3) | The Max Idle Energy Rate (watts/ft3) Must be <= 35 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 32
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | A | Any | Any | EECP | 7 | This measure includes new full-size (≥ 15 ft3) and half-size (< 15 ft3) insulated food holding cabinets. | Yes | Size | Insulated Holding Cabinet Size (square feet) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Insulated Holding Cabinet Size (square feet) | The Insulated Holding Cabinet Size (square feet) Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 45
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | B | Any | Any | EECP | 8 | This measure includes new full-size (≥ 15 ft3) and half-size (< 15 ft3) insulated food holding cabinets. | Yes | Size | Insulated Holding Cabinet Size (square feet) | Numeric Value | [7 empty] | Must be < 15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Insulated Holding Cabinet Size (square feet) | The Insulated Holding Cabinet Size (square feet) Must be < 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 45
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | Any | Any | Any | EECP | 9 | Eligible holding cabinets must be listed on the Food Service Technology Center (FSTC) qualified product list (https://fishnick.com/saveenergy/rebates/). | Yes | FSTC Listed | Is the installed holding cabinet listed on the Food Service Technology Center (FSTC) qualified product list (https://fishnick.com/saveenergy/rebates/)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Using the rebate site below, determine if the product is listed as being a qualified unit https://fishnick.com/saveenergy/rebates/ | The product must be listed as a qualified product on the fishnick website | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 151
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | Any | Any | Any | EECP | 10 | All measures must be electric hot food holding cabinets that are fully insulated (i.e., on all sides) and have solid or transparent doors designed to maintain the temperature of hot food that has been cooked using a separate appliance. This measure does not include cook-and-hold or retherm equipment. | Yes |  | Holding cabinet fully insulated (i.e., on all sides) and has solid or transparent doors? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | When inspecting the holding cabinet, check to see if the cabinet has any glass or transparent (see through) doors or sides | The holding cabinet must be fully insulated with no glass or transparent doors or sides | QA Checklist | Use the manufacturer spec sheet to check to see if the cabinet has any glass or transparent (see through) doors or sides | The holding cabinet must be fully insulated with no glass or transparent doors or sides | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 88
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | Any | Any | Any | EECP | 10 | All measures must be electric hot food holding cabinets that are fully insulated (i.e., on all sides) and have solid or transparent doors designed to maintain the temperature of hot food that has been cooked using a separate appliance. This measure does not include cook-and-hold or retherm equipment. | Yes |  | Is this a cook-and-hold retherm equipment? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet to determine if the holding cabinet is classified as a cook-and-hold retherm equipment | The cook-and-hold retherm type of cabinet is not eligible for rebate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 42
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 12
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 5
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | Any | Any | Any | EECP | 3 | Any cabinets considered in this measure must have an electric resistance heating element, passive holding cabinets with no heating elements are not eligible. | Yes | Gas_Electric | Is Equipment Gas or Electric? | Drop Down List | Gas;Electric | [6 empty] | Must be Electric | QA Checklist | Using the submitted manufacturer spec sheet validate the fuel source type (electric or gas) | The equipment must be electric | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 29
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | Any | Any | Any | QA Checklist | 4 | Used or rebuilt equipment are not eligible. | Yes | New Equipment | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 43
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | A | Any | Any | EECP | 5 | Qualifying cabinets must not exceed the maximum idle energy rate of 25 W/ft3 for full-size cabinets and 35 W/ft3 for half-size cabinets, in accordance with the American Society for Testing and Materials (ASTM) Standard Test Method for the Performance of Hot Food Holding Cabinets (F2140). | Yes | Idle Energy Rate | Max Idle Energy Rate (watts/ft3) | Numeric Value | [7 empty] | Must be <= 12 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Idle Energy Rate (watts/ft3) | The Max Idle Energy Rate (watts/ft3) Must be <= 12 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-09-09 | Kenny Liljestrom |  | Add | 32
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | B | Any | Any | EECP | 6 | Qualifying cabinets must not exceed the maximum idle energy rate of 25 W/ft3 for full-size cabinets and 35 W/ft3 for half-size cabinets, in accordance with the American Society for Testing and Materials (ASTM) Standard Test Method for the Performance of Hot Food Holding Cabinets (F2140). | Yes | Idle Energy Rate | Max Idle Energy Rate (watts/ft3) | Numeric Value | [7 empty] | Must be <= 18 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Idle Energy Rate (watts/ft3) | The Max Idle Energy Rate (watts/ft3) Must be <= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-09-09 | Kenny Liljestrom |  | Add | 32
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | A | Any | Any | EECP | 7 | This measure includes new full-size (≥ 15 ft3) and half-size (< 15 ft3) insulated food holding cabinets. | Yes | Size | Insulated Holding Cabinet Size (square feet) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Insulated Holding Cabinet Size (square feet) | The Insulated Holding Cabinet Size (square feet) Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 45
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | B | Any | Any | EECP | 8 | This measure includes new full-size (≥ 15 ft3) and half-size (< 15 ft3) insulated food holding cabinets. | Yes | Size | Insulated Holding Cabinet Size (square feet) | Numeric Value | [7 empty] | Must be < 15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Insulated Holding Cabinet Size (square feet) | The Insulated Holding Cabinet Size (square feet) Must be < 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 45
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | Any | Any | Any | EECP | 9 | Eligible holding cabinets must be listed on the Food Service Technology Center (FSTC) qualified product list (https://fishnick.com/saveenergy/rebates/). | Yes | FSTC Listed | Is the installed holding cabinet listed on the Food Service Technology Center (FSTC) qualified product list (https://fishnick.com/saveenergy/rebates/)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Using the rebate site below, determine if the product is listed as being a qualified unit https://fishnick.com/saveenergy/rebates/ | The product must be listed as a qualified product on the fishnick website | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 151
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | Any | Any | Any | EECP | 10 | All measures must be electric hot food holding cabinets that are fully insulated (i.e., on all sides) and have solid or transparent doors designed to maintain the temperature of hot food that has been cooked using a separate appliance. This measure does not include cook-and-hold or retherm equipment. | Yes |  | Holding cabinet fully insulated (i.e., on all sides) and has solid or transparent doors? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | When inspecting the holding cabinet, check to see if the cabinet has any glass or transparent (see through) doors or sides | The holding cabinet must be fully insulated with no glass or transparent doors or sides | QA Checklist | Use the manufacturer spec sheet to check to see if the cabinet has any glass or transparent (see through) doors or sides | The holding cabinet must be fully insulated with no glass or transparent doors or sides |  | 2021-09-09 | Kenny Liljestrom |  | Add | 88
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | Any | Any | Any | EECP | 11 | This measure does not include cook-and-hold or retherm equipment. Any cabinets considered in this measure must have an electric resistance heating element, passive holding cabinets with no heating elements are not eligible. | Yes |  | Is this an electric resistance, passive, or cook-and-hold retherm equipment? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet to determine if the holding cabinet is classified as a cook-and-hold retherm equipment | The cook-and-hold retherm type of cabinet is not eligible for rebate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated property label with new measure requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 76
0 | SWFS008 | 1 | Conveyor Oven, Gas, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
0 | SWFS008 | 1 | Conveyor Oven, Gas, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
0 | SWFS008 | 1 | Conveyor Oven, Gas, Commercial | Any | Any | Any | EECP | 3 | Used or rebuilt equipment are not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
0 | SWFS008 | 1 | Conveyor Oven, Gas, Commercial | Any | Any | Any | EECP | 4 | This measure includes new commercial gas conveyor ovens that exceed baking energy efficiency of ≥ 42% and have an idle energy rate ≤ 57,000 Btu/hr, utilizing ASTM Standard F1817. | Yes | Size | Conveyer Width (in) | Numeric Value | [7 empty] | Must be <= 25 | QA Checklist | Use the manufacturer spec sheet to validate the Conveyer Width (in) | The Conveyer Width (in) Must be <= 25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 19
0 | SWFS008 | 1 | Conveyor Oven, Gas, Commercial | Any | Any | Any | EECP | 5 | This measure includes new commercial gas conveyor ovens that exceed baking energy efficiency of ≥ 42% and have an idle energy rate ≤ 57,000 Btu/hr, utilizing ASTM Standard F1817. | Yes | Idle Energy Rate | Max Idle Energy Rate (Btu/h) | Numeric Value | [7 empty] | Must be <= 57000 | QA Checklist | Use the manufacturer spec sheet to validate the Max Idle Energy Rate (Btu/h) | The Max Idle Energy Rate (Btu/h) Must be <= 57000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 28
0 | SWFS008 | 1 | Conveyor Oven, Gas, Commercial | Any | Any | Any | EECP | 6 | This measure includes new commercial gas conveyor ovens that exceed baking energy efficiency of ≥ 42% and have an idle energy rate ≤ 57,000 Btu/hr, utilizing ASTM Standard F1817. | Yes | EFFICIENCY | Min. Cooking Energy Efficiency (%) | Numeric Value | [7 empty] | Must be >= 42% | QA Checklist | Use the manufacturer spec sheet to validate the Min. Cooking Energy Efficiency (%) | The Min. Cooking Energy Efficiency (%) Must be >= 42% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 34
1 | SWFS010 | 1 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
1 | SWFS010 | 1 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
1 | SWFS010 | 1 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any | QA Checklist | 3 | Used or rebuilt equipment are not eligible. | Yes | New Equipment | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
1 | SWFS010 | 1 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any | EECP | 4 | This measure is a new commercial on-demand hand-wrap machine that replaces a conventional or always-on hand-wrap machine. The measure must use either a mechanical or optical control system. | Yes | Control System | Does the installed unit use a mechanical or optical control system? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer spec sheet to validate if the unit has a mechanical or optical control system | The equipment must have a mechanical or optical control system | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured for all programs | 2021-06-15 | Kenny Liljestrom |  | Add | 67
1 | SWFS010 | 1 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any | EECP | 5 | This measure is a new commercial on-demand hand-wrap machine that replaces a conventional or always-on hand-wrap machine. The measure must use either a mechanical or optical control system. | Yes | Replace | Did the installed unit replace a conventional or always-on hand-wrap machine? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured for all programs | 2021-06-15 | Kenny Liljestrom |  | Add | 77
1 | SWFS010 | 1 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any | EECP | 6 | This measure is a new commercial on-demand hand-wrap machine that replaces a conventional or always-on hand-wrap machine. The measure must use either a mechanical or optical control system. | Yes | On Demand Hand Wrap Machine | Is the installed unit an on-demand hand-wrap machine? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer spec sheet to validate if the unit is an on-demand type | The equipment must be listed as being an on-demand type unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured for all programs | 2021-06-21 | Kenny Liljestrom |  | Add | 53
0 | SWFS010 | 2 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  |  | 12
0 | SWFS010 | 2 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  |  | 5
0 | SWFS010 | 2 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any | EECP | 3 | Used or rebuilt equipment are not eligible. | Yes | New Equipment | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  |  | 43
0 | SWFS010 | 2 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any | EECP | 4 | This measure is a new commercial on-demand hand-wrap machine that replaces a conventional or always-on hand-wrap machine. The measure must use either a mechanical or optical control system. | Yes | Control System | Does the installed unit use a mechanical or optical control system? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer spec sheet to validate if the unit has a mechanical or optical control system | The equipment must have a mechanical or optical control system | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured for all programs | 2021-06-15 | Kenny Liljestrom |  |  | 67
0 | SWFS010 | 2 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any | EECP | 5 | This measure is a new commercial on-demand hand-wrap machine that replaces a conventional or always-on hand-wrap machine. The measure must use either a mechanical or optical control system. | Yes | Replace | Did the installed unit replace a conventional or always-on hand-wrap machine? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured for all programs | 2021-06-15 | Kenny Liljestrom |  |  | 77
0 | SWFS010 | 2 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any | EECP | 6 | This measure is a new commercial on-demand hand-wrap machine that replaces a conventional or always-on hand-wrap machine. The measure must use either a mechanical or optical control system. | Yes | On Demand Hand Wrap Machine | Is the installed unit an on-demand hand-wrap machine? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer spec sheet to validate if the unit is an on-demand type | The equipment must be listed as being an on-demand type unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured for all programs | 2021-06-21 | Kenny Liljestrom |  |  | 53
1 | SWFS011 | 2 | Fryer, Commercial | Any | Any | Any | EECP | 1 | - | No | Manufacturer | Manufacturer | Text Box | [8 empty] | - | - | - | - | - | - |  | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 12
1 | SWFS011 | 2 | Fryer, Commercial | Any | Any | Any | EECP | 2 | - | No | Model | Model | Text Box | [8 empty] | - | - | - | - | - | - |  | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 5
1 | SWFS011 | 2 | Fryer, Commercial | Any | Any | Any | EECP | 3 | Used or rebuilt equipment are not eligible. | No | New Equipment | New Equipment | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | - | - | - | - | - | - | Not configured in original upload | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 13
1 | SWFS011 | 2 | Fryer, Commercial | Any | Any | Any | EECP | 4 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | No | Type | Fryer Type | Drop Down List | Standard Vat;Large Vat | [7 empty] | - | - | - | - | - | - |  | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 10
1 | SWFS011 | 2 | Fryer, Commercial | Any | Any | Any | EECP | 5 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | No | Energy Star Qualified | ENERGY STAR Qualified? | Drop Down List | Yes;No | [7 empty] | - | - | - | - | - | - |  | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 22
1 | SWFS011 | 2 | Fryer, Commercial | A | Any | Any | EECP | 6 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | No | Idle Energy Rate | Idle Energy Rate (watts) | Numeric Value | [7 empty] | If 'Energy Star Qualified" is 'No' then make active If 'Fryer Type' is 'Standard Vat' then must be <= 800 If 'Fryer Type' is 'Large Vat' then must be <= 1100 | - | - | - | - | - | - |  | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 24
1 | SWFS011 | 2 | Fryer, Commercial | A | Any | Any | EECP | 7 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | No | EFFICIENCY | Heavy Load Cooking Efficiency (%) | Numeric Value | [7 empty] | If 'Energy Star Qualified" is 'No' then make active If 'Fryer Type' is 'Standard Vat' then must be >= 83% If 'Fryer Type' is 'Large Vat' then must be >= 80 | - | - | - | - | - | - |  | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 33
1 | SWFS011 | 2 | Fryer, Commercial | B | Any | Any | EECP | 8 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | No | Idle Energy Rate | Idle Energy Rate (Btu/hr) | Numeric Value | [7 empty] | If 'Energy Star Qualified" is 'No' then make active If 'Fryer Type' is 'Standard Vat' then must be <= 9000 If 'Fryer Type' is 'Large Vat' then must be <= 12000 | - | - | - | - | - | - |  | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 25
1 | SWFS011 | 2 | Fryer, Commercial | B | Any | Any | EECP | 9 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | No | EFFICIENCY | Heavy Load Cooking Efficiency (%) | Numeric Value | [7 empty] | If 'Energy Star Qualified" is 'No' then make active Must be >= 50% | - | - | - | - | - | - |  | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 33
0 | SWFS011 | 3 | Fryer, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-07 | Kenny Liljestrom |  | Add | 12
0 | SWFS011 | 3 | Fryer, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-07 | Kenny Liljestrom |  | Add | 5
0 | SWFS011 | 3 | Fryer, Commercial | Any | Any | Any | EECP | 3 | Used or rebuilt equipment are not eligible. | Yes | New Equipment | New Equipment | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 13
0 | SWFS011 | 3 | Fryer, Commercial | Any | Any | Any | EECP | 4 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | Type | Fryer Type | Drop Down List | Standard Vat;Large Vat | [7 empty] | QA Checklist | Use the manufacturer spec sheet to validate the fryer vat type (Standard or Large) | The vat type must meet the measure case description | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 10
0 | SWFS011 | 3 | Fryer, Commercial | Any | Any | Any | EECP | 5 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | Energy Star Qualified | ENERGY STAR Qualified? | Drop Down List | Yes;No | [7 empty] | QA Checklist | Use the EnergyStar database and compare the listed make and model in EECP to the list | The database needs to have the make and model listed in EECP as being EnergyStar qualified; if not, criteria below must be met | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 22
0 | SWFS011 | 3 | Fryer, Commercial | A | Any | Any | EECP | 6 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | Idle Energy Rate | Idle Energy Rate (watts) | Numeric Value | [7 empty] | If 'Energy Star Qualified" is 'No' then make active If 'Fryer Type' is 'Standard Vat' then must be <= 800 If 'Fryer Type' is 'Large Vat' then must be <= 1100 | QA Checklist | Use the manufacturer spec sheet to validate the Idle Energy Rate (watts) | If 'Energy Star Qualified" is 'No' then, If 'Fryer Type' is 'Standard Vat' then must be <= 800 If 'Fryer Type' is 'Large Vat' then must be <= 1100 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 24
0 | SWFS011 | 3 | Fryer, Commercial | A | Any | Any | EECP | 7 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | EFFICIENCY | Heavy Load Cooking Efficiency (%) | Numeric Value | [7 empty] | If 'Energy Star Qualified" is 'No' then make active If 'Fryer Type' is 'Standard Vat' then must be >= 83% If 'Fryer Type' is 'Large Vat' then must be >= 80 | QA Checklist | Use the manufacturer spec sheet to validate the Heavy Load Cooking Efficiency (%) | If 'Energy Star Qualified" is 'No' then, If 'Fryer Type' is 'Standard Vat' then must be >= 83% If 'Fryer Type' is 'Large Vat' then must be >= 80 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS011 | 3 | Fryer, Commercial | B | Any | Any | EECP | 8 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | Idle Energy Rate | Idle Energy Rate (Btu/hr) | Numeric Value | [7 empty] | If 'Energy Star Qualified" is 'No' then make active If 'Fryer Type' is 'Standard Vat' then must be <= 9000 If 'Fryer Type' is 'Large Vat' then must be <= 12000 | QA Checklist | Use the manufacturer spec sheet to validate the Idle Energy Rate (Btu/hr) | If 'Energy Star Qualified" is 'No' then, If 'Fryer Type' is 'Standard Vat' then must be <= 9000 If 'Fryer Type' is 'Large Vat' then must be <= 12000 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 25
0 | SWFS011 | 3 | Fryer, Commercial | B | Any | Any | EECP | 9 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | EFFICIENCY | Heavy Load Cooking Efficiency (%) | Numeric Value | [7 empty] | If 'Energy Star Qualified" is 'No' then make active Must be >= 50% | QA Checklist | Use the manufacturer spec sheet to validate the Heavy Load Cooking Efficiency (%) | If 'Energy Star Qualified" is 'No' then, Must be >= 50% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS011 | 3 | Fryer, Commercial | C | Any | Any | EECP | 10 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | Idle Energy Rate | Idle Energy Rate (Btu/hr) | Numeric Value | [7 empty] | If 'Energy Star Qualified" is 'No' then make active Must be <= 6100 | QA Checklist | Use the manufacturer spec sheet to validate the Idle Energy Rate (Btu/hr) | If 'Energy Star Qualified" is 'No' then, Must be <= 6100 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 25
0 | SWFS011 | 3 | Fryer, Commercial | C | Any | Any | EECP | 11 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | EFFICIENCY | Heavy Load Cooking Efficiency (%) | Numeric Value | [7 empty] | If 'Energy Star Qualified" is 'No' then make active Must be >= 60% | QA Checklist | Use the manufacturer spec sheet to validate the Heavy Load Cooking Efficiency (%) | If 'Energy Star Qualified" is 'No' then, Must be >= 60% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 33
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom |  | Add | 12
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom |  | Add | 5
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any | EECP | 3 | Used or rebuilt controls are not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 43
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any | EECP | 4 | This measure pertains to the purchase and installation of a new commercial kitchen exhaust hood control system installed in an existing or a new dedicated commercial kitchen exhaust hood and makeup air system. Specific requirements include: • The measure requires the installation of temperature sensor(s) in the hood exhaust collar or within the hood, and/or an optic sensor on the end of the hood or within the hood that senses cooking conditions and allows the system to automatically vary the rate of exhaust and make-up (ventilation) air by adjusting unit fan speeds accordingly. • The installation of a DCKV must include a temperature or optic sensor that senses cooking conditions. • The control system must be used in conjunction with a variable-speed drive (VSD) on the fan motor. • Installations in a new exhaust hood must have a total kitchen hood airflow ≤ 5,000 cfm. • If installed in an existing exhaust hood > 5,000 cfm, the existing hood must have been installed before July 1, 2014, when the 2013 California Building Energy Efficiency Standards (Title 24) standards came into effect. See Code Requirements | Yes |  | Installation includes temperature sensor(s) and/or an optic sensor to adjust fan speeds? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Using the manufacturer spec sheet validate if the unit comes with a temperature sensor(s) and/or an optic sensor which adjusts the fan speeds | The unit must come with a temperature sensor(s) and/or an optic sensor which adjusts the fan speeds | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 88
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any | EECP | 5 | This measure pertains to the purchase and installation of a new commercial kitchen exhaust hood control system installed in an existing or a new dedicated commercial kitchen exhaust hood and makeup air system. Specific requirements include: • The measure requires the installation of temperature sensor(s) in the hood exhaust collar or within the hood, and/or an optic sensor on the end of the hood or within the hood that senses cooking conditions and allows the system to automatically vary the rate of exhaust and make-up (ventilation) air by adjusting unit fan speeds accordingly. • The installation of a DCKV must include a temperature or optic sensor that senses cooking conditions. • The control system must be used in conjunction with a variable-speed drive (VSD) on the fan motor. • Installations in a new exhaust hood must have a total kitchen hood airflow ≤ 5,000 cfm. • If installed in an existing exhaust hood > 5,000 cfm, the existing hood must have been installed before July 1, 2014, when the 2013 California Building Energy Efficiency Standards (Title 24) standards came into effect. See Code Requirements | Yes |  | Does the control system use a Variable Speed Drive (VSD) on the fan motor? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Using the manufacturer spec sheet validate if the unit comes with a variable speed drive (VSD) for the fan motor | The unit must come with a VSD for the fan | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 74
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any | EECP | 6 | - | No | HP | HP | Numeric Value | [8 empty] | - | - | - | - | - | - | Duplicate property, can be removed and replaced by Size (Rated-HP) already configured | 2021-08-19 | Kenny Liljestrom |  | Add | 2
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any | EECP | 7 | Good to have | Yes | Size | Rated-HP | Numeric Value | [8 empty] | Inspections | If accessible, photograph the nameplate of the fan motor to capture the power rating (hp) | The power rating on the nameplate should match what is listed in EECP | QA Checklist | Using the installation report or manufacturer spec sheet, determine the power rating (hp) of the fan motor or VSD | The power rating (hp) should match what is listed in EECP; if unable to determine the fan size, this property can be assumed correct |  | 2021-08-19 | Kenny Liljestrom |  | Add | 8
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any | EECP | 8 | This measure pertains to the purchase and installation of a new commercial kitchen exhaust hood control system installed in an existing or a new dedicated commercial kitchen exhaust hood and makeup air system. Specific requirements include: • The measure requires the installation of temperature sensor(s) in the hood exhaust collar or within the hood, and/or an optic sensor on the end of the hood or within the hood that senses cooking conditions and allows the system to automatically vary the rate of exhaust and make-up (ventilation) air by adjusting unit fan speeds accordingly. • The installation of a DCKV must include a temperature or optic sensor that senses cooking conditions. • The control system must be used in conjunction with a variable-speed drive (VSD) on the fan motor. • Installations in a new exhaust hood must have a total kitchen hood airflow ≤ 5,000 cfm. • If installed in an existing exhaust hood > 5,000 cfm, the existing hood must have been installed before July 1, 2014, when the 2013 California Building Energy Efficiency Standards (Title 24) standards came into effect. See Code Requirements | Yes |  | Exhaust hood airflow (cfm) | Numeric Value | [7 empty] | If >= 5000 then make available 'Installation date of existing hood' | QA Checklist | Using the installation report validate the exhaust hood flow rate (cfm) | If the airflow is less than 5,000 cfm, there are no validation criteria; if the flowrate is 5,000 cfm or above, the installation date property needs to be validated | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 26
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any | EECP | 9 | This measure pertains to the purchase and installation of a new commercial kitchen exhaust hood control system installed in an existing or a new dedicated commercial kitchen exhaust hood and makeup air system. Specific requirements include: • The measure requires the installation of temperature sensor(s) in the hood exhaust collar or within the hood, and/or an optic sensor on the end of the hood or within the hood that senses cooking conditions and allows the system to automatically vary the rate of exhaust and make-up (ventilation) air by adjusting unit fan speeds accordingly. • The installation of a DCKV must include a temperature or optic sensor that senses cooking conditions. • The control system must be used in conjunction with a variable-speed drive (VSD) on the fan motor. • Installations in a new exhaust hood must have a total kitchen hood airflow ≤ 5,000 cfm. • If installed in an existing exhaust hood > 5,000 cfm, the existing hood must have been installed before July 1, 2014, when the 2013 California Building Energy Efficiency Standards (Title 24) standards came into effect. See Code Requirements | Yes |  | Installation date of existing hood | Date | Make available if Exhaust Hood Airflow > 5000 | [6 empty] | Must be before 07/01/2014 | QA Checklist | If the installation report indicates the airflow of the unit is >= 5,000 cfm, check the installation report for when the exhaust hood was installed in the building | If the airflow rate is >= 5,000 cfm, the exhaust hood must have been installed after 7/1/2014 in order to qualify | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 34
0 | SWFS013 | 1 | Low-Flow Pre-Rinse Spray Valve | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-23 | Kenny Liljestrom |  | Add | 12
0 | SWFS013 | 1 | Low-Flow Pre-Rinse Spray Valve | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-23 | Kenny Liljestrom |  | Add | 5
0 | SWFS013 | 1 | Low-Flow Pre-Rinse Spray Valve | Any | Any | Any | EECP | 3 | Used or rebuilt equipment are not eligible. | Yes |  | New Equipment | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-23 | Kenny Liljestrom |  | Add | 13
0 | SWFS013 | 1 | Low-Flow Pre-Rinse Spray Valve | Any | Any | Any | EECP | 4 | This measure is restricted to operations with natural gas water heaters only. | Yes | Gas PRSV | Is the hot water for the installed commercial-grade PRSV supplied from natural gas water heaters? | Drop Down List | Yes;No | [7 empty] | Inspections | Locate the water heater supplying the spray valve; you may need to ask the customer for the location of the water heater; photograph the nameplate of the water heater or observe the fuel source (look for the yellow pipe going into the water heater) | The water heater serving the spray valve needs to be fueled by natural gas | QA Checklist | Use photographs from the implementer or inspections team to verify if the water heater on site is fueled by natural gas | The water heater serving the spray valve needs to be fueled by natural gas |  | 2021-08-23 | Kenny Liljestrom |  | Add | 97
0 | SWFS013 | 1 | Low-Flow Pre-Rinse Spray Valve | A | Any | Any | EECP | 5 | This measure is defined as a new commercial-grade PRSV with a maximum flow rate ≤ 1.07 gpm that replaces a PRSV with a maximum flow rate of 1.20 gpm for a spray force of > 5.0 ozf and ≤ 8.0 ozf; and as a new commercial-grade PRSV with a maximum flow rate ≤ 0.75 gpm that replaces a PRSV with a maximum flow rate of 1.00 gpm for a spray force of < 5.0 ozf. | Yes | Gas PRSV flow rate | Was a new commercial-grade PRSV with a maximum flow rate = 1.07 gpm installed that replaced an existing PRSV with a maximum flow rate of 1.20 gpm for a spray force of > 5.0 ozf and < 8.0 ozf? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer spec sheet to verify the new spray valve has a maximum flow rate of 1.07 gallons per minute (gpm) | The spray valve must have a maximum flow rate of 1.07 gpm | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-23 | Kenny Liljestrom |  | Add | 191
0 | SWFS013 | 1 | Low-Flow Pre-Rinse Spray Valve | B | Any | Any | EECP | 6 | This measure is defined as a new commercial-grade PRSV with a maximum flow rate ≤ 1.07 gpm that replaces a PRSV with a maximum flow rate of 1.20 gpm for a spray force of > 5.0 ozf and ≤ 8.0 ozf; and as a new commercial-grade PRSV with a maximum flow rate ≤ 0.75 gpm that replaces a PRSV with a maximum flow rate of 1.00 gpm for a spray force of < 5.0 ozf. | Yes | Gas PRSV flow rate | Was a new commercial-grade PRSV with a maximum flow rate = 0.75 gpm installed that replaced an existing PRSV with a maximum flow rate of 1.00 gpm for a spray force of < 5.0 ozf? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer spec sheet to verify the new spray valve has a maximum flow rate of 0.75 gallons per minute (gpm) | The spray valve must have a maximum flow rate of 0.75 gpm | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-23 | Kenny Liljestrom |  | Add | 177
1 | SWFS014 | 2 | Rack Oven, Gas, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
1 | SWFS014 | 2 | Rack Oven, Gas, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
1 | SWFS014 | 2 | Rack Oven, Gas, Commercial | Any | Any | Any | EECP | 3 | Used or rebuilt equipment is not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
1 | SWFS014 | 2 | Rack Oven, Gas, Commercial | A | Any | Any | EECP | 4 | This measure includes new commercial gas single and double rack ovens tested to meet or exceed baking energy efficiency of 50%. | Yes | Size | Oven Size | Drop Down List | Single;Double | [6 empty] | Must be 'Single' | QA Checklist | Use the submitted manufacturer spec sheet to determine the oven size (single or double) | The oven must be listed as a Single oven in the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-23 | Kenny Liljestrom |  | Add | 9
1 | SWFS014 | 2 | Rack Oven, Gas, Commercial | B | Any | Any | EECP | 5 | This measure includes new commercial gas single and double rack ovens tested to meet or exceed baking energy efficiency of 50%. | Yes | Size | Oven Size | Drop Down List | Single;Double | [6 empty] | Must be 'Double' | QA Checklist | Use the submitted manufacturer spec sheet to determine the oven size (single or double) | The oven must be listed as a Double oven in the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 9
1 | SWFS014 | 2 | Rack Oven, Gas, Commercial | Any | Any | Any | EECP | 6 | This measure includes new commercial gas single and double rack ovens tested to meet or exceed baking energy efficiency of 50%. | Yes | EFFICIENCY | Min. Cooking Energy Efficiency (%) | Numeric Value | [7 empty] | Must be >= 50% | QA Checklist | Use the submitted manufacturer spec sheet to determine the oven min cooking efficiency (%) | The min cooking efficiency must be >= 50% and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 34
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | Any | Any | Any | EECP | 3 | Used or rebuilt equipment is not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | Any | Any | Any | EECP | 4 | The replacement automatic conveyor broiler must have a catalyst and an input rate less than 80 kBtu/hr or a dual stage or modulating gas valve with a capability of throttling the input rate below 80 kBtu/hr. | Yes | Existing Conveyor Input Rate | Does the installed automatic conveyor broiler have a catalyst and an input rate less than 80 kBtu/hr or a dual stage or modulating gas valve with a capability of throttling the input rate below 80 kBtu/hr? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Check the manufacturer spec sheet to see if the automatic conveyor broiler has a catalyst and an input rate less than 80 kBtu/hr or a dual stage or modulating gas valve with a capability of throttling the input rate below 80 kBtu/hr | The replacement automatic conveyor broiler must have a catalyst and an input rate less than 80 kBtu/hr or a dual stage or modulating gas valve with a capability of throttling the input rate below 80 kBtu/hr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 205
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | A | Any | Any | EECP | 5 | Measure Description | Yes | Size | Automatic Conveyor Broilers Belt Width (in) | Numeric Value | [7 empty] | Must be < 20 | QA Checklist | Check the manufacturer spec sheet for the belt width on the broiler | The belt width needs to be < 20 inches | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | B | Any | Any | EECP | 6 | Measure Description | Yes | Size | Automatic Conveyor Broilers Belt Width (in) | Numeric Value | [7 empty] | Must be >= 20 and <= 26 | QA Checklist | Check the manufacturer spec sheet for the belt width on the broiler | The belt width needs to be >= 20 and < 26 inches | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | C | Any | Any | EECP | 7 | Measure Description | Yes | Size | Automatic Conveyor Broilers Belt Width (in) | Numeric Value | [7 empty] | Must be > 26 | QA Checklist | Check the manufacturer spec sheet for the belt width on the broiler | The belt width needs to be > 26 inches | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | A | Any | Any | EECP | 8 | The existing (base case) broiler must be an automatic conveyor broiler than can maintain a temperature above 600 °F with a tested idle rate greater than: • 40 kBtu/hr for a belt narrower than 20" • 60 kBtu/hr for a belt between 20 and 26" • 70 kBtu/hr for a belt wider than 26" | Yes | Existing Conveyor Temp | Was the existing broiler an automatic conveyor broiler than could maintain a temperature above 600 °F with a tested idle rate greater than 40 kBtu/hr for a belt narrower than 20 inches? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 185
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | B | Any | Any | EECP | 9 | The existing (base case) broiler must be an automatic conveyor broiler than can maintain a temperature above 600 °F with a tested idle rate greater than: • 40 kBtu/hr for a belt narrower than 20" • 60 kBtu/hr for a belt between 20 and 26" • 70 kBtu/hr for a belt wider than 26" | Yes | Existing Conveyor Temp | Was the existing broiler an automatic conveyor broiler than could maintain a temperature above 600 °F with a tested idle rate greater than 40 kBtu/hr for a belt narrower than 20 inches? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 185
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | C | Any | Any | EECP | 10 | The existing (base case) broiler must be an automatic conveyor broiler than can maintain a temperature above 600 °F with a tested idle rate greater than: • 40 kBtu/hr for a belt narrower than 20" • 60 kBtu/hr for a belt between 20 and 26" • 70 kBtu/hr for a belt wider than 26" | Yes | Existing Conveyor Temp | Was the existing broiler an automatic conveyor broiler than could maintain a temperature above 600 °F with a tested idle rate greater than 40 kBtu/hr for a belt narrower than 20 inches? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 185
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | Any | Any | Any | EECP | 11 | The conveyor broiler must be replaced by a conveyor broiler similar in size or smaller. | Yes | Existing Conveyor Replaced | Is the existing conveyor broiler being replaced by a conveyor broiler similar in size or smaller? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 97
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | Any | Any | Any | EECP | 12 | Installation shall comply with all policies, codes and regulations within the installation territory. | Yes |  | Installation complies with all policies, codes and regulations within the site territory? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-23 | Kenny Liljestrom |  | Add | 89
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | Any | Any | Any | EECP | 3 | Used or rebuilt equipment is not eligible. | Yes | New Equipment | New Equipment | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 13
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | Any | Any | Any | EECP | 4 | Other dishwasher types (conveyor, door-type, flight-type) are not eligible. | Yes | Undercounter dishwasher | Was an undercounter high temperature dishwasher installed (not another dishwasher types such as: conveyor, door-type, flight-type)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted manufacturer spec sheet to validate the dishwasher type | The dishwasher type must be listed as undercounter | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 131
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | A | Any | Any | EECP | 5 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [7 empty] | Must be <=0.86 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 0.86 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 44
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | B | Any | Any | EECP | 6 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [7 empty] | Must be <= 0.73 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 0.73 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 44
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | C | Any | Any | EECP | 7 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [7 empty] | Must be <= 1.19 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 1.19 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 44
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | D | Any | Any | EECP | 8 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [7 empty] | Must be <= 1.01 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 1.01 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 44
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | A | Any | Any | EECP | 9 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <= 0.50 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.50 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 25
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | B | Any | Any | EECP | 10 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <=0.43 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.43 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 25
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | C | Any | Any | EECP | 11 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <= 0.50 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.50 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 25
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | D | Any | Any | EECP | 12 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <=0.43 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.43 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 25
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 12
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 5
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | Any | Any | Any | QA Checklist | 3 | Used or rebuilt equipment is not eligible. | Yes | New Equipment | New Equipment | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | Any | Any | Any | QA Checklist | 4 | Other dishwasher types (conveyor, door-type, flight-type) are not eligible. | Yes | Undercounter dishwasher | Was an undercounter high temperature dishwasher installed (not another dishwasher types such as: conveyor, door-type, flight-type)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted manufacturer spec sheet to validate the dishwasher type | The dishwasher type must be listed as undercounter | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 131
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | A | Any | Any | EECP | 5 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [7 empty] | Must be <=0.86 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 0.86 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 44
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | B | Any | Any | EECP | 6 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [7 empty] | Must be <= 0.73 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 0.73 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 44
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | C | Any | Any | EECP | 7 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [7 empty] | Must be <= 1.19 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 1.19 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 44
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | D | Any | Any | EECP | 8 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [7 empty] | Must be <= 1.01 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 1.01 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 44
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | A | Any | Any | EECP | 9 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <= 0.30 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.30 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-09-09 | Kenny Liljestrom |  | Add | 25
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | B | Any | Any | EECP | 10 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <=0.26 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.26 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-09-09 | Kenny Liljestrom |  | Add | 25
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | C | Any | Any | EECP | 11 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <= 0.25 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.25 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-09-09 | Kenny Liljestrom |  | Add | 25
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | D | Any | Any | EECP | 12 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <=0.21 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.21 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-09-09 | Kenny Liljestrom |  | Add | 25
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | A | Any | Any | EECP | 13 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | EFFICIENCY | Max washing energy (kWh/rack) | Numeric Value | [7 empty] | Must be <=0.35 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum washing energy (kWh/rack) | The max washing energy rate must be <= 0.35 kWh/rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-09-09 | Kenny Liljestrom |  | Add | 29
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | B | Any | Any | EECP | 14 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | EFFICIENCY | Max washing energy (kWh/rack) | Numeric Value | [7 empty] | Must be <=0.30 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum washing energy (kWh/rack) | The max washing energy rate must be <= 0.30 kWh/rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-09-09 | Kenny Liljestrom |  | Add | 29
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | C | Any | Any | EECP | 15 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | EFFICIENCY | Max washing energy (kWh/rack) | Numeric Value | [7 empty] | Must be <=0.15 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum washing energy (kWh/rack) | The max washing energy rate must be <= 0.15 kWh/rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-09-09 | Kenny Liljestrom |  | Add | 29
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | D | Any | Any | EECP | 16 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | EFFICIENCY | Max washing energy (kWh/rack) | Numeric Value | [7 empty] | Must be <=0.13 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum washing energy (kWh/rack) | The max washing energy rate must be <= 0.13 kWh/rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-09-09 | Kenny Liljestrom |  | Add | 29
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-22 | Kenny Liljestrom |  |  | 12
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-22 | Kenny Liljestrom |  |  | 5
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | Any | Any | Any | QA Checklist | 3 | Used or rebuilt equipment is not eligible. | Yes | New Equipment | New Equipment | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-22 | Kenny Liljestrom |  |  | 13
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | Any | Any | Any | QA Checklist | 4 | Other dishwasher types (conveyor, door-type, flight-type) are not eligible. | Yes | Undercounter dishwasher | Was an undercounter high temperature dishwasher installed (not another dishwasher types such as: conveyor, door-type, flight-type)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted manufacturer spec sheet to validate the dishwasher type | The dishwasher type must be listed as undercounter | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-22 | Kenny Liljestrom |  |  | 131
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | A | Any | Any | EECP | 5 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [7 empty] | Must be <=0.86 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 0.86 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-22 | Kenny Liljestrom |  |  | 44
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | B | Any | Any | EECP | 6 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [7 empty] | Must be <= 0.73 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 0.73 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-22 | Kenny Liljestrom |  |  | 44
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | C | Any | Any | EECP | 7 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [7 empty] | Must be <= 1.19 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 1.19 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-22 | Kenny Liljestrom |  |  | 44
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | D | Any | Any | EECP | 8 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [7 empty] | Must be <= 1.01 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 1.01 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-22 | Kenny Liljestrom |  |  | 44
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | A | Any | Any | EECP | 9 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <= 0.30 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.30 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-11-22 | Kenny Liljestrom |  |  | 25
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | B | Any | Any | EECP | 10 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <=0.26 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.26 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-11-22 | Kenny Liljestrom |  |  | 25
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | C | Any | Any | EECP | 11 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <= 0.25 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.25 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-11-22 | Kenny Liljestrom |  |  | 25
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | D | Any | Any | EECP | 12 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <=0.21 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.21 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-11-22 | Kenny Liljestrom |  |  | 25
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | A | Any | Any | EECP | 13 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes |  | Max washing energy (kWh/rack) | Numeric Value | [7 empty] | Must be <=0.35 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum washing energy (kWh/rack) | The max washing energy rate must be <= 0.35 kWh/rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | B | Any | Any | EECP | 14 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes |  | Max washing energy (kWh/rack) | Numeric Value | [7 empty] | Must be <=0.30 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum washing energy (kWh/rack) | The max washing energy rate must be <= 0.30 kWh/rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | C | Any | Any | EECP | 15 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes |  | Max washing energy (kWh/rack) | Numeric Value | [7 empty] | Must be <=0.15 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum washing energy (kWh/rack) | The max washing energy rate must be <= 0.15 kWh/rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | D | Any | Any | EECP | 16 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes |  | Max washing energy (kWh/rack) | Numeric Value | [7 empty] | Must be <=0.13 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum washing energy (kWh/rack) | The max washing energy rate must be <= 0.13 kWh/rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-11-22 | Kenny Liljestrom |  |  | 29
0 | SWFS019 | 1 | Underfired Broiler, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
0 | SWFS019 | 1 | Underfired Broiler, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
0 | SWFS019 | 1 | Underfired Broiler, Commercial | Any | Any | Any | EECP | 3 | Used or rebuilt equipment is not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
0 | SWFS019 | 1 | Underfired Broiler, Commercial | Any | Any | Any | EECP | 4 | The measure case (replacement) underfired broiler must have an input rate ≤ 22 kBtu/hr/len-ft while maintaining a surface temperature of 600 °F, per ASTM F1695 standard. | Yes | ASTM standard | Installed broiler has an input rate <= 22 kBtu/hr/len-ft with a surface temperature of 600 °F? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the equipment is has the Input Rating listed (kBtu/hr/len-ft) and surface temperature (F) listed | The submitted installation report or manufacturer spec sheet needs to have the Input Rating listed as being <= 22 kBtu/hr/len-ft (or 22,000 Btu/hr/len-ft) and surface temperature of 600 F | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be updated to include the "<" symbol in the property label | 2021-06-15 | Kenny Liljestrom |  | Add | 94
0 | SWFS019 | 1 | Underfired Broiler, Commercial | Any | Any | Any | EECP | 5 | The base case broiler must be similar size or larger than the replacement unit. | Yes | Broiler size | Is the base case broiler a similar size or larger than the replacement unit? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 76
1 | SWFS019 | 2 | Underfired Broiler, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
1 | SWFS019 | 2 | Underfired Broiler, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
1 | SWFS019 | 2 | Underfired Broiler, Commercial | Any | Any | Any | EECP | 3 | Used or rebuilt equipment is not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
1 | SWFS019 | 2 | Underfired Broiler, Commercial | Any | Any | Any | EECP | 4 | The measure case (replacement) underfired broiler must have an input rate ≤ 22 kBtu/hr/len-ft while maintaining a surface temperature of 600 °F, per ASTM F1695 standard. | Yes | ASTM standard | Installed broiler has an input rate <= 22 kBtu/hr/len-ft with a surface temperature of 600 °F? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the equipment is has the Input Rating listed (kBtu/hr/len-ft) and surface temperature (F) listed | The submitted installation report or manufacturer spec sheet needs to have the Input Rating listed as being <= 22 kBtu/hr/len-ft (or 22,000 Btu/hr/len-ft) and surface temperature of 600 F | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be updated to include the "<" symbol in the property label | 2021-06-15 | Kenny Liljestrom |  | Add | 94
1 | SWFS019 | 2 | Underfired Broiler, Commercial | Any | Any | Any | EECP | 5 | The base case broiler must be similar size or larger than the replacement unit. | Yes | Broiler size | Is the base case broiler a similar size or larger than the replacement unit? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 76
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-15 | Kenny Liljestrom |  | Add | 12
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-15 | Kenny Liljestrom |  | Add | 5
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any | EECP | 3 | Used or rebuilt equipment are not eligible. | Yes | New Equipment | New Equipment | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | - | - | - | - | - | - | Remove property | 2021-07-15 | Kenny Liljestrom |  | Add | 13
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any | EECP | 4 | To qualify as a high performance conveyor toaster, the unit must meet the energy per sandwich requirement specified in the Measure Case Description. | Yes |  | Production Capacity (units/hr) | Numeric Value | [7 empty] | Must be >= 698 | - | - | - | - | - | - | Remove property | 2021-07-15 | Kenny Liljestrom | Measure property removed, workpaper requirements incorrectly identified in EECP upload. 7/15/2021 request to remove property from EECP and replace with Energy per Bun. | Add | 30
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any | EECP | 5 | To qualify as a high performance conveyor toaster, the unit must meet the energy per sandwich requirement specified in the Measure Case Description. | Yes |  | Idle Energy Rate (kW) | Numeric Value | [7 empty] | Must be <= 0.64 | - | - | - | - | - | - | Remove property | 2021-07-15 | Kenny Liljestrom | Measure property removed, workpaper requirements incorrectly identified in EECP upload. 7/15/2021 request to remove property from EECP and replace with Energy per Bun. | Add | 21
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any | EECP | 6 | To qualify as a high performance conveyor toaster, the unit must meet the energy per sandwich requirement specified in the Measure Case Description. | Yes |  | Cooking Energy Rate (kW) | Numeric Value | [7 empty] | Must be <= 2.0633 | - | - | - | - | - | - | Remove property | 2021-07-15 | Kenny Liljestrom | Measure property removed, workpaper requirements incorrectly identified in EECP upload. 7/15/2021 request to remove property from EECP and replace with Energy per Bun. | Add | 24
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any | EECP | 7 | To qualify as a high performance conveyor toaster, the unit must meet the energy per sandwich requirement specified in the Measure Case Description. | Yes |  | Preheat Energy Rate (kW) | Numeric Value | [7 empty] | Must be <= 2.1196 | - | - | - | - | - | - | Remove property | 2021-07-15 | Kenny Liljestrom | Measure property removed, workpaper requirements incorrectly identified in EECP upload. 7/15/2021 request to remove property from EECP and replace with Energy per Bun. | Add | 24
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any | EECP | 8 | To qualify as a high performance conveyor toaster, the unit must meet the energy per sandwich requirement specified in the Measure Case Description. | Yes |  | Preheat Time (mins) | Numeric Value | [7 empty] | Must be <= 9.83 | - | - | - | - | - | - | Remove property | 2021-07-15 | Kenny Liljestrom | Measure property removed, workpaper requirements incorrectly identified in EECP upload. 7/15/2021 request to remove property from EECP and replace with Energy per Bun. | Add | 19
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any | EECP | 9 | To qualify as a high performance conveyor toaster, the unit must meet the energy per sandwich requirement specified in the Measure Case Description. | Yes |  | Energy per Bun (W/bun) | Numeric Value | [7 empty] | Must be <=3.75 | QA Checklist | Use manufacturer specification sheet to determine if energy per bun is less than the measure case description, 3.75 W/bun | Use the equation: Energy per Bun = (Cooking Energy Rate, kW * 1,000 W/kW) / (Units produced per hour) *Cooking Energy Rate, kW: May be given in Watts, in which case remove the 1,000 W/kW conversion from the equation *Units produced per hour can be calculated by: (Units produced / time interval in seconds) * (60 sec / 1 min) * (60 min / 1 hr) This value needs to be equal to or less than 3.75 W/bun | QA Checklist | Consult with the manufacturer to determine if the energy per bun meets the measure case description of 3.75 W/bun | The manufacturer should be able to specify if the cooking energy and production rate of the unit results in a energy per bun of less than or equal to 3.75 W/bun | Add property | 2021-07-15 | Kenny Liljestrom | Added 7/15/2021 after review of measure properties and requirements. | Add | 22
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | UpDeemed | EECP | 1 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | UpDeemed | EECP | 2 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | Any | EECP | 3 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-02 | Kenny Liljestrom |  | Add | 12
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | Any | EECP | 4 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-02 | Kenny Liljestrom |  | Add | 5
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | UpDeemed | EECP | 5 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | UpDeemed | EECP | 6 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | UpDeemed | EECP | 7 | E-5152 Data Collection Requirements | Yes | Measure Size Category | Measure Size Category | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | UpDeemed | EECP | 8 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | UpDeemed | EECP | 9 | Required for SW Program | Yes | ZC | Zip Code | Numeric Value | [8 empty] | QA Checklist | Evaluate the zip code in EECP for accuracy | Ensure zip code is real and locatable | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-02 | Kenny Liljestrom | Configured for SW UpDeemed Program | Add | 8
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | UpDeemed | EECP | 10 | Required for SW Program | Yes | ClimateZone | CA Climate Zone | Formula | [7 empty] | Lookup table for ZC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-02 | Kenny Liljestrom | Configured for SW UpDeemed Program | Add | 15
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | Any | QA Checklist | 11 | Wall furnaces that are direct-vent systems that mount on an outside wall are not eligible. | Yes | - | Wall furnaces that are direct-vent systems that mount on an outside wall are not eligible. | None | [8 empty] | Inspections | Photograph the wall furnace and make note of it's location relative to the house or dwelling unit | The system should not be located outside | QA Checklist | Look for photographic evidence in the installation report indicating the unit is not installed outdoors | Photographs of the existing or installed system showing location of unit is not outside |  | 2021-07-02 | Kenny Liljestrom |  | Add | 90
1 | SWHC001 | 2 | Wall Furnace, Residential | A | Any | Any | EECP | 12 | Gravity wall furnaces ≤ 19,000 Btu/hr and ≥ 60,000 Btu/hr are not eligible | Yes | Gas Input Rating (Btu/hr) | Gas Input Rating (Btu/hr) | Numeric Value | [7 empty] | Must be ≥ 19,000 Btu/hr and ≤ 27,000 Btu/hr | Inspections | Photograph of the furnace nameplate showing the make and model; data can be crosschecked with specification sheet or ENERGYSTAR or ANSI databases; photograph of Gas Input rating (Btu/hr) | The Gas Input Rating (Btu/hr) must be between 19,000 and 60,000 Btu/hr | QA Checklist | Check the make and model against specification sheet, ENERGYSTAR or ANSI databases; to validate the Gas Input Rating (Btu/hr) | The Gas Input Rating (Btu/hr) must be between 19,000 and 60,000 Btu/hr | Not configured in original upload | 2022-05-17 | Kenny Liljestrom |  | Add | 25
1 | SWHC001 | 2 | Wall Furnace, Residential | B | Any | Any | EECP | 13 | Gravity wall furnaces ≤ 19,000 Btu/hr and ≥ 60,000 Btu/hr are not eligible | Yes | Gas Input Rating (Btu/hr) | Gas Input Rating (Btu/hr) | Numeric Value | [7 empty] | Must be > 27,000 Btu/hr and ≤ 46,000 Btu/hr | Inspections | Photograph of the furnace nameplate showing the make and model; data can be crosschecked with specification sheet or ENERGYSTAR or ANSI databases; photograph of Gas Input rating (Btu/hr) | The Gas Input Rating (Btu/hr) must be between 19,000 and 60,000 Btu/hr | QA Checklist | Check the make and model against specification sheet, ENERGYSTAR or ANSI databases; to validate the Gas Input Rating (Btu/hr) | The Gas Input Rating (Btu/hr) must be between 19,000 and 60,000 Btu/hr | Not configured in original upload | 2022-05-17 | Kenny Liljestrom |  | Add | 25
1 | SWHC001 | 2 | Wall Furnace, Residential | C | Any | Any | EECP | 14 | Gravity wall furnaces ≤ 19,000 Btu/hr and ≥ 60,000 Btu/hr are not eligible | Yes | Gas Input Rating (Btu/hr) | Gas Input Rating (Btu/hr) | Numeric Value | [7 empty] | Must be > 46,000 Btu/hr and ≤ 60,000 Btu/hr | Inspections | Photograph of the furnace nameplate showing the make and model; data can be crosschecked with specification sheet or ENERGYSTAR or ANSI databases; photograph of Gas Input rating (Btu/hr) | The Gas Input Rating (Btu/hr) must be between 19,000 and 60,000 Btu/hr | QA Checklist | Check the make and model against specification sheet, ENERGYSTAR or ANSI databases; to validate the Gas Input Rating (Btu/hr) | The Gas Input Rating (Btu/hr) must be between 19,000 and 60,000 Btu/hr | Not configured in original upload | 2022-05-17 | Kenny Liljestrom |  | Add | 25
1 | SWHC001 | 2 | Wall Furnace, Residential | D | Any | Any | EECP | 15 | Fan type wall furnaces ≤ 19,000 Btu/hr and ≥ 42,000 Btu/hr are not eligible | Yes | Gas Input Rating (Btu/hr) | Gas Input Rating (Btu/hr) | Numeric Value | [7 empty] | Must be ≥ 19,000 Btu/hr and ≤ 42,000 Btu/hr | Inspections | Photograph of the furnace nameplate showing the make and model; data can be crosschecked with specification sheet or ENERGYSTAR or ANSI databases; photograph of Gas Input rating (Btu/hr) | The Gas Input Rating (Btu/hr) must be between 19,000 and 42,000 Btu/hr | QA Checklist | Check the make and model against specification sheet, ENERGYSTAR or ANSI databases; to validate the Gas Input Rating (Btu/hr) | The Gas Input Rating (Btu/hr) must be between 19,000 and 42,000 Btu/hr | Not configured in original upload | 2022-05-17 | Kenny Liljestrom |  | Add | 25
1 | SWHC001 | 2 | Wall Furnace, Residential | A | Any | Any | EECP | 16 | E-5152 Data Collection Requirements | Yes | AFUE | AFUE % | Numeric Value | [7 empty] | Must be >70% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 70% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use EnergyStar or ANSI databases of equipment to check the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 70% |  | 2022-05-18 | Kenny Liljestrom |  |  | 6
1 | SWHC001 | 2 | Wall Furnace, Residential | B | Any | Any | EECP | 17 | E-5152 Data Collection Requirements | Yes | AFUE | AFUE % | Numeric Value | [7 empty] | Must be >70% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 70% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use EnergyStar or ANSI databases of equipment to check the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 70% |  | 2022-05-18 | Kenny Liljestrom |  |  | 6
1 | SWHC001 | 2 | Wall Furnace, Residential | C | Any | Any | EECP | 18 | E-5152 Data Collection Requirements | Yes | AFUE | AFUE % | Numeric Value | [7 empty] | Must be >70% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 70% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use EnergyStar or ANSI databases of equipment to check the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 70% |  | 2022-05-18 | Kenny Liljestrom |  |  | 6
1 | SWHC001 | 2 | Wall Furnace, Residential | D | Any | Any | EECP | 19 | E-5152 Data Collection Requirements | Yes | AFUE | AFUE % | Numeric Value | [7 empty] | Must be >82% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 82% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use EnergyStar or ANSI databases of equipment to check the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 82% |  | 2022-05-18 | Kenny Liljestrom |  |  | 6
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | Any | QA Checklist | 20 | The purchase invoice must be provided as a proof that the wall furnace has been purchased to replace a previously existing unit. Additionally, the customer must agree to a post measure installation inspection. | Yes | - | The purchase invoice must be provided as a proof that the wall furnace has been purchased to replace a previously existing unit. Additionally, the customer must agree to a post measure installation inspection. | [9 empty] | QA Checklist | Check the EECP documentation for an invoice | Ensure the purchase invoice is submitted as part of the uploaded documentation | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-02 | Kenny Liljestrom |  | Add | 209
0 | SWHC002 | 2 | Intermittent Pilot Light, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 12
0 | SWHC002 | 2 | Intermittent Pilot Light, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 5
0 | SWHC002 | 2 | Intermittent Pilot Light, Residential | Any | Any | Any | EECP | 3 | The customer must agree to a post installation inspection. | Yes |  | Has the customer agreed to a post installation inspection? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 58
0 | SWHC002 | 2 | Intermittent Pilot Light, Residential | B | Any | Any | EECP | 4 | Proof of purchase of a gravity wall furnace manufactured with an integrated intermittent pilot light must be provided. | Yes |  | Proof of purchase submitted showing Integrated intermittent pilot light in the wall furnace? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Check the documentation submitted to check for a proof of purchase documents (i.e. receipt and specification sheet) showing the new gravity wall furnace has an integrated intermittent pilot light | Proof of purchase documents must be submitted to verify the gravity wall furnace is new and has an intermittent integrated pilot light | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 92
0 | SWHC002 | 2 | Intermittent Pilot Light, Residential | B | Any | Any | EECP | 5 | Eligibility requirements for this measure are: • This measure pertains to gravity wall furnaces manufactured with integrated IPL controls, furnaces with a standing pilot light, and any fireplace with standing pilot light. • A furnace manufactured with integrated IPL controls can only replace a gravity wall furnace. • The IPL controls shall be capable of either using a battery or voltage line to effectively operate as intended. | Yes |  | New gravity wall furnace is replacing an existing gravity wall furnace? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 71
0 | SWHC002 | 2 | Intermittent Pilot Light, Residential | Any | Any | Any | EECP | 6 | Eligibility requirements for this measure are: • This measure pertains to gravity wall furnaces manufactured with integrated IPL controls, furnaces with a standing pilot light, and any fireplace with standing pilot light. • A furnace manufactured with integrated IPL controls can only replace a gravity wall furnace. • The IPL controls shall be capable of either using a battery or voltage line to effectively operate as intended. | Yes |  | Integrated pilot light controls are capable of using a battery or voltage line to operate? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer spec sheet to determine if the IPL is capable of using either a battery or electricity to operate | The controls must be capable of operating via a battery or direct line voltage (electricity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 90
0 | SWHC002 | 2 | Intermittent Pilot Light, Residential | A | Any | DnDeemDI | EECP | 7 | Implementation and installation requirements are: • For direct install installations, the wall furnace or fireplace insert shall be functional prior to the IPL retrofit. • For direct install installations, the IPL control cannot replace an existing functional or non- functional pilot light control on a furnace or fireplace insert. • Any technology manufacturer qualifies for measure offerings specified, if safety and all other regulations are met and the technology is commercially available. | Yes |  | Is the existing wall furnace or fireplace insert in working condition (not requiring major repairs)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | An installation report or photos of the existing system should be submitted to verify the existing equipment | The existing equipment must be in working condition, not in need of any major repairs or retrofits; this is difficult to distinguish but photographs of existing systems should suffice | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 100
0 | SWHC002 | 2 | Intermittent Pilot Light, Residential | Any | Any | DnDeemDI | EECP | 8 | Implementation and installation requirements are: • For direct install installations, the wall furnace or fireplace insert shall be functional prior to the IPL retrofit. • For direct install installations, the IPL control cannot replace an existing functional or non- functional pilot light control on a furnace or fireplace insert. • Any technology manufacturer qualifies for measure offerings specified, if safety and all other regulations are met and the technology is commercially available. | Yes |  | Does the existing wall furnace or fireplace insert have pilot light controls? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | QA Checklist | An installation report or photos of the existing system should be submitted to verify the existing equipment | The existing equipment must not have controls already installed for the pilot light | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 77
1 | SWHC004 | 1 | Space Heating Boiler | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-10 | Kenny Liljestrom |  | Add | 12
1 | SWHC004 | 1 | Space Heating Boiler | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-10 | Kenny Liljestrom |  | Add | 5
1 | SWHC004 | 1 | Space Heating Boiler | Any | Any | Any | EECP | 3 | Retire | Yes | Cap-kBtuh | Cap-kBtuh | Numeric Value | [8 empty] | - | - | - | - | - | - | Legacy property, retire | 2021-08-10 | Kenny Liljestrom |  | Add | 9
1 | SWHC004 | 1 | Space Heating Boiler | Any | Any | Any | EECP | 4 | Retire | Yes | OA Reset Control (degrees in Fahrenheit) | OA Reset Control (F) | Numeric Value | [8 empty] | - | - | - | - | - | - | Remove property, can be located in measure description | 2021-08-10 | Kenny Liljestrom |  | Add | 20
1 | SWHC004 | 1 | Space Heating Boiler | Any | Any | Any | EECP | 5 | Good to have | Yes | Rated Input (Btuh) | Rated Input (Btuh) | Numeric Value | [8 empty] | Inspections | Photograph the equipment nameplate to capture the Input Rating; commonly referenced with the units MMBtu/hr, kBtu/hr, or Btu/hr | The value on the nameplate, if listed in Btu/hr, should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Input Rating Btu/hr is listed | The capacity (Btu/hr) listed in EECP should match the value listed in the specification sheet | Update property name and property label, Remove validation criteria | 2021-08-10 | Kenny Liljestrom |  | Add | 18
1 | SWHC004 | 1 | Space Heating Boiler | Any | Any | Any | EECP | 6 | Retire | Yes | Size | Cap-kBtuh | Numeric Value | [8 empty] | - | - | - | - | - | - | Legacy property, retire | 2021-08-10 | Kenny Liljestrom |  | Add | 9
1 | SWHC004 | 1 | Space Heating Boiler | A | Any | Any | EECP | 7 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | AFUE (%) | Numeric Value | [7 empty] | Must be >= 84% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 8
1 | SWHC004 | 1 | Space Heating Boiler | B | Any | Any | EECP | 8 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 85% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | C | Any | Any | EECP | 9 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | D | Any | Any | EECP | 10 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | E | Any | Any | EECP | 11 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 83% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | E | Any | Any | EECP | 12 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes |  | Combustion Efficiency (%) | Numeric Value | [7 empty] | Must be >= 85% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Combustion Efficiency (%) is listed | The Combustion Efficiency (%) listed in EECP should match the value listed in the specification sheet | New property | 2021-08-10 | Kenny Liljestrom |  | Add | 25
1 | SWHC004 | 1 | Space Heating Boiler | F | Any | Any | EECP | 13 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | G | Any | Any | EECP | 14 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | H | Any | Any | EECP | 15 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 82% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | I | Any | Any | EECP | 16 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 80% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | J | Any | Any | EECP | 17 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 82% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | Any | Any | Any | EECP | 18 | The boiler must be used for space heating to induce human comfort, as defined by the California Appliance Efficiency Regulations (Title 20) and Building Energy Efficiency Standards (Title 24). | Yes | Title 24 | Boiler used for space comfort (not domestic or process hot water)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured for all SWHC004 measures | 2021-08-10 | Kenny Liljestrom |  | Add | 66
1 | SWHC004 | 1 | Space Heating Boiler | Any | Any | Any | QA Checklist | 19 | The installation address must have a commercial natural gas account. | Yes |  | The installation address must have a commercial natural gas account. | [9 empty] | QA Checklist | Use EECP to determine if the customer purchases natural gas from SDG&E | The customer must be an active account holder and purchase natural gas from SDG&E | - | - | - |  | 2021-08-10 | Kenny Liljestrom |  | Add | 68
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any | EECP | 1 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 12
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any | EECP | 2 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 5
0 | SWHC004 | 2 | Space Heating Boiler | A | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type is Residential Multifamily? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | Observe the building type | The building type must be Residential Multi-family | QA Checklist | Use the installation report to validate the building type | The building type must be Residential Multi-family | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 41
0 | SWHC004 | 2 | Space Heating Boiler | B | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | C | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | D | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | E | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | F | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | G | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | H | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | I | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | J | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [6 empty] | Must not be 'Residential Multifamily' | Inspections | Observe the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any | EECP | 4 |  | Yes | Serial Number | Condenser Serial Number | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 23
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any | EECP | 5 |  | Yes | RefNum | AHRI Reference Number | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any | EECP | 6 |  | Yes | RetailPrice | Retail Price | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any | EECP | 7 |  | Yes | ZC | Zip Code | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any | EECP | 8 |  | Yes | ClimateZone | CA Climate Zone | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any | EECP | 9 | Good to have | Yes | Rated Input (Btuh) | Rated Input (Btuh) | Numeric Value | [8 empty] | Inspections | Photograph the equipment nameplate to capture the Input Rating; commonly referenced with the units MMBtu/hr, kBtu/hr, or Btu/hr | The value on the nameplate, if listed in Btu/hr, should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Input Rating Btu/hr is listed | The capacity (Btu/hr) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 18
0 | SWHC004 | 2 | Space Heating Boiler | A | Any | Any | EECP | 10 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | AFUE (%) | Numeric Value | [7 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the AFUE (%) is listed | The AFUE (%) listed in EECP should match the value listed in the specification sheet; the value must be >= 94% | Updated validation criteria | 2021-09-09 | Kenny Liljestrom |  | Add | 8
0 | SWHC004 | 2 | Space Heating Boiler | B | Any | Any | EECP | 11 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 85% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | C | Any | Any | EECP | 12 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | D | Any | Any | EECP | 13 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | E | Any | Any | EECP | 14 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 83% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | E | Any | Any | EECP | 15 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes |  | Combustion Efficiency (%) | Numeric Value | [7 empty] | Must be >= 85% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Combustion Efficiency (%) is listed | The Combustion Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 25
0 | SWHC004 | 2 | Space Heating Boiler | F | Any | Any | EECP | 16 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | G | Any | Any | EECP | 17 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | H | Any | Any | EECP | 18 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 82% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | I | Any | Any | EECP | 19 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 80% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | J | Any | Any | EECP | 20 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 82% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any | EECP | 21 | The boiler must be used for space heating to induce human comfort, as defined by the California Appliance Efficiency Regulations (Title 20) and Building Energy Efficiency Standards (Title 24). | Yes | Title 24 | Boiler used for space comfort (not domestic or process hot water)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-09-09 | Kenny Liljestrom |  | Add | 66
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any | QA Checklist | 22 | The installation address must have a commercial natural gas account. | Yes | - | The installation address must have a commercial natural gas account. | [9 empty] | QA Checklist | Use EECP to determine if the customer purchases natural gas from SDG&E | The customer must be an active account holder and purchase natural gas from SDG&E | - | - | - |  | 2021-09-09 | Kenny Liljestrom |  | Add | 68
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | UpDeemed | EECP | 1 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any | EECP | 1 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 12
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | UpDeemed | EECP | 2 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any | EECP | 2 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 5
1 | SWHC004 | 3 | Space Heating Boiler | A | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | Observe the building type | The building type must be Residential Multi-family | QA Checklist | Use the installation report to validate the building type | The building type must be Residential Multi-family | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | B | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | C | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | D | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | E | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | F | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | G | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | H | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | I | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | J | Any | Any | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Inspections | Observe the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any | EECP | 4 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any | EECP | 4 | E-5152 Data Collection Requirements | Yes | Rated Input (Btuh) | Rated Input (Btuh) | Numeric Value | [8 empty] | Inspections | Photograph the equipment nameplate to capture the Input Rating; commonly referenced with the units MMBtu/hr, kBtu/hr, or Btu/hr | The value on the nameplate, if listed in Btu/hr, should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Input Rating Btu/hr is listed | The capacity (Btu/hr) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 18
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any | EECP | 5 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC004 | 3 | Space Heating Boiler | A | Any | Any | EECP | 5 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | AFUE (%) | Numeric Value | [7 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the AFUE (%) is listed | The AFUE (%) listed in EECP should match the value listed in the specification sheet; the value must be >= 94% | Updated validation criteria | 2021-09-09 | Kenny Liljestrom |  | Add | 8
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any | EECP | 6 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC004 | 3 | Space Heating Boiler | B | Any | Any | EECP | 6 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 85% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any | EECP | 7 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
1 | SWHC004 | 3 | Space Heating Boiler | C | Any | Any | EECP | 7 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any | EECP | 8 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
1 | SWHC004 | 3 | Space Heating Boiler | D | Any | Any | EECP | 8 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | E | Any | Any | EECP | 9 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 83% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | E | Any | Any | EECP | 10 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Combustion Efficiency (%) | Combustion Efficiency (%) | Numeric Value | [7 empty] | Must be >= 85% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Combustion Efficiency (%) is listed | The Combustion Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 25
1 | SWHC004 | 3 | Space Heating Boiler | F | Any | Any | EECP | 11 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | G | Any | Any | EECP | 12 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | H | Any | Any | EECP | 13 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 82% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | I | Any | Any | EECP | 14 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 80% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | J | Any | Any | EECP | 15 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 82% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any | EECP | 16 | The boiler must be used for space heating to induce human comfort, as defined by the California Appliance Efficiency Regulations (Title 20) and Building Energy Efficiency Standards (Title 24). | Yes | Title 24 | Boiler used for space comfort (not domestic or process hot water)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-09-09 | Kenny Liljestrom |  | Add | 66
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any | QA Checklist | 17 | The installation address must have a commercial natural gas account. | Yes | - | The installation address must have a commercial natural gas account. | [9 empty] | QA Checklist | Use EECP to determine if the customer purchases natural gas from SDG&E | The customer must be an active account holder and purchase natural gas from SDG&E | - | - | - |  | 2021-09-09 | Kenny Liljestrom |  |  | 68
0 | SWHC005 | 1 | Water-Cooled Chiller | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-10 | Kenny Liljestrom |  | Add | 12
0 | SWHC005 | 1 | Water-Cooled Chiller | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-10 | Kenny Liljestrom |  | Add | 5
0 | SWHC005 | 1 | Water-Cooled Chiller | Any | Any | Any | EECP | 3 | Good to have | Yes | Nominal Capacity (Tons) | Nominal Capacity (tons) | Numeric Value | [8 empty] | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 23
0 | SWHC005 | 1 | Water-Cooled Chiller | A | Any | Any | EECP | 4 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.540 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.540 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | A | Any | Any | EECP | 5 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.340 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.340 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | B | Any | Any | EECP | 6 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.572 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.572 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | B | Any | Any | EECP | 7 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.360 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.360 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | C | Any | Any | EECP | 8 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.506 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.506 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | C | Any | Any | EECP | 9 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.332 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.332 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | D | Any | Any | EECP | 10 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.536 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.536 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | D | Any | Any | EECP | 11 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.351 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.351 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | E | Any | Any | EECP | 12 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.497 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.497 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | E | Any | Any | EECP | 13 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.323 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.323 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | F | Any | Any | EECP | 14 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.527 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.527 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | F | Any | Any | EECP | 15 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.342 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.342 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | G | Any | Any | EECP | 16 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.497 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.497 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | G | Any | Any | EECP | 17 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.323 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.323 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | H | Any | Any | EECP | 18 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.527 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.527 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | H | Any | Any | EECP | 19 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.342 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.342 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | I | Any | Any | EECP | 20 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.591 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.591 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | I | Any | Any | EECP | 21 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.374 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.374 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | J | Any | Any | EECP | 22 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.626 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.626 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | J | Any | Any | EECP | 23 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.396 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.396 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | K | Any | Any | EECP | 24 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.578 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.578 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | K | Any | Any | EECP | 25 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.374 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.374 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | L | Any | Any | EECP | 26 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.612 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.612 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | L | Any | Any | EECP | 27 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.396 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.396 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | M | Any | Any | EECP | 28 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.531 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.531 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | M | Any | Any | EECP | 29 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.349 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.349 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | N | Any | Any | EECP | 30 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.563 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.563 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | N | Any | Any | EECP | 31 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.369 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.369 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | O | Any | Any | EECP | 32 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.638 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.638 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | O | Any | Any | EECP | 33 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.417 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.417 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | P | Any | Any | EECP | 34 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.675 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.675 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | P | Any | Any | EECP | 35 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.441 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.441 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | Q | Any | Any | EECP | 36 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.497 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.497 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | Q | Any | Any | EECP | 37 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.323 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.323 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | R | Any | Any | EECP | 38 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.527 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.527 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | R | Any | Any | EECP | 39 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.342 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.342 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | S | Any | Any | EECP | 40 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.663 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.663 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | S | Any | Any | EECP | 41 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.425 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.425 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | T | Any | Any | EECP | 42 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.702 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.702 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | T | Any | Any | EECP | 43 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.450 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.450 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | Any | Any | Any | QA Checklist | 44 | All measures related to constant speed screw, constant speed centrifugal, and frictionless chillers are excluded due to the stringency of the tiers specified for the 2020 update of the Database of Energy Efficient Resources (DEER) and equipment availability in the market. | Yes |  | All measures related to constant speed screw, constant speed centrifugal, and frictionless chillers are excluded due to the stringency of the tiers specified for the 2020 update of the Database of Energy Efficient Resources (DEER) and equipment availability in the market. | [9 empty] | QA Checklist | Using the manufacturer spec sheet, verify the chiller is not a constant speed or frictionless type chiller | The chiller type should match the measure case description (Centrifugal w/VSD or Screw w/ VSD) and not be constant speed or frictionless | - | - | - |  | 2021-08-11 | Kenny Liljestrom |  | Add | 272
1 | SWHC005 | 2 | Water-Cooled Chiller | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-22 | Kenny Liljestrom |  |  | 12
1 | SWHC005 | 2 | Water-Cooled Chiller | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-22 | Kenny Liljestrom |  |  | 5
1 | SWHC005 | 2 | Water-Cooled Chiller | Any | Any | Any | EECP | 3 | Good to have | Yes | Nominal Capacity (Tons) | Nominal Capacity (tons) | Numeric Value | [8 empty] | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 23
1 | SWHC005 | 2 | Water-Cooled Chiller | A | Any | Any | EECP | 4 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.540 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.540 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | A | Any | Any | EECP | 5 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.340 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.340 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | B | Any | Any | EECP | 6 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.572 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.572 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | B | Any | Any | EECP | 7 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.360 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.360 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | C | Any | Any | EECP | 8 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.506 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.506 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | C | Any | Any | EECP | 9 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.332 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.332 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | D | Any | Any | EECP | 10 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.536 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.536 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | D | Any | Any | EECP | 11 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.351 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.351 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | E | Any | Any | EECP | 12 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.497 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.497 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | E | Any | Any | EECP | 13 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.323 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.323 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | F | Any | Any | EECP | 14 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.527 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.527 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | F | Any | Any | EECP | 15 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.342 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.342 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | G | Any | Any | EECP | 16 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.497 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.497 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | G | Any | Any | EECP | 17 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.323 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.323 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | H | Any | Any | EECP | 18 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.527 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.527 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | H | Any | Any | EECP | 19 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.342 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.342 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | I | Any | Any | EECP | 20 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.591 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.591 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | I | Any | Any | EECP | 21 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.374 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.374 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | J | Any | Any | EECP | 22 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.626 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.626 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | J | Any | Any | EECP | 23 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.396 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.396 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | K | Any | Any | EECP | 24 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.578 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.578 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | K | Any | Any | EECP | 25 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.374 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.374 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | L | Any | Any | EECP | 26 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.612 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.612 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | L | Any | Any | EECP | 27 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.396 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.396 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | M | Any | Any | EECP | 28 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.531 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.531 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | M | Any | Any | EECP | 29 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.349 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.349 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | N | Any | Any | EECP | 30 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.563 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.563 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | N | Any | Any | EECP | 31 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.369 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.369 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | O | Any | Any | EECP | 32 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.638 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.638 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | O | Any | Any | EECP | 33 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.417 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.417 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | P | Any | Any | EECP | 34 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.675 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.675 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | P | Any | Any | EECP | 35 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.441 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.441 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | Q | Any | Any | EECP | 36 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.497 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.497 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | Q | Any | Any | EECP | 37 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.323 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.323 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | R | Any | Any | EECP | 38 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.527 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.527 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | R | Any | Any | EECP | 39 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.342 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.342 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | S | Any | Any | EECP | 40 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.663 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.663 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | S | Any | Any | EECP | 41 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.425 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.425 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | T | Any | Any | EECP | 42 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.702 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.702 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | T | Any | Any | EECP | 43 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [7 empty] | Must be <= 0.450 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.450 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | Any | Any | Any | QA Checklist | 44 | All measures related to constant speed screw, constant speed centrifugal, and frictionless chillers are excluded due to the stringency of the tiers specified for the 2020 update of the Database of Energy Efficient Resources (DEER) and equipment availability in the market. | Yes |  | All measures related to constant speed screw, constant speed centrifugal, and frictionless chillers are excluded due to the stringency of the tiers specified for the 2020 update of the Database of Energy Efficient Resources (DEER) and equipment availability in the market. | [9 empty] | QA Checklist | Using the manufacturer spec sheet, verify the chiller is not a constant speed or frictionless type chiller | The chiller type should match the measure case description (Centrifugal w/VSD or Screw w/ VSD) and not be constant speed or frictionless | - | - | - |  | 2021-11-22 | Kenny Liljestrom |  |  | 272
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | A | Any | Any | EECP | 3 | Required for defining Energy Use | Yes | Host Equipment | Host equipment type? | Drop Down List | AC Only Unit;AC Unit with Gas Heat;Heat Pump;Variable Volume AC Unit with Gas Heat; | [6 empty] | Must be 'AC Only Unit' | QA Checklist | Use the manufacturer spec sheet to determine the HVAC equipment type | The HVAC type must be listed as Packaged Air Conditioner or Rooftop Unit (not an AC with a furnace) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 20
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | B | Any | Any | EECP | 4 | Required for defining Energy Use | Yes | Host Equipment | Host equipment type? | Drop Down List | AC Only Unit;AC Unit with Gas Heat;Heat Pump;Variable Volume AC Unit with Gas Heat; | [6 empty] | Must be 'AC Unit with Gas Heat' | QA Checklist | Use the manufacturer spec sheet to determine the HVAC equipment type | The HVAC type must be listed as Packaged Air Conditioner with Gas Furnace or Heating | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 20
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | C | Any | Any | EECP | 5 | Required for defining Energy Use | Yes | Host Equipment | Host equipment type? | Drop Down List | AC Only Unit;AC Unit with Gas Heat;Heat Pump;Variable Volume AC Unit with Gas Heat; | [6 empty] | Must be 'Heat Pump' | QA Checklist | Use the manufacturer spec sheet to determine the HVAC equipment type | The HVAC type must be listed as a Heat Pump | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 20
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | D | Any | Any | EECP | 6 | Required for defining Energy Use | Yes | Host Equipment | Host equipment type? | Drop Down List | AC Only Unit with Gas Heat;Heat Pump;Variable Volume AC Unit with Gas Heat; | [6 empty] | Must be 'Variable Volume AC Unit with Gas Heat' | QA Checklist | Use the manufacturer spec sheet to determine the HVAC equipment type | The HVAC type must be listed as a Variable Air Volume Unit with Gas Furnace or heating | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property needs to be updated with correct validation criteria | 2021-06-15 | Kenny Liljestrom |  | Add | 20
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | Any | Any | Any | EECP | 7 | This measure does not apply if the rooftop unit (RTU) has a fully operational and/or non-snapdisc sensor and is adjusted to the appropriate changeover setpoint based on the number of thermostat stages available for cooling. | Yes |  | Existing RTU could adjust the changeover setpoint based on the number of thermostat cooling stages? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload, similar in language to 'Changeover Setpoint' | 2021-08-24 | Kenny Liljestrom |  | Add | 99
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | Any | Any | Any | EECP | 8 | This measure requires field documentation of the existing conditions that verify the measure was necessary and that the measure was successfully applied. | Yes | Field docs | Was field documentation of the existing conditions that verify the measure was necessary and that the measure was successfully applied submitted? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Review the submitted documentation in EECP to check the existing conditions of the system were recorded | This measure requires field documentation of the existing conditions that verify the measure was necessary and that the measure was successfully applied. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 145
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | Any | Any | Any | EECP | 9 | Additional technician verification of thermostat wiring and the number of cooling stages that should be performed to ensure that the first stage of cooling is dedicated to economizer operation and two-stage thermostat operation is enabled where possible. | Yes | Tech verification | Was add. tech verification of thermostat wiring and number of cooling stages that should be performed to ensure the 1st stage of cooling is dedicated to economizer operation and 2-stage thermostat operation is enabled performed if possible? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 240
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | Any | Any | Any | EECP | 10 | The controller changeover setpoint should be adjusted appropriately based on the available number of thermostat cooling stages. | Yes | Changeover Setpoint | Was the controller changeover setpoint adjusted appropriately based on the available number of thermostat cooling stages? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 121
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | Any | Any | Any | EECP | 11 | Contractors and technicians that implement the measure must meet all certification and training requirements in accordance with program requirements. | Yes | Cert and Train | Do the contractors and technicians that implement the measure meet all certification and training requirements in accordance with program requirements? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 151
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | Any | Any | Any | EECP | 12 | Contractors and technicians that implement this measure must ensure that the existing unit does not already have the supply fan in automatic mode or switched OFF during unoccupied periods. This measure does not apply if the unoccupied supply fan operation is already set to “Auto” or intermittent. | Yes | Switched Off | Did the existing unit have the supply fan in automatic mode or switched OFF during unoccupied periods? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 102
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | C | Any | Any | EECP | 13 | The measure SWHC009C (cDXHP) excludes building type WRf. | Yes |  | Is the HVAC type a DX Heat Pump (cDXHP) and the building a refrigerated warehouse (WRf)? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-24 | Kenny Liljestrom |  | Add | 88
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | D | Any | Any | EECP | 14 | Measure offering SWHC009D (cPVVG) excludes building type Asm, EPr, ERC, Gro, MLI, RFF, RSD, RtL, RtS, SCn, WRf | Yes |  | HVAC type is a packaged VAV with gas furnace (cPVVG)? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet to determine the HVAC equipment type | The HVAC system must not be listed as a packaged variable air volume unit with a gas furnace | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-24 | Kenny Liljestrom |  | Add | 53
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | D | Any | Any | EECP | 14 | Measure offering SWHC009D (cPVVG) excludes building type Asm, EPr, ERC, Gro, MLI, RFF, RSD, RtL, RtS, SCn, WRf | Yes |  | Building type one of the following: Asm, EPr, ERC, Gro, MLI, RFF, RSD, RtL, RtS, SCn, WRf? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-24 | Kenny Liljestrom |  | Add | 90
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | UpDeemed | EECP | 1 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | UpDeemed | EECP | 2 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | Any | EECP | 3 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-11 | Kenny Liljestrom |  | Add | 12
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | Any | EECP | 4 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-11 | Kenny Liljestrom |  | Add | 5
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | UpDeemed | EECP | 5 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | UpDeemed | EECP | 6 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | UpDeemed | EECP | 7 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | UpDeemed | EECP | 8 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | Any | EECP | 9 | The measure is only applicable for classrooms in education primary schools (EPr), education secondary schools (ESe), and education re-locatable classrooms (ERC). This measure is not applicable for education community colleges, and education universities, unless these buildings have relocatable classrooms with packaged HVAC units. This measure is applicable to all vintages. | Yes | Installation Epr | Building Type | Drop Down List | Education primary schools (EPr);Education secondary schools (ESe);Education re-locatable classrooms (ERC); | [7 empty] | QA Checklist | Use EECP to determine the site location type | The building should be a primary education school (K-8), Secondary education school (9-12), or relocatable classrooms at any Primary, Secondary, Universities, or Community College school types | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property needs to be updated fully to be in compliance with the workpaper; update property label, property values, and remove validation criteria | 2021-08-11 | Kenny Liljestrom |  | Add | 13
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | Any | EECP | 10 | The measure requires installation of an HVAC occupancy sensing thermostat in the classroom. This control equipment includes, but is not limited to: • An occupancy sensing thermostat • An occupancy sensor (wired or wireless) • Wiring (if wired) • Signal receiver and power pack (if wireless) | Yes | System Include | Does the system include following? 1.An occupancy sensing thermostat 2. An occupancy sensor (wired or wireless) 3. Wiring (if wired) 4. Signal receiver and power pack (if wireless) | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | An installation report should indicate the components installed as part of the project | The components need to include: 1. An occupancy sensing thermostat 2. An occupancy sensor (wired or wireless) 3. Wiring (if wired) 4. Signal receiver and power pack (if wireless) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-11 | Kenny Liljestrom |  | Add | 180
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | QA Checklist | 1 | The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Yes |  | The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Drop Down List | Air-Conditioning, Heating, and Refrigeration Institute (AHRI);Consortium for Energy Efficiency (CEE) database;Manufacturers specification sheets | [7 empty] | QA Checklist | Document how you plan to validate the equipment properties related to this measure | The options for verification include: • Air-Conditioning, Heating, and Refrigeration Institute (AHRI) • Consortium for Energy Efficiency (CEE) database • Manufacturers specification sheets | - | - | - |  | 2021-08-11 | Kenny Liljestrom |  | Add | 444
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Manufacturer | Condenser Manufacturer | Text Box | [8 empty] | Inspections | Photograph the condenser (outdoor) equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet | Update property label | 2021-08-11 | Kenny Liljestrom |  | Add | 22
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 3 | - | Yes | Model | Condenser Model | Text Box | [8 empty] | Inspections | Photograph the condenser (outdoor) equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet | Update property label | 2021-08-11 | Kenny Liljestrom |  | Add | 15
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 4 | Good for Tracking | Yes | RefNum | AHRI Reference Number | Text Box | [8 empty] | QA Checklist | Use the data from EECP to check the AHRI equipment database; this reference number may also help in identifying other equipment specifications including type, capacity, EER, and IEER | Ensure the AHRI number matches with the make and model of the equipment | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update EECP sort order (this on top) | 2021-08-11 | Kenny Liljestrom |  | Add | 21
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 5 | - | Yes | Evaporator Manufacturer | Evaporator Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet |  | 2021-08-11 | Kenny Liljestrom |  | Add | 23
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 6 | - | Yes | Evaporator Model | Evaporator Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet |  | 2021-08-11 | Kenny Liljestrom |  | Add | 16
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 7 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes | System Type | System Type | Drop Down List | Split System;Unitary;Other; | [7 empty] | - | - | - | - | - | - | Property can be removed | 2021-08-11 | Kenny Liljestrom |  | Add | 11
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 8 | Good to have for tracking | Yes | Serial Number | Condenser Serial Number | Text Box | [8 empty] | Inspections | Photograph the condenser (outdoor) equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number listed in EECP should match the serial number listed in the invoice or installation report | Update EECP sorting order, below Condenser Model | 2021-08-11 | Kenny Liljestrom |  | Add | 23
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 9 | Good to have for tracking | Yes | RetailPrice | Retail Price | Numeric Value | [8 empty] | QA Checklist | Use the customer submitted invoice to verify the price of the unit | The value on the invoice should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-11 | Kenny Liljestrom |  | Add | 12
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed | EECP | 10 | Required for UpDeemed Programs | Yes | ZC | Zip Code | Numeric Value | [8 empty] | QA Checklist | Evaluate the zip code in EECP for accuracy | Ensure zip code is real and locatable | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-11 | Kenny Liljestrom |  | Add | 8
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed | EECP | 11 | Required for UpDeemed Programs | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-11 | Kenny Liljestrom |  | Add | 15
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 12 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes |  | Replacement like-for-like (i.e. air conditioner for an air conditioner or heat pump for heat pump)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 99
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 13 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes |  | Existing Equipment within +/- 5% of the replacement equipment Cooling Capacity (kBtuh)? | Drop Down List | Yes;No; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 87
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 14 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes |  | Contractor provided load calculations showing new unit is sized correctly for the load? | Drop Down List | Yes;No;N/A; | [6 empty] | If 'Is the Existing Equipment Cooling Capacity (kBtuh) within +/- 5% of the replacement equipment cooling capacity (kBtuh)?' is 'No' then must be 'Yes' Else must be N/A | QA Checklist | Review the EECP documentation and look for any load calculations submitted by the implementer | The load calculations from the implementer are used to justify an increase in load from the existing HVAC unit; the load calculations should show justification, which can be assisted by engineering, for new loads or inadequate load sizing of the original system | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 87
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 15 | Central systems and domestic hot water systems are not eligible. Package terminal air conditioning units, which are units manufactured for installation through a wall or window and are usually ≤ 2 tons, are not eligible. | Yes |  | System Type | Drop Down List | Air Conditioner or Heat Pump;Packaged Terminal Air Conditioner (PTAC);Packaged Terminal Heat Pump (PTHP);Central System; | [6 empty] | Must be 'Air Conditioner or Heat Pump' | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the System Type is listed | The System Type listed in EECP should match the type listed in the invoice, installation report, or spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 11
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 16 | Good to have | Yes |  | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be >= 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 24
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | A | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | B | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | C | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 12.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | D | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 13.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | E | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | F | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | G | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 12.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | H | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 10.8 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 10.8 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | I | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | J | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 12.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | K | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 10.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 10.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | L | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 11.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | M | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | N | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | O | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | P | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Q | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | R | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 10.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 10.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | S | Any | Any | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 10.8 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 10.8 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | A | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 13.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | B | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 13.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | C | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 14.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 14.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | D | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 13.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | E | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 13.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | F | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 13.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | G | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 14.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 14.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | H | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 12.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | I | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 12.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | J | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 15.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | K | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 11.6 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.6 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | L | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 12.3 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.3 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | M | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 13.8 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.8 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | N | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 32
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | O | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 32
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | P | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 32
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Q | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 32
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | R | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 32
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | S | Any | Any | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 32
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | QA Checklist | 19 | Field inspections should be performed to verify the condenser/unit model number for quality assurance purposes. | Yes |  | Has a field inspection been performed to verify the condenser and if applicable evaporator make and model? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Indicate if an inspection was completed by the inspections team | There is no pass or fail criteria | - | - | - |  | 2021-08-11 | Kenny Liljestrom |  | Add | 106
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | QA Checklist | 1 | The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Yes | - | The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Drop Down List | Air-Conditioning, Heating, and Refrigeration Institute (AHRI);Consortium for Energy Efficiency (CEE) database;Manufacturers specification sheets | [7 empty] | QA Checklist | Document how you plan to validate the equipment properties related to this measure | The options for verification include: • Air-Conditioning, Heating, and Refrigeration Institute (AHRI) • Consortium for Energy Efficiency (CEE) database • Manufacturers specification sheets | - | - | - |  | 2021-11-22 | Kenny Liljestrom |  |  | 444
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 2 | Data collection requirements for midstream and upstream deliveries, when possible, the program administrator (PA) shall claim the “specific building type savings” in which the equipment will be installed and submit that information at claims level on CEDARS website. In cases where there is no “building type” information available for a given project, program administrator shall claim the weighted savings of “Com” building type.” | Yes | - | Building Type | Text Box | [8 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report or invoice to determine the building type the equipment was installed at | The building type should match what is listed in EECP | Configure at enrollment level | 2021-11-22 | Kenny Liljestrom |  |  | 13
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed | EECP | 3 | Data Collection Requirements For upstream and midstream programs, data collection requirements are as follows: R1503 Site ID - A unique identifier for the installed location of the incentivized equipment Equipment ID - A unique identifier for each unit of incentivized equipment on the site Measure Size Category - General size or capacity range specific to each measure type Equipment manufacturer Equipment model number Rated capacity Rated efficiency unit - The engineering unit basis for the efficiency or performance rating Rated efficiency - Efficiency or performance rating value for the rated efficiency unit basis Quantity per sales transaction, project or site Existing equipment type (i.e., AC or HP) for the NR MAT | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-13 | Kenny Liljestrom |  |  | 7
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed | EECP | 4 | Data Collection Requirements For upstream and midstream programs, data collection requirements are as follows: R1503 Site ID - A unique identifier for the installed location of the incentivized equipment Equipment ID - A unique identifier for each unit of incentivized equipment on the site Measure Size Category - General size or capacity range specific to each measure type Equipment manufacturer Equipment model number Rated capacity Rated efficiency unit - The engineering unit basis for the efficiency or performance rating Rated efficiency - Efficiency or performance rating value for the rated efficiency unit basis Quantity per sales transaction, project or site Existing equipment type (i.e., AC or HP) for the NR MAT | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-13 | Kenny Liljestrom |  |  | 12
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed | EECP | 5 | Data Collection Requirements For upstream and midstream programs, data collection requirements are as follows: R1503 Site ID - A unique identifier for the installed location of the incentivized equipment Equipment ID - A unique identifier for each unit of incentivized equipment on the site Measure Size Category - General size or capacity range specific to each measure type Equipment manufacturer Equipment model number Rated capacity Rated efficiency unit - The engineering unit basis for the efficiency or performance rating Rated efficiency - Efficiency or performance rating value for the rated efficiency unit basis Quantity per sales transaction, project or site Existing equipment type (i.e., AC or HP) for the NR MAT | Yes | Measure Size Category | Measure Size Category | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-13 | Kenny Liljestrom |  |  | 21
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | A | NR | UpDeemed | EECP | 6 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | B | NR | UpDeemed | EECP | 7 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | C | NR | UpDeemed | EECP | 8 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | D | NR | UpDeemed | EECP | 9 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | E | NR | UpDeemed | EECP | 10 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | F | NR | UpDeemed | EECP | 11 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | G | NR | UpDeemed | EECP | 12 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | H | NR | UpDeemed | EECP | 13 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | I | NR | UpDeemed | EECP | 14 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | J | NR | UpDeemed | EECP | 15 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | K | NR | UpDeemed | EECP | 16 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | L | NR | UpDeemed | EECP | 17 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | M | NR | UpDeemed | EECP | 18 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | O | NR | UpDeemed | EECP | 19 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | P | NR | UpDeemed | EECP | 20 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Q | NR | UpDeemed | EECP | 21 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | R | NR | UpDeemed | EECP | 22 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | S | NR | UpDeemed | EECP | 23 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 24 | E-5152 Data Collection Requirements | Yes | Manufacturer | Condenser Manufacturer | Text Box | [8 empty] | Inspections | Photograph the condenser (outdoor) equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 22
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 25 | E-5152 Data Collection Requirements | Yes | Model | Condenser Model | Text Box | [8 empty] | Inspections | Photograph the condenser (outdoor) equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 15
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed | EECP | 26 | E-5152 Data Collection Requirements | Yes | Serial Number | Condenser Serial Number | Text Box | [8 empty] | Inspections | Photograph the condenser (outdoor) equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number listed in EECP should match the serial number listed in the invoice or installation report | Update EECP sorting order, below Condenser Model | 2021-11-22 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed | EECP | 27 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [8 empty] | QA Checklist | Use the data from EECP to check the AHRI equipment database; this reference number may also help in identifying other equipment specifications including type, capacity, EER, and IEER | Ensure the AHRI number matches with the make and model of the equipment | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update EECP sort order (this on top) | 2021-11-22 | Kenny Liljestrom |  |  | 21
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed | EECP | 28 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | System Type | System Type | Drop Down List | Split System;Unitary;Other; | [7 empty] | - | - | - | - | - | - | Property can be removed | 2021-11-22 | Kenny Liljestrom |  |  | 11
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed | EECP | 29 | E-5152 Data Collection Requirements | Yes | Evaporator Manufacturer | Evaporator Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet |  | 2021-11-22 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed | EECP | 30 | E-5152 Data Collection Requirements | Yes | Evaporator Model | Evaporator Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet |  | 2021-11-22 | Kenny Liljestrom |  |  | 16
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed | EECP | 31 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [8 empty] | QA Checklist | Use the customer submitted invoice to verify the price of the unit | The value on the invoice should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-22 | Kenny Liljestrom |  |  | 12
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed | EECP | 32 | Required for UpDeemed Programs | Yes | ZC | Zip Code | Numeric Value | [8 empty] | QA Checklist | Evaluate the zip code in EECP for accuracy | Ensure zip code is real and locatable | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-22 | Kenny Liljestrom |  |  | 8
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed | EECP | 33 | Required for UpDeemed Programs | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-22 | Kenny Liljestrom |  |  | 15
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed | EECP | 34 | Required for UpDeemed Programs | No | Refrigerant Type | Refrigerant Type | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the refrigerant type | The listed refrigerant in EECP should match the nameplate | QA Checklist | Use the make and model number to locate the refrigerant type | The refrigerant type should be listed on the manufacturer specfication sheet or can be validated with nameplate data | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 16
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 35 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | - | Replacement like-for-like (i.e. air conditioner for an air conditioner or heat pump for heat pump)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Property removed based on discussion with CPUC on removal of +/-5% |  | 99
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 36 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | - | Existing Equipment within +/- 5% of the replacement equipment Cooling Capacity (kBtuh)? | Drop Down List | Yes;No; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Property removed based on discussion with CPUC on removal of +/-5% |  | 87
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | EECP | 37 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | - | Contractor provided load calculations showing new unit is sized correctly for the load? | Drop Down List | Yes;No;N/A; | [6 empty] | If 'Is the Existing Equipment Cooling Capacity (kBtuh) within +/- 5% of the replacement equipment cooling capacity (kBtuh)?' is 'No' then must be 'Yes' Else must be N/A | QA Checklist | Review the EECP documentation and look for any load calculations submitted by the implementer | The load calculations from the implementer are used to justify an increase in load from the existing HVAC unit; the load calculations should show justification, which can be assisted by engineering, for new loads or inadequate load sizing of the original system | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom | Property removed based on discussion with CPUC on removal of +/-5% |  | 87
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | QA Checklist | 38 | Central systems and domestic hot water systems are not eligible. Package terminal air conditioning units, which are units manufactured for installation through a wall or window and are usually ≤ 2 tons, are not eligible. | No | - | System Type | Drop Down List | Air Conditioner;Heat Pump;Other; | [6 empty] | Must be 'Air Conditioner or Heat Pump' | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the System Type is listed | The System Type listed in EECP should match the type listed in the invoice, installation report, or spec sheet | - | - | - |  | 2021-11-22 | Kenny Liljestrom | Property does not need to be included in EECP |  | 11
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | A | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 65 <= x < 134 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | B | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 65 <= x < 134 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | C | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 65 <= x < 134 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | D | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 65 <= x < 134 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | E | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 134 <= x < 239 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | F | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 134 <= x < 239 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | G | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 134 <= x < 239 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | H | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 240 <= x < 759 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | I | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 240 <= x < 759 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | J | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 240 <= x < 759 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | K | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be > 760 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | L | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be > 760 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | M | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be > 760 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | N | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 65 <= x < 134 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | O | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 65 <= x < 134 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | P | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 134 <= x < 239 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Q | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 134 <= x < 239 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | R | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 240 <= x < 759 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | S | Any | Any | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 240 <= x < 759 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | A | Any | Any | EECP | 40 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | B | Any | Any | EECP | 41 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | C | Any | Any | EECP | 42 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 12.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | D | Any | Any | EECP | 43 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 13.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | E | Any | Any | EECP | 44 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | F | Any | Any | EECP | 45 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | G | Any | Any | EECP | 46 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 12.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | H | Any | Any | EECP | 47 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 10.8 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 10.8 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | I | Any | Any | EECP | 48 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | J | Any | Any | EECP | 49 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 12.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | K | Any | Any | EECP | 50 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 10.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 10.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | L | Any | Any | EECP | 51 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 11.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | M | Any | Any | EECP | 52 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | N | Any | Any | EECP | 53 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | O | Any | Any | EECP | 54 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | P | Any | Any | EECP | 55 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Q | Any | Any | EECP | 56 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | R | Any | Any | EECP | 57 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 10.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 10.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | S | Any | Any | EECP | 58 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [7 empty] | Must be >= 10.8 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 10.8 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | A | Any | Any | EECP | 59 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 13.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | B | Any | Any | EECP | 60 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 13.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | C | Any | Any | EECP | 61 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 14.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 14.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | D | Any | Any | EECP | 62 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 13.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | E | Any | Any | EECP | 63 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 13.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | F | Any | Any | EECP | 64 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 13.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | G | Any | Any | EECP | 65 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 14.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 14.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | H | Any | Any | EECP | 66 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 12.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | I | Any | Any | EECP | 67 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 12.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | J | Any | Any | EECP | 68 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 15.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | K | Any | Any | EECP | 69 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 11.6 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.6 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | L | Any | Any | EECP | 70 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 12.3 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.3 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | M | Any | Any | EECP | 71 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [7 empty] | Must be >= 13.8 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.8 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | N | Any | Any | EECP | 72 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 32
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | O | Any | Any | EECP | 73 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 32
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | P | Any | Any | EECP | 74 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 32
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Q | Any | Any | EECP | 75 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 32
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | R | Any | Any | EECP | 76 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 32
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | S | Any | Any | EECP | 77 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 32
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any | QA Checklist | 78 | Field inspections should be performed to verify the condenser/unit model number for quality assurance purposes. | Yes | - | Has a field inspection been performed to verify the condenser and if applicable evaporator make and model? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Indicate if an inspection was completed by the inspections team | There is no pass or fail criteria | - | - | - |  | 2021-11-22 | Kenny Liljestrom |  |  | 106
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | QA Checklist | 1 | The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Yes | - | The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Drop Down List | Air-Conditioning, Heating, and Refrigeration Institute (AHRI);Consortium for Energy Efficiency (CEE) database;Manufacturers specification sheets | [7 empty] | QA Checklist | Document how you plan to validate the equipment properties related to this measure | The options for verification include: • Air-Conditioning, Heating, and Refrigeration Institute (AHRI) • Consortium for Energy Efficiency (CEE) database • Manufacturers specification sheets | - | - | - |  | 2021-08-11 | Kenny Liljestrom |  | Add | 444
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Manufacturer | Condenser Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet | Update property label | 2021-08-11 | Kenny Liljestrom |  | Add | 22
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 3 | - | Yes | Model | Condenser Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet | Update property label | 2021-08-11 | Kenny Liljestrom |  | Add | 15
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 4 | Good to have for tracking | Yes | Serial Number | Condenser Serial Number | Text Box | [8 empty] | Inspections | Photograph the condenser (outdoor) equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number listed in EECP should match the serial number listed in the invoice or installation report | Update EECP sorting order, below Condenser Model | 2021-08-11 | Kenny Liljestrom |  | Add | 23
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 5 | Good for Tracking | Yes | RefNum | AHRI Reference Number | Text Box | [8 empty] | QA Checklist | Use the data from EECP to check the AHRI equipment database; this reference number may also help in identifying other equipment specifications including type, capacity, EER, and IEER | Ensure the AHRI number matches with the make and model of the equipment | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update EECP sort order (this on top) | 2021-08-11 | Kenny Liljestrom |  | Add | 21
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 6 | - | Yes | Evaporator Manufacturer | Evaporator Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet |  | 2021-08-11 | Kenny Liljestrom |  | Add | 23
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 7 | - | Yes | Evaporator Model | Evaporator Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet |  | 2021-08-11 | Kenny Liljestrom |  | Add | 16
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 8 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes | System Type | System Type | Drop Down List | Split System;Unitary;Other; | [7 empty] | - | - | - | - | - | - | Property can be removed | 2021-08-11 | Kenny Liljestrom |  | Add | 11
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 9 | Good to have for tracking | Yes | RetailPrice | Retail Price | Numeric Value | [8 empty] | QA Checklist | Use the customer submitted invoice to verify the price of the unit | The value on the invoice should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-11 | Kenny Liljestrom |  | Add | 12
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed | EECP | 10 | Required for UpDeemed Programs | Yes | ZC | Zip Code | Numeric Value | [8 empty] | QA Checklist | Evaluate the zip code in EECP for accuracy | Ensure zip code is real and locatable | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-11 | Kenny Liljestrom |  | Add | 8
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed | EECP | 11 | Required for UpDeemed Programs | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-11 | Kenny Liljestrom |  | Add | 15
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 12 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes | - | Replacement like-for-like (i.e. air conditioner for an air conditioner or heat pump for heat pump)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 99
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 13 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes | - | Existing Equipment within +/- 5% of the replacement equipment Cooling Capacity (kBtuh)? | Drop Down List | Yes;No; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 87
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 14 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes | - | Contractor provided load calculations showing new unit is sized correctly for the load? | Drop Down List | Yes;No;N/A; | [6 empty] | If 'Is the Existing Equipment Cooling Capacity (kBtuh) within +/- 5% of the replacement equipment cooling capacity (kBtuh)?' is 'No' then must be 'Yes' Else must be N/A | QA Checklist | Review the EECP documentation and look for any load calculations submitted by the implementer | The load calculations from the implementer are used to justify an increase in load from the existing HVAC unit; the load calculations should show justification, which can be assisted by engineering, for new loads or inadequate load sizing of the original system | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 87
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | QA Checklist | 15 | Central systems and domestic hot water systems are not eligible. Package terminal air conditioning units, which are units manufactured for installation through a wall or window and are usually ≤ 2 tons, are not eligible. | Yes | - | System Type | Drop Down List | Air Conditioner or Heat Pump;Packaged Terminal Air Conditioner (PTAC);Packaged Terminal Heat Pump (PTHP);Central System; | [6 empty] | Must be 'Air Conditioner or Heat Pump' | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the System Type is listed | The System Type listed in EECP should match the type listed in the invoice, installation report, or spec sheet | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 11
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 16 | Good to have | Yes | - | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 24
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 17 | Need to have for validation | Yes | - | Efficiency type used for equipment eligibility | Drop Down List | Energy Efficiency Ratio (EER);Seasonal Energy Efficiency Ratio (SEER); | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-12 | Kenny Liljestrom |  | Add | 46
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | A | Any | Any | EECP | 18 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | B | Any | Any | EECP | 19 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.4 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.4 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | C | Any | Any | EECP | 20 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | D | Any | Any | EECP | 21 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | E | Any | Any | EECP | 22 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | F | Any | Any | EECP | 23 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.4 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.4 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | G | Any | Any | EECP | 24 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | H | Any | Any | EECP | 25 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | I | Any | Any | EECP | 26 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | J | Any | Any | EECP | 27 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | K | Any | Any | EECP | 28 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | L | Any | Any | EECP | 29 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | M | Any | Any | EECP | 30 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | N | Any | Any | EECP | 31 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | O | Any | Any | EECP | 32 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | P | Any | Any | EECP | 33 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Q | Any | Any | EECP | 34 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | R | Any | Any | EECP | 35 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | S | Any | Any | EECP | 36 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | T | Any | Any | EECP | 37 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | U | Any | Any | EECP | 38 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | V | Any | Any | EECP | 39 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.4 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.4 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | W | Any | Any | EECP | 40 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | X | Any | Any | EECP | 41 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Y | Any | Any | EECP | 42 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Z | Any | Any | EECP | 43 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.4 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.4 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AA | Any | Any | EECP | 44 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AB | Any | Any | EECP | 45 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AC | Any | Any | EECP | 46 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AD | Any | Any | EECP | 47 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AE | Any | Any | EECP | 48 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AF | Any | Any | EECP | 49 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AG | Any | Any | EECP | 50 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AH | Any | Any | EECP | 51 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AI | Any | Any | EECP | 52 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AJ | Any | Any | EECP | 53 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | QA Checklist | 1 | The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Yes | - | The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Drop Down List | Air-Conditioning, Heating, and Refrigeration Institute (AHRI);Consortium for Energy Efficiency (CEE) database;Manufacturers specification sheets | [7 empty] | QA Checklist | Document how you plan to validate the equipment properties related to this measure | The options for verification include: • Air-Conditioning, Heating, and Refrigeration Institute (AHRI) • Consortium for Energy Efficiency (CEE) database • Manufacturers specification sheets | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 444
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 2 | Data collection requirements for midstream and upstream deliveries, when possible, the program administrator (PA) shall claim the “specific building type savings” in which the equipment will be installed and submit that information at claims level on CEDARS website. In cases where there is no “building type” information available for a given project, program administrator shall claim the weighted savings of “Com” building type.” | Yes | - | Building Type | Text Box | [8 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report or invoice to determine the building type the equipment was installed at | The building type should match what is listed in EECP | Can be configured at the enrollment level | 2021-11-23 | Kenny Liljestrom |  |  | 13
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed | EECP | 3 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed | EECP | 4 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | A | NR | UpDeemed | EECP | 5 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | B | NR | UpDeemed | EECP | 6 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | C | NR | UpDeemed | EECP | 7 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | D | NR | UpDeemed | EECP | 8 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | E | NR | UpDeemed | EECP | 9 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | F | NR | UpDeemed | EECP | 10 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | G | NR | UpDeemed | EECP | 11 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | H | NR | UpDeemed | EECP | 12 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | I | NR | UpDeemed | EECP | 13 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | J | NR | UpDeemed | EECP | 14 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | K | NR | UpDeemed | EECP | 15 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | L | NR | UpDeemed | EECP | 16 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | M | NR | UpDeemed | EECP | 17 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | N | NR | UpDeemed | EECP | 18 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | O | NR | UpDeemed | EECP | 19 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | P | NR | UpDeemed | EECP | 20 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Q | NR | UpDeemed | EECP | 21 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | R | NR | UpDeemed | EECP | 22 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | S | NR | UpDeemed | EECP | 23 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | T | NR | UpDeemed | EECP | 24 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | U | NR | UpDeemed | EECP | 25 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | V | NR | UpDeemed | EECP | 26 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | W | NR | UpDeemed | EECP | 27 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | X | NR | UpDeemed | EECP | 28 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Y | NR | UpDeemed | EECP | 29 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Z | NR | UpDeemed | EECP | 30 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AA | NR | UpDeemed | EECP | 31 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AB | NR | UpDeemed | EECP | 32 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AC | NR | UpDeemed | EECP | 33 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AD | NR | UpDeemed | EECP | 34 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AE | NR | UpDeemed | EECP | 35 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AF | NR | UpDeemed | EECP | 36 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AG | NR | UpDeemed | EECP | 37 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AH | NR | UpDeemed | EECP | 38 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AI | NR | UpDeemed | EECP | 39 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AJ | NR | UpDeemed | EECP | 40 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [6 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 41 | E-5152 Data Collection Requirements | Yes | Manufacturer | Condenser Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet | Update property label | 2021-11-23 | Kenny Liljestrom |  |  | 22
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 42 | E-5152 Data Collection Requirements | Yes | Model | Condenser Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet | Update property label | 2021-11-23 | Kenny Liljestrom |  |  | 15
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed | EECP | 43 | E-5152 Data Collection Requirements | Yes | Serial Number | Condenser Serial Number | Text Box | [8 empty] | Inspections | Photograph the condenser (outdoor) equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number listed in EECP should match the serial number listed in the invoice or installation report | Update EECP sorting order, below Condenser Model | 2021-11-23 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed | EECP | 44 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [8 empty] | QA Checklist | Use the data from EECP to check the AHRI equipment database; this reference number may also help in identifying other equipment specifications including type, capacity, EER, and IEER | Ensure the AHRI number matches with the make and model of the equipment | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update EECP sort order (this on top) | 2021-11-23 | Kenny Liljestrom |  |  | 21
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 45 | E-5152 Data Collection Requirements | Yes | Evaporator Manufacturer | Evaporator Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet |  | 2021-11-23 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 46 | E-5152 Data Collection Requirements | Yes | Evaporator Model | Evaporator Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet |  | 2021-11-23 | Kenny Liljestrom |  |  | 16
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed | EECP | 47 | E-5152 Data Collection Requirements | No | Refrigerant Type | Refrigerant Type | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the refrigerant type | The listed refrigerant in EECP should match the nameplate | QA Checklist | Use the make and model number to locate the refrigerant type | The refrigerant type should be listed on the manufacturer specfication sheet or can be validated with nameplate data | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 16
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed | EECP | 47 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | System Type | System Type | Drop Down List | Split System;Unitary;Other; | [7 empty] | - | - | - | - | - | - | Property can be removed | 2021-11-23 | Kenny Liljestrom |  |  | 11
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed | EECP | 48 | Good to have for tracking | Yes | RetailPrice | Retail Price | Numeric Value | [8 empty] | QA Checklist | Use the customer submitted invoice to verify the price of the unit | The value on the invoice should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 12
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed | EECP | 49 | Required for UpDeemed Programs | Yes | ZC | Zip Code | Numeric Value | [8 empty] | QA Checklist | Evaluate the zip code in EECP for accuracy | Ensure zip code is real and locatable | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 8
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed | EECP | 50 | Required for UpDeemed Programs | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 15
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 51 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | - | Replacement like-for-like (i.e. air conditioner for an air conditioner or heat pump for heat pump)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-05-16 | Kenny Liljestrom | Removal of requirement per collaboration with CPUC on measure package eligibility updates |  | 99
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 52 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | - | Existing Equipment within +/- 5% of the replacement equipment Cooling Capacity (kBtuh)? | Drop Down List | Yes;No; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-05-16 | Kenny Liljestrom | Removal of requirement per collaboration with CPUC on measure package eligibility updates |  | 87
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 53 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | - | Contractor provided load calculations showing new unit is sized correctly for the load? | Drop Down List | Yes;No;N/A; | [6 empty] | If 'Is the Existing Equipment Cooling Capacity (kBtuh) within +/- 5% of the replacement equipment cooling capacity (kBtuh)?' is 'No' then must be 'Yes' Else must be N/A | QA Checklist | Review the EECP documentation and look for any load calculations submitted by the implementer | The load calculations from the implementer are used to justify an increase in load from the existing HVAC unit; the load calculations should show justification, which can be assisted by engineering, for new loads or inadequate load sizing of the original system | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-16 | Kenny Liljestrom | Removal of requirement per collaboration with CPUC on measure package eligibility updates |  | 87
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 54 | Central systems and domestic hot water systems are not eligible. Package terminal air conditioning units, which are units manufactured for installation through a wall or window and are usually ≤ 2 tons, are not eligible. | No | - | System Type | Drop Down List | Air Conditioner or Heat Pump;Packaged Terminal Air Conditioner (PTAC);Packaged Terminal Heat Pump (PTHP);Central System; | [6 empty] | Must be 'Air Conditioner or Heat Pump' | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the System Type is listed | The System Type listed in EECP should match the type listed in the invoice, installation report, or spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-16 | Kenny Liljestrom | Removal of requirement per collaboration with CPUC on measure package eligibility updates |  | 11
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 55 | Data Collection Requirements For upstream and midstream programs, data collection requirements are as follows: R1503 Site ID - A unique identifier for the installed location of the incentivized equipment Equipment ID - A unique identifier for each unit of incentivized equipment on the site Measure Size Category - General size or capacity range specific to each measure type Equipment manufacturer Equipment model number Rated capacity Rated efficiency unit - The engineering unit basis for the efficiency or performance rating Rated efficiency - Efficiency or performance rating value for the rated efficiency unit basis Quantity per sales transaction, project or site Existing equipment type (i.e., AC or HP) for the NR MAT | Yes | Measure Size Category | Measure Size Category | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-13 | Kenny Liljestrom |  |  | 21
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | A | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | B | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | C | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | D | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | E | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | F | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | G | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | H | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | I | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 45 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | J | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 45 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | K | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 45 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | L | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 45 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | M | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 45 - 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | N | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 45 - 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | O | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 45 - 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | P | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 45 - 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Q | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | R | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | S | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | T | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | U | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | V | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | W | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | X | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Y | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Z | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AA | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AB | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AC | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AD | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AE | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AF | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AG | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AH | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AI | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AJ | Any | Any | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [7 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any | EECP | 57 | Need to have for validation | No | Efficiency Type | Efficiency type used for equipment eligibility | Drop Down List | Energy Efficiency Ratio (EER);Seasonal Energy Efficiency Ratio (SEER); | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom | Clarification in the measure package indicates only one efficinecy requirement is relevant |  | 46
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | A | Any | Any | EECP | 58 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | B | Any | Any | EECP | 59 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | C | Any | Any | EECP | 60 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | D | Any | Any | EECP | 61 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | E | Any | Any | EECP | 62 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | F | Any | Any | EECP | 63 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | G | Any | Any | EECP | 64 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | H | Any | Any | EECP | 65 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | I | Any | Any | EECP | 66 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | J | Any | Any | EECP | 67 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | K | Any | Any | EECP | 68 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | L | Any | Any | EECP | 69 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | M | Any | Any | EECP | 70 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | N | Any | Any | EECP | 71 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | O | Any | Any | EECP | 72 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | P | Any | Any | EECP | 73 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Q | Any | Any | EECP | 74 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | R | Any | Any | EECP | 75 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | S | Any | Any | EECP | 76 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | T | Any | Any | EECP | 77 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | U | Any | Any | EECP | 78 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | V | Any | Any | EECP | 79 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | W | Any | Any | EECP | 80 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | X | Any | Any | EECP | 81 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Y | Any | Any | EECP | 82 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Z | Any | Any | EECP | 83 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AA | Any | Any | EECP | 84 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AB | Any | Any | EECP | 85 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AC | Any | Any | EECP | 86 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AD | Any | Any | EECP | 87 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AE | Any | Any | EECP | 88 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AF | Any | Any | EECP | 89 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AG | Any | Any | EECP | 90 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AH | Any | Any | EECP | 91 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AI | Any | Any | EECP | 92 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AJ | Any | Any | EECP | 93 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [7 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
0 | SWHC018 | 2 | VSD for HVAC Fan Controls, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-28 | Kenny Liljestrom |  | Add | 12
0 | SWHC018 | 2 | VSD for HVAC Fan Controls, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-28 | Kenny Liljestrom |  | Add | 5
0 | SWHC018 | 2 | VSD for HVAC Fan Controls, Commercial | Any | Any | Any | EECP | 3 | This measure is applicable for the following nonresidential building types: Education – Secondary School Education – Community College Education – University Health/Medical – Hospital Health/Medical – Nursing Home Lodging – Hotel Office – Large Retail – Multistory Large Grocery – Grocery | Yes | - | Building Type | Drop Down List | Education – Secondary School;Education – Community College;Education – University;Health/Medical – Hospital;Health/Medical – Nursing Home;Lodging – Hotel;Office – Large;Retail – Multistory Large;Grocery – Grocery; | [7 empty] | Inspections | Make note of the building type at the inspection site | The building type must be one of the following and match what is listed in EECP: Education – Secondary School; Education – Community College; Education – University; Health/Medical – Hospital; Health/Medical – Nursing Home; Lodging – Hotel; Office – Large; Retail – Multistory Large; Grocery – Grocery; | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-24 | Kenny Liljestrom |  | Add | 13
0 | SWHC018 | 2 | VSD for HVAC Fan Controls, Commercial | Any | Any | Any | EECP | 4 | This measure requires the installation of a VSD and associated controls on a motor driving a ventilation fan. Eligibility requirements include: • The fan must be ≤ 100 hp. • As an add-on equipment installation, the VSD must be applied to the HVAC supply or return air system. • Any other throttling devices, such as inlet vanes or bypass dampers, and throttling valves, must be removed or permanently disabled. | Yes | Input Rating (HP) | Input rating (HP) | Numeric Value | [7 empty] | Must be ≤ 100 hp | Inspections | Photograph the nameplate of the HVAC Fan to capture the power rating, hp (if accessible); if the fan is inaccessible, inform the processor to verify the power rating via the manufacturer spec sheet | Use the nameplate power rating (hp) to validate what is listed in EECP; the power rating must be <= 100 hp | QA Checklist | Use photographs of the fan motor nameplate or manufacturer spec sheet to validate the power rating (hp) of the fan motor | The power rating of the fan must be <= 100 hp |  | 2021-06-28 | Kenny Liljestrom |  | Add | 17
0 | SWHC018 | 2 | VSD for HVAC Fan Controls, Commercial | Any | Any | Any | EECP | 5 | This measure requires the installation of a VSD and associated controls on a motor driving a ventilation fan. Eligibility requirements include: • The fan must be ≤ 100 hp. • As an add-on equipment installation, the VSD must be applied to the HVAC supply or return air system. • Any other throttling devices, such as inlet vanes or bypass dampers, and throttling valves, must be removed or permanently disabled. | Yes | VFD Installed Existing HVAC Supply_Return | Is the VFD being installed on an existing HVAC supply or return air system | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-28 | Kenny Liljestrom |  | Add | 74
0 | SWHC018 | 2 | VSD for HVAC Fan Controls, Commercial | Any | Any | Any | EECP | 6 | This measure requires the installation of a VSD and associated controls on a motor driving a ventilation fan. Eligibility requirements include: • The fan must be ≤ 100 hp. • As an add-on equipment installation, the VSD must be applied to the HVAC supply or return air system. • Any other throttling devices, such as inlet vanes or bypass dampers, and throttling valves, must be removed or permanently disabled. | Yes | Throttling Devices | Are there any other throttling devices, such as inlet vanes or bypass dampers, and throttling valves still operating? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-28 | Kenny Liljestrom |  | Add | 117
0 | SWHC018 | 2 | VSD for HVAC Fan Controls, Commercial | Any | Any | Any | EECP | 7 | Replacement of multiple-speed or variable speed motors (VSM) are not eligible. | Yes | Installation Include VSM | Does the installation include the replacement of multiple-speed or variable speed motors (VSM)? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-28 | Kenny Liljestrom |  | Add | 95
0 | SWHC018 | 2 | VSD for HVAC Fan Controls, Commercial | Any | Any | Any | EECP | 8 | Variable frequency drives on cooling tower fans are not eligible. | Yes | VFD Installed Cooling Tower Fans | Is the VFD being installed on cooling tower fans? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | Inspections | Observe the equipment where the motor was installed | The Variable Speed Drive must not be installed in a cooling tower | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-28 | Kenny Liljestrom |  | Add | 49
1 | SWHC020 | 1 | Air Cooled Chiller | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet |  | 2021-08-12 | Kenny Liljestrom |  | Add | 12
1 | SWHC020 | 1 | Air Cooled Chiller | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet |  | 2021-08-12 | Kenny Liljestrom |  | Add | 5
1 | SWHC020 | 1 | Air Cooled Chiller | Any | Any | Any | EECP | 3 | The energy and demand impacts of this measure are applicable only to commercial buildings with chiller equipment serving space comfort. Other chiller measures serving non-space comfort and/or processes and/or industrial applications shall be evaluated and incentivized under custom programs. | Yes |  | Does the chiller serve space conditioning equipment? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 52
1 | SWHC020 | 1 | Air Cooled Chiller | Any | Any | Any | EECP | 4 | Per Section 140.4 (j) of the 2019 California Building Energy Efficiency Standards (Title-24), chilled water plants shall not have more than 300 tons provided by air cooled chillers, except where the water quality at the building site fails to meet the manufacturer specifications for the use of water-cooled chillers, chillers that are used to charge a thermal energy storage system with a design temperature of less than 40 °F or systems serving healthcare facilities. | Yes |  | Sizing exemption for chillers > 300 tons | Drop Down List | N/A;Water quality does not meet equipment specs;Charge thermal energy storage with temp < 40F;Healthcare facility; | [7 empty] | Inspections | Use the data listed in EECP and try to validate the claim from the implementer | If EECP indicates, "N/A", then no action is required If EECP indicates, "Water quality does not meet equipment specs", then no action is required If EECP indicates, "Charge thermal energy storage with temp < 40F", then ask the customer to inspect the thermal energy storage system (the customer must have thermal energy storage) If EECP indicates, "Healthcare facility", then indicate whether or not the building is a healthcare facility (i.e. hospital, nursing home, etc.) | QA Checklist | Use the data listed in EECP and try to validate the claim from the implementer | If EECP indicates, "N/A", then no action is required If EECP indicates, "Water quality does not meet equipment specs", then check for proof of poor water quality in an installation report If EECP indicates, "Charge thermal energy storage with temp < 40F", then check for proof of the customer having a thermal energy storage system in an installation report If EECP indicates, "Healthcare facility", then check for proof of building type in EECP or installation report | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 40
1 | SWHC020 | 1 | Air Cooled Chiller | Any | Any | Any | EECP | 5 | Required for determining eligibility | Yes | Capacity (Tons) | Capacity (tons) | Numeric Value | [8 empty] | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 15
1 | SWHC020 | 1 | Air Cooled Chiller | A | Any | Any | EECP | 6 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency Rating | Full Load Energy Efficiency Rating (EER) | Numeric Value | [7 empty] | Must be >= 11.1 | QA Checklist | Use the manufacturer spec sheet to validate the Full Load Energy Efficiency Ratio (EER) is listed and matches EECP | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 40
1 | SWHC020 | 1 | Air Cooled Chiller | A | Any | Any | EECP | 7 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value | Integrated Part Load Value (IPLV) | Numeric Value | [7 empty] | Must be >= 15.4 | QA Checklist | Use the manufacturer spec sheet to validate the Integrated Part Load Value (IPLV) is listed and matches EECP | The Integrated Part Load Value (IPLV) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 33
1 | SWHC020 | 1 | Air Cooled Chiller | B | Any | Any | EECP | 8 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency Rating | Full Load Energy Efficiency Rating (EER) | Numeric Value | [7 empty] | Must be >= 12.1 | QA Checklist | Use the manufacturer spec sheet to validate the Full Load Energy Efficiency Ratio (EER) is listed and matches EECP | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 40
1 | SWHC020 | 1 | Air Cooled Chiller | B | Any | Any | EECP | 9 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value | Integrated Part Load Value (IPLV) | Numeric Value | [7 empty] | Must be >= 16.9 | QA Checklist | Use the manufacturer spec sheet to validate the Integrated Part Load Value (IPLV) is listed and matches EECP | The Integrated Part Load Value (IPLV) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16.9 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 33
1 | SWHC020 | 1 | Air Cooled Chiller | C | Any | Any | EECP | 10 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency Rating | Full Load Energy Efficiency Rating (EER) | Numeric Value | [7 empty] | Must be >= 11.1 | QA Checklist | Use the manufacturer spec sheet to validate the Full Load Energy Efficiency Ratio (EER) is listed and matches EECP | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 40
1 | SWHC020 | 1 | Air Cooled Chiller | C | Any | Any | EECP | 11 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value | Integrated Part Load Value (IPLV) | Numeric Value | [7 empty] | Must be >= 15.1 | QA Checklist | Use the manufacturer spec sheet to validate the Integrated Part Load Value (IPLV) is listed and matches EECP | The Integrated Part Load Value (IPLV) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 33
1 | SWHC020 | 1 | Air Cooled Chiller | D | Any | Any | EECP | 12 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency Rating | Full Load Energy Efficiency Rating (EER) | Numeric Value | [7 empty] | Must be >= 12.1 | QA Checklist | Use the manufacturer spec sheet to validate the Full Load Energy Efficiency Ratio (EER) is listed and matches EECP | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 40
1 | SWHC020 | 1 | Air Cooled Chiller | D | Any | Any | EECP | 13 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value | Integrated Part Load Value (IPLV) | Numeric Value | [7 empty] | Must be >= 16.6 | QA Checklist | Use the manufacturer spec sheet to validate the Integrated Part Load Value (IPLV) is listed and matches EECP | The Integrated Part Load Value (IPLV) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16.6 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 33
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | UpDeemed | EECP | 0 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | UpDeemed | EECP | 5 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | Any | EECP | 10 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet |  | 2021-11-12 | Kenny Liljestrom |  |  | 12
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | Any | EECP | 15 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet |  | 2021-11-12 | Kenny Liljestrom |  |  | 5
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | UpDeemed | EECP | 20 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number in EECP should match what is listed in the invoice or installation report |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | UpDeemed | EECP | 25 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [8 empty] | QA Checklist | Review the AHRI database to check for the make and model of the installed equipment | The equipment in EECP should be locatable on the AHRI database as being a certified product and should match the make and model of the equipment | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | UpDeemed | EECP | 30 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value |  |  |  | Currency |  |  | 2 |  | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | UpDeemed | EECP | 190 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value |  |  |  | General |  |  | 0 |  | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | UpDeemed | EECP | 195 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | Any | EECP | 35 | The energy and demand impacts of this measure are applicable only to commercial buildings with chiller equipment serving space comfort. Other chiller measures serving non-space comfort and/or processes and/or industrial applications shall be evaluated and incentivized under custom programs. | Yes | ChillerPurpose | Does the chiller serve space conditioning/comfort equipment? | Drop Down List | Yes;No; | Equal | Yes |  |  |  |  | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Updated property label | 2021-11-12 | Kenny Liljestrom |  |  | 60
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | Any | EECP | 40 | Per Section 140.4 (j) of the 2019 California Building Energy Efficiency Standards (Title-24), chilled water plants shall not have more than 300 tons provided by air cooled chillers, except where the water quality at the building site fails to meet the manufacturer specifications for the use of water-cooled chillers, chillers that are used to charge a thermal energy storage system with a design temperature of less than 40 °F or systems serving healthcare facilities. | Yes | Size Exemption | Sizing exemption for chillers > 300 tons | Drop Down List | N/A;Water quality does not meet equipment specs;Charge thermal energy storage with temp < 40F;Healthcare facility; | [7 empty] | Inspections | Use the data listed in EECP and try to validate the claim from the implementer | If EECP indicates, "N/A", then no action is required If EECP indicates, "Water quality does not meet equipment specs", then no action is required If EECP indicates, "Charge thermal energy storage with temp < 40F", then ask the customer to inspect the thermal energy storage system (the customer must have thermal energy storage) If EECP indicates, "Healthcare facility", then indicate whether or not the building is a healthcare facility (i.e. hospital, nursing home, etc.) | QA Checklist | Use the data listed in EECP and try to validate the claim from the implementer | If EECP indicates, "N/A", then no action is required If EECP indicates, "Water quality does not meet equipment specs", then check for proof of poor water quality in an installation report If EECP indicates, "Charge thermal energy storage with temp < 40F", then check for proof of the customer having a thermal energy storage system in an installation report If EECP indicates, "Healthcare facility", then check for proof of building type in EECP or installation report | Not configured in original upload | 2021-11-12 | Kenny Liljestrom |  |  | 40
0 | SWHC020 | 2 | Air Cooled Chiller | A | Any | Any | EECP | 45 | Required for determining eligibility | Yes | Capacity (Tons) | Capacity (tons) | Numeric Value |  |  |  | General | 150 |  | 0 | Must be >= 150 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 15
0 | SWHC020 | 2 | Air Cooled Chiller | B | Any | Any | EECP | 45 | Required for determining eligibility | Yes | Capacity (Tons) | Capacity (tons) | Numeric Value |  |  |  | General | 150 |  | 0 | Must be >= 150 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 15
0 | SWHC020 | 2 | Air Cooled Chiller | C | Any | Any | EECP | 45 | Required for determining eligibility | Yes | Capacity (Tons) | Capacity (tons) | Numeric Value |  |  |  | General | 0 | 149 | 0 | Must be < 150 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 15
0 | SWHC020 | 2 | Air Cooled Chiller | D | Any | Any | EECP | 45 | Required for determining eligibility | Yes | Capacity (Tons) | Capacity (tons) | Numeric Value |  |  |  | General | 0 | 149 | 0 | Must be < 150 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 15
0 | SWHC020 | 2 | Air Cooled Chiller | A | Any | Any | EECP | 50 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | FL EER | Full Load Energy Efficiency Rating (EER) | Numeric Value |  |  |  | General | 11.1 |  | 1 | Must be >= 11.1 | QA Checklist | Use the manufacturer spec sheet to validate the Full Load Energy Efficiency Ratio (EER) is listed and matches EECP | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 40
0 | SWHC020 | 2 | Air Cooled Chiller | A | Any | Any | EECP | 55 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | IPLV | Integrated Part Load Value (IPLV) | Numeric Value |  |  |  | General | 15.4 |  | 1 | Must be >= 15.4 | QA Checklist | Use the manufacturer spec sheet to validate the Integrated Part Load Value (IPLV) is listed and matches EECP | The Integrated Part Load Value (IPLV) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 33
0 | SWHC020 | 2 | Air Cooled Chiller | B | Any | Any | EECP | 50 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | FL EER | Full Load Energy Efficiency Rating (EER) | Numeric Value |  |  |  | General | 12.1 |  | 1 | Must be >= 12.1 | QA Checklist | Use the manufacturer spec sheet to validate the Full Load Energy Efficiency Ratio (EER) is listed and matches EECP | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 40
0 | SWHC020 | 2 | Air Cooled Chiller | B | Any | Any | EECP | 55 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | IPLV | Integrated Part Load Value (IPLV) | Numeric Value |  |  |  | General | 16.9 |  | 1 | Must be >= 16.9 | QA Checklist | Use the manufacturer spec sheet to validate the Integrated Part Load Value (IPLV) is listed and matches EECP | The Integrated Part Load Value (IPLV) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16.9 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 33
0 | SWHC020 | 2 | Air Cooled Chiller | C | Any | Any | EECP | 50 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | FL EER | Full Load Energy Efficiency Rating (EER) | Numeric Value |  |  |  | General | 11.1 |  | 1 | Must be >= 11.1 | QA Checklist | Use the manufacturer spec sheet to validate the Full Load Energy Efficiency Ratio (EER) is listed and matches EECP | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 40
0 | SWHC020 | 2 | Air Cooled Chiller | C | Any | Any | EECP | 55 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | IPLV | Integrated Part Load Value (IPLV) | Numeric Value |  |  |  | General | 15.1 |  | 1 | Must be >= 15.1 | QA Checklist | Use the manufacturer spec sheet to validate the Integrated Part Load Value (IPLV) is listed and matches EECP | The Integrated Part Load Value (IPLV) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 33
0 | SWHC020 | 2 | Air Cooled Chiller | D | Any | Any | EECP | 50 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | FL EER | Full Load Energy Efficiency Rating (EER) | Numeric Value |  |  |  | General | 12.1 |  | 1 | Must be >= 12.1 | QA Checklist | Use the manufacturer spec sheet to validate the Full Load Energy Efficiency Ratio (EER) is listed and matches EECP | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 40
0 | SWHC020 | 2 | Air Cooled Chiller | D | Any | Any | EECP | 55 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | IPLV | Integrated Part Load Value (IPLV) | Numeric Value |  |  |  | General | 16.6 |  | 1 | Must be >= 16.6 | QA Checklist | Use the manufacturer spec sheet to validate the Integrated Part Load Value (IPLV) is listed and matches EECP | The Integrated Part Load Value (IPLV) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16.6 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 33
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-12 | Kenny Liljestrom |  | Add | 12
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-12 | Kenny Liljestrom |  | Add | 5
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any | EECP | 3 | This measure requires field documentation of the existing conditions that verify the measure was necessary and that the measure was successfully applied. Contractors and technicians that implement these measures must ensure that the existing unit does not already have these measures. This measure must replace existing equipment with the addition of controls for existing units. | Yes |  | Have existing conditions been recorded and measures are were NOT previously installed? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the submitted installation report to verify existing conditions have been documented (i.e. unit is operational, supply fan is working, economizer is functioning, etc.). | The installation report should indicate the existing conditions (conditions in following checkpoints) of the unit and the proposed measures were not previously installed on the unit. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 86
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any | EECP | 4 | Terms and conditions are noted below. Other terms and conditions are set by individual programs. • The existing system must be packaged single zone DX cooling unit with gas heat, cooling only unit, or heat pump. • The existing system must have a constant volume supply fan. • The existing system must have an operable airside economizer installed, and economizer high limit must be optimized for the climate per Title 24 2016 Table 140.4-B, adapted below in Table 2 for reference. • Maintenance, and repairs to economizer should be completed prior to or in conjunction with this measure. | Yes |  | Existing system is packaged single zone DX cooling w/ gas heat, cooling only, or heat pump? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Using the manufacturer spec sheet, verify the unit type is either a packaged single zone DX cooling w/ gas heat, cooling only, or heat pump | The unit type must either be a packaged single zone DX cooling w/ gas heat, cooling only, or heat pump. Rooftop Unit (RTU) is also acceptable. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 91
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any | EECP | 5 | Terms and conditions are noted below. Other terms and conditions are set by individual programs. • The existing system must be packaged single zone DX cooling unit with gas heat, cooling only unit, or heat pump. • The existing system must have a constant volume supply fan. • The existing system must have an operable airside economizer installed, and economizer high limit must be optimized for the climate per Title 24 2016 Table 140.4-B, adapted below in Table 2 for reference. • Maintenance, and repairs to economizer should be completed prior to or in conjunction with this measure. | Yes |  | Existing system has a constant volume supply fan? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Using the installation report, verify the supply fan is a constant volume type | The existing supply fan must be a constant volume type to be eligible | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 49
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any | EECP | 6 | Terms and conditions are noted below. Other terms and conditions are set by individual programs. • The existing system must be packaged single zone DX cooling unit with gas heat, cooling only unit, or heat pump. • The existing system must have a constant volume supply fan. • The existing system must have an operable airside economizer installed, and economizer high limit must be optimized for the climate per Title 24 2016 Table 140.4-B, adapted below in Table 2 for reference. • Maintenance, and repairs to economizer should be completed prior to or in conjunction with this measure. | Yes |  | Existing system has operable economizer with high limit set per Title 24 2016 Table 140.4-B? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | The installation report should indicate the Climate Zone of the site and the Economizer high limit (F) | Using the table in the workpaper, or using EnergyCodeAce's Reference Ace for Title-24 2016 Table 140.4-B, verify the Economizer setpoint is eligible based on the climate zone of the site. Toa in the workpaper is also referred to as Outside Air Temperature (OAT). Tra is also referred to as Return Air Temperature (RAT). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 92
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any | EECP | 7 | This measure does not apply if the rooftop unit (RTU) has a fully operational and/or non-snapdisc sensor and is adjusted to the appropriate changeover setpoint based on the number of thermostat stages available for cooling. | Yes |  | Existing system can adjust to changeover setpoint based on thermostat stages available for cooling? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 99
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any | EECP | 8 | This measure does not apply if the unoccupied supply fan operation is already set to “Auto” or intermittent. | Yes |  | Unoccupied supply fan operation already set to “Auto” or intermittent? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 70
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any | EECP | 9 | Terms and conditions are noted below. Other terms and conditions are set by individual programs. • The existing system must be packaged single zone DX cooling unit with gas heat, cooling only unit, or heat pump. • The existing system must have a constant volume supply fan. • The existing system must have an operable airside economizer installed, and economizer high limit must be optimized for the climate per Title 24 2016 Table 140.4-B, adapted below in Table 2 for reference. • Maintenance, and repairs to economizer should be completed prior to or in conjunction with this measure. | Yes |  | Any maintenance or repairs to economizer? If so, what was done? | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 63
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any | EECP | 10 | Implementation requires proper setup of the damper limits and fan speeds in order to provide ventilation in accordance with Title 24 2016 (see Code requirements). Total unit airflow must be verified for at least one of the fan speeds. The percentage of outdoor air must be verified for each of the unit operating modes, including heating and cooling for each stage as well as the ventilation only mode. | Yes |  | Total unit airflow has been verified for at least one of the fan speeds? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Using the installation report, verify the total unit airflow has been recorded after the measure installation | As long as there is a value for the total unit airflow at one of the operating speeds, there are no other validation criteria to check | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 72
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any | EECP | 11 | Implementation requires proper setup of the damper limits and fan speeds in order to provide ventilation in accordance with Title 24 2016 (see Code requirements). Total unit airflow must be verified for at least one of the fan speeds. The percentage of outdoor air must be verified for each of the unit operating modes, including heating and cooling for each stage as well as the ventilation only mode. | Yes |  | Percent OA verified for heating and cooling for each stage as well as ventilation only mode? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 92
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any | EECP | 12 | This measure is applicable for all nonresidential buildings served by unitary direct expansion (DX) and split systems that do not serve process or refrigeration loads. The target market for this measure includes commercial buildings served by packaged single zone HVAC units, sometimes referred to as rooftop units (RTUs). | Yes |  | System used for comfort/space cooling, not process or refrigeration loads? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 74
0 | SWHC024 | 1 | Cogged V-Belt For HVAC Fan, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-17 | Kenny Liljestrom |  | Add | 12
0 | SWHC024 | 1 | Cogged V-Belt For HVAC Fan, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-17 | Kenny Liljestrom |  | Add | 5
0 | SWHC024 | 1 | Cogged V-Belt For HVAC Fan, Commercial | Any | Any | Any | EECP | 3 | This measure is applicable for package rooftop HVAC systems in the following nonresidential building types. The measure is eligible for all vintages (old, existing, recent, and new). | Yes |  | Building Type | Drop Down List | Assembly;Health/Medical – Nursing Home;Education – Community College;Office – Large;Education – Primary School;Office – Small;Education – Secondary School;Restaurant - Fast-Food;Education – University;Restaurant - Sit-Down;Education – Relocatable Classroom;Retail - Multistory Large;Health/Medical – Hospital;Retail - Single-Story Large;Lodging – Hotel;Retail – Small;Lodging – Motel;Storage – Conditioned;Manufacturing - Bio/Tech;Grocery;Manufacturing – Light Industrial; | [7 empty] | Inspections | Document the type of building the V-belt was installed in | The building type listed in EECP should match the building type during the inspection | QA Checklist | Use the building type from the EECP enrollment phase to determine if the project is eligible | The building type validation is set in EECP, verify building type is one of the following: Assembly; Health/Medical – Nursing Home; Education – Community College; Office – Large; Education – Primary School; Office – Small; Education – Secondary School; Restaurant - Fast-Food; Education – University; Restaurant - Sit-Down; Education – Relocatable Classroom; Retail - Multistory Large; Health/Medical – Hospital; Retail - Single-Story Large; Lodging – Hotel; Retail – Small; Lodging – Motel; Storage – Conditioned; Manufacturing - Bio/Tech; Grocery; Manufacturing – Light Industrial; | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 13
0 | SWHC024 | 1 | Cogged V-Belt For HVAC Fan, Commercial | Any | Any | Any | EECP | 4 | Good to have for data collection | Yes | Capacity (Tons) | Capacity (Tons) | Numeric Value | [8 empty] | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-17 | Kenny Liljestrom |  | Add | 15
0 | SWHC024 | 1 | Cogged V-Belt For HVAC Fan, Commercial | Any | Any | Any | EECP | 5 | - | Yes | Size | Capacity (Tons) | Numeric Value | [8 empty] | - | - | - | - | - | - | Duplicate property, can be removed | 2021-08-17 | Kenny Liljestrom |  | Add | 15
0 | SWHC024 | 1 | Cogged V-Belt For HVAC Fan, Commercial | Any | Any | Any | EECP | 6 | Only “A” and “B” V-belts, the two types typically used in rooftop units, are applicable for this measure. | Yes | Belt Type | Belt Type Installed | Drop Down List | A Belt¦1;B Belt¦2;Both¦3 | [7 empty] | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the type of V-Belt is listed | The V-Belt type listed in EECP should match what is listed in spec sheet; the V-Belt type should either be A, B, or both (it should not be type C or D) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-17 | Kenny Liljestrom |  | Add | 19
0 | SWHC024 | 1 | Cogged V-Belt For HVAC Fan, Commercial | Any | Any | Any | EECP | 7 | A cogged V-belt can be installed on supply air and return air fans in rooftop units that do not already have a cogged V-belt. | Yes | Cogged V Belt | Is the existing belt a cogged V-belt? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-17 | Kenny Liljestrom |  | Add | 37
1 | SWHC024 | 2 | Cogged V-Belt for HVAC Fan, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-28 | Kenny Liljestrom |  | Add | 12
1 | SWHC024 | 2 | Cogged V-Belt for HVAC Fan, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-28 | Kenny Liljestrom |  | Add | 5
1 | SWHC024 | 2 | Cogged V-Belt for HVAC Fan, Commercial | Any | Any | Any | EECP | 3 | A cogged V-belt can be installed on supply air and return air fans in rooftop units that do not already have a cogged V-belt. | Yes | Belt Type | Belt Type Installed | Drop Down List | A Belt¦1;B Belt¦2;Both¦3 | [7 empty] | QA Checklist | Use the manufacturer spec sheet to validate the type of V-Belt installed (A, B, C, or D) | The belt must be listed as Type A, Type B, or both Type A and B; it must not be listed as Type C or D | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-28 | Kenny Liljestrom |  | Add | 19
1 | SWHC024 | 2 | Cogged V-Belt for HVAC Fan, Commercial | Any | Any | Any | EECP | 4 | A cogged V-belt can be installed on supply air and return air fans in rooftop units that do not already have a cogged V-belt. | Yes | Cogged V Belt | Is the existing belt a cogged V-belt? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet to validate the belt is listed as a cogged V-belt | The belt must be listed as a cogged v-belt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-28 | Kenny Liljestrom |  | Add | 37
1 | SWHC024 | 2 | Cogged V-Belt for HVAC Fan, Commercial | Any | Any | Any | QA Checklist | 5 | This measure is applicable for package rooftop HVAC systems in the following nonresidential building types. The measure is eligible for all vintages (old, existing, recent, and new). Assembly, Education - Community College, Education - Primary School, Education - Secondary School, Education - University, Education - Relocatable Classroom, Health/Medical - Hospital, Lodging - Hotel, Lodging - Motel, Manufacturing - Bio/Tech, Manufacturing - Light Industrial, Health/Medical - Nursing Home, Office Large, Office Small, Restaurant - Fast Food, Restaurant - Sit-Down, Retail - Multistory Large, Retail - Small, Storage - Conditioned, Grocery | Yes |  | Building Type | Drop Down List | Assembly;Education - Community College;Education - Primary School;Education - Secondary School;Education - University;Education - Relocatable Classroom;Health/Medical - Hospital;Lodging - Hotel;Lodging - Motel;Manufacturing - Bio/Tech;Manufacturing - Light Industrial;Health/Medical - Nursing Home;Office Large;Office Small;Restaurant - Fast Food;Restaurant - Sit-Down;Retail - Multistory Large;Retail - Small;Storage - Conditioned;Grocery; | [7 empty] | QA Checklist | Ensure building type in EECP matches one of the eligible building types | The building type must be one of the following and match what is listed in EECP: Assembly; Education - Community College; Education - Primary School; Education - Secondary School; Education - University; Education - Relocatable Classroom; Health/Medical - Hospital; Lodging - Hotel; Lodging - Motel; Manufacturing - Bio/Tech; Manufacturing - Light Industrial; Health/Medical - Nursing Home; Office Large; Office Small; Restaurant - Fast Food; Restaurant - Sit-Down; Retail - Multistory Large; Retail - Small; Storage - Conditioned; Grocery; | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Ensure building type in EECP matches one of the eligible building types | 2021-08-24 | Kenny Liljestrom |  | Add | 13
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-28 | Kenny Liljestrom |  | Add | 12
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-28 | Kenny Liljestrom |  | Add | 5
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any | QA Checklist | 3 | All existing building vintages are eligible for all building types; new construction is only available for nonresidential building types. Eligible building types include: Health/Medical - Nursing Home, Lodging - Hotel, Lodging - Guest Rooms, Lodging - Motel, Manufacturing - Bio/Tech, Manufacturing - Light Industrial, Office - Large, Office - Small, Restaurant - Fast-Food, Restaurant - Small, Warehouse - Refrigerated, Residential Multi-Family (Common), Residential Multi-Family (Dwelling Unit), Residential Single Family. | Yes |  | Building Type | [8 empty] | Must meet measure level building type | QA Checklist | Ensure building type in EECP matches one of the eligible building types | All existing building vintages are eligible for all building types; new construction is only available for nonresidential building types. Eligible building types include: Health/Medical - Nursing Home, Lodging - Hotel, Lodging - Guest Rooms, Lodging - Motel, Manufacturing - Bio/Tech, Manufacturing - Light Industrial, Office - Large, Office - Small, Restaurant - Fast-Food, Restaurant - Small, Warehouse - Refrigerated, Residential Multi-Family (Common), Residential Multi-Family (Dwelling Unit), Residential Single Family. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-24 | Kenny Liljestrom |  | Add | 13
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | A | Any | Any | EECP | 4 | Ductless mini-split AC are not eligible. | Yes | Mini-Split AC | Is the equipment a ductless mini-split air conditioner? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Use the manufacturer spec sheet to validate the HVAC equipment type | The HVAC equipment must not be listed as a ductless split system air conditioner or ductless split system heat pump | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-28 | Kenny Liljestrom |  | Add | 55
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | A | Any | Any | EECP | 5 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes |  | Size (Btu/hr) | Numeric Value | [8 empty] | Inspections | Photograph the nameplate showing the capacity (Btu/hr) of the unit; if the nameplate is inaccessible, this property can be validated by the processing team | The capacity listed in EECP should match what is listed on the nameplate | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the capacity (Btu/hr) is listed | The capacity listed in EECP should match the what is listed in the installation report or manufacturer spec sheet | Needs to be reconfigured to be in-line with measure case descriptions | 2021-08-24 | Kenny Liljestrom |  | Add | 13
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | A | Any | Any | EECP | 6 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | EER | Equipment Efficiency (EER) | Numeric Value | [8 empty] | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The EER listed in EECP should match the what is listed in the installation report or manufacturer spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Remove, Incorrect property label and duplicate with 'Energy Efficiency Rating (EER)' | 2021-06-28 | Kenny Liljestrom |  | Add | 26
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | A | NR | Any | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [7 empty] | If 'Size' is <= 7000 then must be >= 11.29 If 'Size' is 7000 < x <= 15000 then must be >= 10.27 If 'Size' is > 15000 then must be >= 9.25 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-06-28 | Kenny Liljestrom |  | Add | 30
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | A | NC | Any | EECP | 8 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [7 empty] | If 'Size' is <= 7000 then must be >= 14.28 If 'Size' is 7000 < x <= 15000 then must be >= 12.84 If 'Size' is > 15000 then must be >= 11.40 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 14.28 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 12.84 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 11.40 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-06-28 | Kenny Liljestrom |  | Add | 30
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | A | Any | Any | EECP | 9 | The measure case is defined as a package terminal air conditioner (PTAC) or a package terminal heat pump (PTHP) that is through-the-wall, self-contained, with a cooling capacity ≤ 2 tons (≤ 24 kBtu/hr) and an energy efficient rating (EER) that is 20% higher than the base case. | Yes | EER Exceed Code | Does the EER of the installed unit exceed code by at least 20%? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | - | - | - | - | - | - | Seems a bit redundant with the measure case description, can remove | 2021-06-28 | Kenny Liljestrom |  | Add | 63
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | A | Any | Any | EECP | 10 | Ductless mini-split AC are not eligible. | Yes | High Eff PTAC DX Unit Installed | Was a High Efficiency Package Terminal Air Conditioner (Non Res) DX Unit installed? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | - | - | - | - | - | - | Seems a bit redundant with the measure case description, can remove | 2021-06-28 | Kenny Liljestrom |  | Add | 83
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-11 | Kenny Liljestrom |  |  | 12
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-11 | Kenny Liljestrom |  |  | 5
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any | QA Checklist | 3 | All existing building vintages are eligible for all building types; new construction is only available for nonresidential building types. Eligible building types include: Health/Medical - Nursing Home, Lodging - Hotel, Lodging - Guest Rooms, Lodging - Motel, Manufacturing - Bio/Tech, Manufacturing - Light Industrial, Office - Large, Office - Small, Restaurant - Fast-Food, Restaurant - Small, Warehouse - Refrigerated, Residential Multi-Family (Common), Residential Multi-Family (Dwelling Unit), Residential Single Family. | Yes |  | Building Type | [8 empty] | Must meet measure level building type | QA Checklist | Ensure building type in EECP matches one of the eligible building types | All existing building vintages are eligible for all building types; new construction is only available for nonresidential building types. Eligible building types include: Health/Medical - Nursing Home, Lodging - Hotel, Lodging - Guest Rooms, Lodging - Motel, Manufacturing - Bio/Tech, Manufacturing - Light Industrial, Office - Large, Office - Small, Restaurant - Fast-Food, Restaurant - Small, Warehouse - Refrigerated, Residential Multi-Family (Common), Residential Multi-Family (Dwelling Unit), Residential Single Family. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-11 | Kenny Liljestrom |  |  | 13
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any | EECP | 4 | Required for measure case description check, Ductless mini-split AC are not eligible. | Yes | Mini-Split AC | Is the equipment a ductless mini-split air conditioner? | Drop Down List | Yes;No; | [6 empty] | Must be No | QA Checklist | Use the manufacturer spec sheet to validate the HVAC equipment type | The HVAC equipment must not be listed as a ductless split system air conditioner or ductless split system heat pump | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Retire/remove Property, captured in the property below and moved to QA Checklist | 2021-11-11 | Kenny Liljestrom |  |  | 55
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any | QA Checklist | 4 | Required for measure case description check, Ductless mini-split AC are not eligible. | Yes |  | Does the equipment type match the Measure Case Description (Air Conditioner or Heat Pump) and is not a ductless mini-split air conditioner? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer spec sheet to validate the HVAC equipment type | The HVAC equipment must not be listed as a ductless split system air conditioner or ductless split system heat pump | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-11 | Kenny Liljestrom |  |  | 139
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any | EECP | 5 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Capacity (BTU/hr) | Capacity (BTU/hr) | Numeric Value | [8 empty] | Inspections | Photograph the nameplate showing the capacity (Btu/hr) of the unit; if the nameplate is inaccessible, this property can be validated by the processing team | The capacity listed in EECP should match what is listed on the nameplate | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the capacity (Btu/hr) is listed | The capacity listed in EECP should match the what is listed in the installation report or manufacturer spec sheet | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 17
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | A | NR | Any | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [7 empty] | If 'Size' is <= 7000 then must be >= 11.29 If 'Size' is 7000 < x <= 15000 then must be >= 10.27 If 'Size' is > 15000 then must be >= 9.25 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | B | NR | Any | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [7 empty] | If 'Size' is <= 7000 then must be >= 11.29 If 'Size' is 7000 < x <= 15000 then must be >= 10.27 If 'Size' is > 15000 then must be >= 9.25 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | C | NR | Any | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [7 empty] | If 'Size' is <= 7000 then must be >= 11.17 If 'Size' is 7000 < x <= 15000 then must be >= 10.15 If 'Size' is > 15000 then must be >= 9.13 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | D | NR | Any | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [7 empty] | If 'Size' is <= 7000 then must be >= 11.29 If 'Size' is 7000 < x <= 15000 then must be >= 10.27 If 'Size' is > 15000 then must be >= 9.25 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | E | NR | Any | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [7 empty] | If 'Size' is <= 7000 then must be >= 11.17 If 'Size' is 7000 < x <= 15000 then must be >= 10.15 If 'Size' is > 15000 then must be >= 9.13 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | F | NR | Any | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [7 empty] | If 'Size' is <= 7000 then must be >= 11.17 If 'Size' is 7000 < x <= 15000 then must be >= 10.15 If 'Size' is > 15000 then must be >= 9.13 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | G | NR | Any | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [7 empty] | If 'Size' is <= 7000 then must be >= 11.29 If 'Size' is 7000 < x <= 15000 then must be >= 10.27 If 'Size' is > 15000 then must be >= 9.25 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | H | NR | Any | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [7 empty] | If 'Size' is <= 7000 then must be >= 11.17 If 'Size' is 7000 < x <= 15000 then must be >= 10.15 If 'Size' is > 15000 then must be >= 9.13 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | NC | Any | EECP | 8 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [7 empty] | If 'Size' is <= 7000 then must be >= 14.28 If 'Size' is 7000 < x <= 15000 then must be >= 12.84 If 'Size' is > 15000 then must be >= 11.40 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 14.28 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 12.84 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 11.40 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any | EECP | 9 | The measure case is defined as a package terminal air conditioner (PTAC) or a package terminal heat pump (PTHP) that is through-the-wall, self-contained, with a cooling capacity ≤ 2 tons (≤ 24 kBtu/hr) and an energy efficient rating (EER) that is 20% higher than the base case. | Yes | EER Exceed Code | Does the EER of the installed unit exceed code by at least 20%? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | - | - | - | - | - | - | Seems a bit redundant with the measure case description, can remove/retire | 2021-11-11 | Kenny Liljestrom |  |  | 63
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any | EECP | 10 | Ductless mini-split AC are not eligible. | Yes | High Eff PTAC DX Unit Installed | Was a High Efficiency Package Terminal Air Conditioner (Non Res) DX Unit installed? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | - | - | - | - | - | - | Seems a bit redundant with the measure case description, can remove/retire | 2021-11-11 | Kenny Liljestrom |  |  | 83
0 | SWHC029 | 1 | Fan Controller for Air Conditioner, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWHC029 | 1 | Fan Controller for Air Conditioner, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWHC029 | 1 | Fan Controller for Air Conditioner, Residential | Any | Any | Any | EECP | 3 | Both automated (logic-based) fan controllers and manually set time-delay fan controllers are eligible. | Yes | Type | Type of fan controller installed? | Drop Down List | Automated (logic-based) fan controller;Manually set time-delay fan controller | [7 empty] | QA Checklist | Use the manufacturer specification sheet to determine the type of fan controller installed | The fan controller type should be: Automated (logic-based) fan controller or Manually set time-delay fan controller | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 33
0 | SWHC029 | 1 | Fan Controller for Air Conditioner, Residential | Any | Any | Any | EECP | 4 | The installation of a manually set time-delay fan controller requires the invoice and/or installation contract that verifies the equipment was installed by a qualified HVAC contractor. | Yes | Manually Set Time Delay | This equipment must be installed by a qualified HVAC Contractor. Please verify the invoice and/or installation contract that verifies the equipment was installed by a qualified HVAC contractor has been submitted. | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Invoice or documentation should indicate who installed the controller | Cross check if the installer is a qualified contractor by searching their contractor license number or company against the trade pro list | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 212
0 | SWHC029 | 1 | Fan Controller for Air Conditioner, Residential | Any | Any | Any | EECP | 5 | This measure only applies to a fully functional central residential air conditioning unit equipped with cooling/evaporator (DX) coils. | Yes | Working HVAC | Installed to a functional HVAC unit with cooling/evaporator (dx) coils? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Check the HVAC system to see if it is energized and functional | Check the HVAC system to see if it is energized and functional (operating if there is a call for conditioned air) | QA Checklist | Use the installation report to ensure the baseline (existing conditions) are documented | A detailed report from the implementer showing the baseline operating performance (tested data before and after); before data should show values indicating the fan was working |  | 2021-06-21 | Kenny Liljestrom |  | Add | 71
0 | SWHC029 | 1 | Fan Controller for Air Conditioner, Residential | Any | Any | Any | EECP | 6 | All installations shall comply with all current applicable regulations, code, and standards including (but not limited to) the California Building Energy Efficiency Standards (Title 24), the California Appliance Efficiency Regulations (Title 20), and the National Electrical Code (NEC). | Yes | Code | Does the installation comply with all current applicable regulations, code, and standards? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 90
0 | SWHC029 | 1 | Fan Controller for Air Conditioner, Residential | Any | Any | Any | EECP | 7 | A fan controller used for solely optimizing and improving heating efficiency including those for gas furnaces is not eligible. | Yes | Fan Controller | Is the fan controller used for solely optimizing and improving heating efficiency including those for gas furnaces? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Locate the fan controller for the associated gas furnace | Check to see whether the fan controller is installed on a fan in the ducting supplied by a gas fired furnace | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 115
0 | SWHC029 | 1 | Fan Controller for Air Conditioner, Residential | Any | Any | Any | EECP | 8 | The baseline air conditioning system cannot be equipped with a hardware based built-in delay controller. | Yes | Baseline AC | Is the baseline air conditioning system equipped with a hardware based built-in delay controller? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 97
1 | SWHC029 | 2 | Fan Controller for Air Conditioner, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
1 | SWHC029 | 2 | Fan Controller for Air Conditioner, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
1 | SWHC029 | 2 | Fan Controller for Air Conditioner, Residential | Any | Any | Any | EECP | 3 | Both automated (logic-based) fan controllers and manually set time-delay fan controllers are eligible. | Yes | Type | Type of fan controller installed? | Drop Down List | Automated (logic-based) fan controller;Manually set time-delay fan controller | [7 empty] | QA Checklist | Use the manufacturer specification sheet to determine the type of fan controller installed | The fan controller type should be: Automated (logic-based) fan controller or Manually set time-delay fan controller | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 33
1 | SWHC029 | 2 | Fan Controller for Air Conditioner, Residential | Any | Any | Any | EECP | 4 | The installation of a manually set time-delay fan controller requires the invoice and/or installation contract that verifies the equipment was installed by a qualified HVAC contractor. | Yes | Manually Set Time Delay | This equipment must be installed by a qualified HVAC Contractor. Please verify the invoice and/or installation contract that verifies the equipment was installed by a qualified HVAC contractor has been submitted. | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Invoice or documentation should indicate who installed the controller | Cross check if the installer is a qualified contractor by searching their contractor license number or company against the trade pro list | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 212
1 | SWHC029 | 2 | Fan Controller for Air Conditioner, Residential | Any | Any | Any | EECP | 5 | This measure only applies to a fully functional central residential air conditioning unit equipped with cooling/evaporator (DX) coils. | Yes | Working HVAC | Installed to a functional HVAC unit with cooling/evaporator (dx) coils? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Check the HVAC system to see if it is energized and functional | Check the HVAC system to see if it is energized and functional (operating if there is a call for conditioned air) | QA Checklist | Use the installation report to ensure the baseline (existing conditions) are documented | A detailed report from the implementer showing the baseline operating performance (tested data before and after); before data should show values indicating the fan was working |  | 2021-06-21 | Kenny Liljestrom |  | Add | 71
1 | SWHC029 | 2 | Fan Controller for Air Conditioner, Residential | Any | Any | Any | EECP | 6 | All installations shall comply with all current applicable regulations, code, and standards including (but not limited to) the California Building Energy Efficiency Standards (Title 24), the California Appliance Efficiency Regulations (Title 20), and the National Electrical Code (NEC). | Yes | Code | Does the installation comply with all current applicable regulations, code, and standards? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 90
1 | SWHC029 | 2 | Fan Controller for Air Conditioner, Residential | Any | Any | Any | EECP | 7 | A fan controller used for solely optimizing and improving heating efficiency including those for gas furnaces is not eligible. | Yes | Fan Controller | Is the fan controller used for solely optimizing and improving heating efficiency including those for gas furnaces? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Locate the fan controller for the associated gas furnace | Check to see whether the fan controller is installed on a fan in the ducting supplied by a gas fired furnace | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 115
1 | SWHC029 | 2 | Fan Controller for Air Conditioner, Residential | Any | Any | Any | EECP | 8 | The baseline air conditioning system cannot be equipped with a hardware based built-in delay controller. | Yes | Baseline AC | Is the baseline air conditioning system equipped with a hardware based built-in delay controller? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 97
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-24 | Kenny Liljestrom |  |  | 12
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-24 | Kenny Liljestrom |  |  | 5
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | Any | Any | Any | EECP | 3 | Eligibility requirements for this measure include: • The customer must have natural gas distributed to the installation address. • The new furnace must replace an existing gas furnace. | Yes |  | Customer has an active natural gas account? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Verify through internal systems or supplied documentation to verify the customer has an active gas account for one of the CA IOUs | Use EECP or other means to verify the customer has an active gas account supplied by SDG&E; or in the case of Statewide Programs, an account provided by SDG&E, SCG, or PG&E | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-24 | Kenny Liljestrom |  |  | 43
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | Any | Any | Any | EECP | 4 | Eligibility requirements for this measure include: • The customer must have natural gas distributed to the installation address. • The new furnace must replace an existing gas furnace. | Yes |  | Proposed furnace is replacing an existing gas furnace? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use an installation report or photographs from the existing conditions showing the gas furnace manufacturer and model | The existing furnace must be a gas fired furnace; this can be verified if the nameplate indicates the Input Rating of the furnace has the units of Btu/hr (Btuh) or there is a visible gas pipeline entering the furnace | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-24 | Kenny Liljestrom |  |  | 54
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | A | Any | Any | EECP | 5 | This measure must meet the minimum AFUE efficiency ratings in the Measure Case Description. | Yes |  | Annual Fuel Utilization Efficiency, AFUE (%) | Numeric Value | [7 empty] | Must be >= 92% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 92% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use the following link the verify the equipment is listed and the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 92% https://www.ahridirectory.org/ahridirectory/pages/home.aspx |  | 2021-11-24 | Kenny Liljestrom |  |  | 44
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | B | Any | Any | EECP | 6 | This measure must meet the minimum AFUE efficiency ratings in the Measure Case Description. | Yes |  | Annual Fuel Utilization Efficiency, AFUE (%) | Numeric Value | [7 empty] | Must be >= 95% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 95% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use the following link the verify the equipment is listed and the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 95% https://www.ahridirectory.org/ahridirectory/pages/home.aspx |  | 2021-11-24 | Kenny Liljestrom |  |  | 44
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | C | Any | Any | EECP | 7 | This measure must meet the minimum AFUE efficiency ratings in the Measure Case Description. | Yes |  | Annual Fuel Utilization Efficiency, AFUE (%) | Numeric Value | [7 empty] | Must be >= 97% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 97% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use the following link the verify the equipment is listed and the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 97% https://www.ahridirectory.org/ahridirectory/pages/home.aspx |  | 2021-11-24 | Kenny Liljestrom |  |  | 44
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | Any | Any | Any | EECP | 8 | A brushless DC motor, also known as an electronically commutated motor (ECM) may be eligible for the high-efficiency furnace with a variable speed motor (VSM). | Yes |  | Fan motor type | Drop Down List | Electronically Commutated Motor (ECM);Variable Speed Motor (VSM); | [7 empty] | QA Checklist | Use the make and model of the furnace to locate the product submittal or cutsheet; locate the type of fan used | The fan type listed on the product submittal/cutsheet needs to be either an Electronically Commutated Motor (ECM) or a Variable Speed Motor (VSM) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-24 | Kenny Liljestrom |  |  | 14
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | Any | Any | Any | EECP | 9 | A licensed contractor must verify the furnace has a built-in VSM, if applicable. | Yes |  | Contractor license number | Text Box | [8 empty] | QA Checklist | Verify the contractor used to install the furnace has a valid and active license in the state of CA | Use the following link to verify the contractor utilized is licensed by the ststae of CA; the contractor must have an active and valid license https://www.cslb.ca.gov/onlineservices/checklicenseII/checklicense.aspx | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-24 | Kenny Liljestrom |  |  | 25
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | Any | Any | Any | QA Checklist | 10 | A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | Yes |  | A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | Text Box | [8 empty] | QA Checklist | The equipment must be listed on the AHRI directory | A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-24 | Kenny Liljestrom |  |  | 188
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | UpDeemed | EECP | 1 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | UpDeemed | EECP | 2 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | UpDeemed | EECP | 3 | E-5152 Data Collection Requirements | Yes | Measure Size Category | Measure Size Category | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | Any | EECP | 4 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-24 | Kenny Liljestrom |  |  | 12
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | Any | EECP | 5 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-24 | Kenny Liljestrom |  |  | 5
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | UpDeemed | EECP | 6 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | UpDeemed | EECP | 7 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [8 empty] | QA Checklist | The equipment must be listed on the AHRI directory | A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | UpDeemed | EECP | 8 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | UpDeemed | EECP | 9 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | UpDeemed | EECP | 10 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | Any | EECP | 11 | Eligibility requirements for this measure include: • The customer must have natural gas distributed to the installation address. • The new furnace must replace an existing gas furnace. | Yes | ActiveGas | Customer has an active natural gas account? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Verify through internal systems or supplied documentation to verify the customer has an active gas account for one of the CA IOUs | Use EECP or other means to verify the customer has an active gas account supplied by SDG&E; or in the case of Statewide Programs, an account provided by SDG&E, SCG, or PG&E | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-24 | Kenny Liljestrom |  |  | 43
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | Any | EECP | 12 | Eligibility requirements for this measure include: • The customer must have natural gas distributed to the installation address. • The new furnace must replace an existing gas furnace. | No | - | Proposed furnace is replacing an existing gas furnace? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use an installation report or photographs from the existing conditions showing the gas furnace manufacturer and model | The existing furnace must be a gas fired furnace; this can be verified if the nameplate indicates the Input Rating of the furnace has the units of Btu/hr (Btuh) or there is a visible gas pipeline entering the furnace | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property to be retired, no longer a measure package requirement | 2021-11-24 | Kenny Liljestrom |  |  | 54
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | Any | EECP | 13 | A brushless DC motor, also known as an electronically commutated motor (ECM) may be eligible for the high-efficiency furnace with a variable speed motor (VSM). | No | - | Fan motor type | Drop Down List | Electronically Commutated Motor (ECM);Variable Speed Motor (VSM); | [7 empty] | QA Checklist | Use the make and model of the furnace to locate the product submittal or cutsheet; locate the type of fan used | The fan type listed on the product submittal/cutsheet needs to be either an Electronically Commutated Motor (ECM) or a Variable Speed Motor (VSM) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property to be retired, no longer a measure package requirement | 2021-11-24 | Kenny Liljestrom |  |  | 14
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | Any | EECP | 13 | E-5152 Data Collection Requirements | Yes | Capacity (BTU/hr) | Input Capacity (BTU/hr) | Numeric Value | [8 empty] | Inspections | Photograph the nameplate showing theinput rating of the unit in BTU/HR | The Input Rating listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the Input Rating is listed | The Input Rating (BTU/HR) listed in EECP should match the Input Rating listed in the invoice or installation report |  | 2022-05-18 | Kenny Liljestrom |  |  | 23
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | A | Any | Any | EECP | 14 | This measure must meet the minimum AFUE efficiency ratings in the Measure Case Description. | Yes | AFUE | Annual Fuel Utilization Efficiency, AFUE (%) | Numeric Value | [7 empty] | Must be >= 92% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 92% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use the following link the verify the equipment is listed and the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 92% https://www.ahridirectory.org/ahridirectory/pages/home.aspx |  | 2021-11-24 | Kenny Liljestrom |  |  | 44
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | B | Any | Any | EECP | 15 | This measure must meet the minimum AFUE efficiency ratings in the Measure Case Description. | Yes | AFUE | Annual Fuel Utilization Efficiency, AFUE (%) | Numeric Value | [7 empty] | Must be >= 95% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 95% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use the following link the verify the equipment is listed and the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 95% https://www.ahridirectory.org/ahridirectory/pages/home.aspx |  | 2021-11-24 | Kenny Liljestrom |  |  | 44
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | C | Any | Any | EECP | 16 | This measure must meet the minimum AFUE efficiency ratings in the Measure Case Description. | Yes | AFUE | Annual Fuel Utilization Efficiency, AFUE (%) | Numeric Value | [7 empty] | Must be >= 97% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 97% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use the following link the verify the equipment is listed and the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 97% https://www.ahridirectory.org/ahridirectory/pages/home.aspx |  | 2021-11-24 | Kenny Liljestrom |  |  | 44
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | Any | EECP | 17 | A licensed contractor must verify the furnace has a built-in VSM, if applicable. | No | - | Contractor license number | Text Box | [8 empty] | QA Checklist | Verify the contractor used to install the furnace has a valid and active license in the state of CA | Use the following link to verify the contractor utilized is licensed by the state of CA; the contractor must have an active and valid license https://www.cslb.ca.gov/onlineservices/checklicenseII/checklicense.aspx | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property to be retired, no longer a measure package requirement | 2022-05-16 | Kenny Liljestrom | Property removed as part of mid-year update to address eligiblity clarifications |  | 25
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | Any | QA Checklist | 18 | A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | No | - | A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | Text Box | [8 empty] | QA Checklist | The equipment must be listed on the AHRI directory | A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-05-16 | Kenny Liljestrom | Removed, added criteria to RefNum instead of standalone property |  | 188
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 3 | The HVAC system must be functional/operable and drawing power. | Yes | Operational | Is the HVAC system functional/operable and drawing power? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Ask the customer if they are able to start the AC unit and observe the equipment (outdoor condenser and indoor vents) | Check the HVAC system to see if it is energized and functional (operating without issues) | QA Checklist | A detailed report from the implementer showing the baseline operating performance (tested data before and after) | The existing conditions should show before data values indicating the fan was working |  | 2021-06-21 | Kenny Liljestrom |  | Add | 57
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 4 | The HVAC system shall be capable of delivering a supply air flow rate of at least 350 cfm/ton. The minimum 350 cfm/ton airflow requirement ensures that the refrigerant system can be properly diagnosed and charged as part of a maintenance service. If the system is not delivering 350 cfm/ton upon initial inspection, an assessment should be made to determine if the system will be able to deliver 350 cfm/ton by implementing repairs related to airflow. If it is determined that the supply fan and duct system in place do not have the capability to deliver at least 350 cfm/ton with or without airflow repairs, the savings in this measure are invalid. | Yes | Air Flow Rate | Minimum HVAC delivery air flow rate (cfm/ton) | Numeric Value | [7 empty] | Must be >= 350 | QA Checklist | A detailed report from the implementer showing the baseline and measure case operating performance | the airflow rate should be >= 350 cfm/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 5 | The replacement brushless fan motor (BFM) motor capacity and rated voltage shall match that of existing fan motor being replaced. | Yes | New Match Existing | Does the replacement BFM motor capacity and rated voltage match that of the existing fan motor being replaced? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | A detailed report from the implementer showing the baseline and measure case operating performance should show existing conditions | The replacement brushless fan motor (BFM) motor capacity and rated voltage shall match that of existing fan motor being replaced. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 110
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 6 | The replacement BFM motor and motor controls assembly shall be “UL Listed.” | Yes | UL Listed | Is the replacement brushless fan motor (BFM) motor and motor controls assembly “UL Listed.”? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Photograph of the motor nameplate and motor casing to look for the 'UL' sticker | A UL sticker or logo should be present on the motor or casing indicating it is a qualified UL listed motor | QA Checklist | Check the motor manufacturer and model number against the UL database of motors or have the implementer provide a screenshot of the manufacturer and model number on the UL database | The motor must be listed as being UL qualified | This property may require SDG&E to be part of a QPL membership | 2021-06-21 | Kenny Liljestrom |  | Add | 93
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 7 | The replacement BFM motor shall have a warranty of at least two years from date of installation. | Yes | Warranty | Does the replacement BFM motor have a warranty of at least two years from date of installation? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Standard warranty documentation should be submitted or included in the package upload | warranty coverage, if not included from the manufacturer, needs to be supplied by the installer | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 95
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 8 | The measure shall include HVAC system start-up. During the start-up, the installer shall ensure that system maintain programmed level airflows under both cooling and/or heating and that these are adequate. | Yes | HVAC Start Up | During start-up, system maintains programmed level airflows under both cooling and/or heating? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Update the property label | 2021-06-21 | Kenny Liljestrom |  | Add | 94
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 9 | The installation (as applicable) shall comply with all applicable regulations including but not limited to California Building Energy Efficiency Standards (Title-24), California Electrical Code, and NEC, and any applicable local jurisdiction regulations. See Code Requirement | Yes | Regulations | Does the installation comply with all applicable regulations? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 61
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 10 | This measure only supports HVAC (evaporator) fan motors with nominal capacities of ½-hp and/or less typically serving HVAC systems with nominal capacities of 3.5 ton (or less). | Yes | HVAC EVAP Fan | Is the measure an HVAC (evaporator) fan motor with nominal capacity of ½-hp (or less) typically serving HVAC systems with nominal capacities of 3.5 ton (or less)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Photograph the HVAC system nameplate and the evaporator fan (indoor fan near the cooling coils, if accessible) | HVAC system should have a capacity of less than or equal to 3.5 tons; fan motor should be less than 1/2hp | QA Checklist | Inspection report should indicate the size of the HVAC system and the manufacturer and model number can be used to identify the fan motor size | HVAC system should have a capacity of less than or equal to 3.5 tons; fan motor should be less than 1/2hp |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 11 | The measure applies to units with shaded pole (SHP) or permanent split capacitor (PSC) motors currently installed. As stated previously, the replacement motor is to be a brushless direct current motor with selectable speed control designed to replace a PSC motor in a residential direct drive fan application. | Yes | Replacement | Is the measure replacing a shaded pole or permanent split capacitor (PSC) motor with a brushless direct current motor with selectable speed control? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | An installation report can list the existing equipment and specifications | the existing equipment make and model can be searched online to show if it is a shaded pole or permanent split capacitor motor | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 148
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-23 | Kenny Liljestrom |  |  | 12
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-23 | Kenny Liljestrom |  |  | 5
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 3 | The HVAC system must be functional/operable and drawing power. | Yes | Operational | Is the HVAC system functional/operable and drawing power? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Ask the customer if they are able to start the AC unit and observe the equipment (outdoor condenser and indoor vents) | Check the HVAC system to see if it is energized and functional (operating without issues) | QA Checklist | A detailed report from the implementer showing the baseline operating performance (tested data before and after) | The existing conditions should show before data values indicating the fan was working |  | 2021-11-23 | Kenny Liljestrom |  |  | 57
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 4 | The HVAC system shall be capable of delivering a supply air flow rate of at least 350 cfm/ton. The minimum 350 cfm/ton airflow requirement ensures that the refrigerant system can be properly diagnosed and charged as part of a maintenance service. If the system is not delivering 350 cfm/ton upon initial inspection, an assessment should be made to determine if the system will be able to deliver 350 cfm/ton by implementing repairs related to airflow. If it is determined that the supply fan and duct system in place do not have the capability to deliver at least 350 cfm/ton with or without airflow repairs, the savings in this measure are invalid. | Yes | Air Flow Rate | Minimum HVAC delivery air flow rate (cfm/ton) | Numeric Value | [7 empty] | Must be >= 350 | QA Checklist | A detailed report from the implementer showing the baseline and measure case operating performance | the airflow rate should be >= 350 cfm/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 5 | The replacement brushless fan motor (BFM) motor capacity and rated voltage shall match that of existing fan motor being replaced. | Yes | New Match Existing | Does the replacement BFM motor capacity and rated voltage match that of the existing fan motor being replaced? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | A detailed report from the implementer showing the baseline and measure case operating performance should show existing conditions | The replacement brushless fan motor (BFM) motor capacity and rated voltage shall match that of existing fan motor being replaced. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 110
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 6 | The replacement BFM motor and motor controls assembly shall be “UL Listed.” | Yes | UL Listed | Is the replacement brushless fan motor (BFM) motor and motor controls assembly “UL Listed.”? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Photograph of the motor nameplate and motor casing to look for the 'UL' sticker | A UL sticker or logo should be present on the motor or casing indicating it is a qualified UL listed motor | QA Checklist | Check the motor manufacturer and model number against the UL database of motors or have the implementer provide a screenshot of the manufacturer and model number on the UL database | The motor must be listed as being UL qualified | This property may require SDG&E to be part of a QPL membership | 2021-11-23 | Kenny Liljestrom |  |  | 93
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 7 | The replacement BFM motor shall have a warranty of at least two years from date of installation. | Yes | Warranty | Does the replacement BFM motor have a warranty of at least two years from date of installation? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Standard warranty documentation should be submitted or included in the package upload | warranty coverage, if not included from the manufacturer, needs to be supplied by the installer | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 95
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 8 | The measure shall include HVAC system start-up. During the start-up, the installer shall ensure that system maintain programmed level airflows under both cooling and/or heating and that these are adequate. | Yes | HVAC Start Up | During start-up, system maintains programmed level airflows under both cooling and/or heating? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Update the property label | 2021-11-23 | Kenny Liljestrom |  |  | 94
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 9 | The installation (as applicable) shall comply with all applicable regulations including but not limited to California Building Energy Efficiency Standards (Title-24), California Electrical Code, and NEC, and any applicable local jurisdiction regulations. See Code Requirement | Yes | Regulations | Does the installation comply with all applicable regulations? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 61
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 10 | This measure only supports HVAC (evaporator) fan motors with nominal capacities of ½-hp and/or less typically serving HVAC systems with nominal capacities of 3.5 ton (or less). | Yes | HVAC EVAP Fan | Is the measure an HVAC (evaporator) fan motor with nominal capacity of ½-hp (or less) typically serving HVAC systems with nominal capacities of 3.5 ton (or less)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Photograph the HVAC system nameplate and the evaporator fan (indoor fan near the cooling coils, if accessible) | HVAC system should have a capacity of less than or equal to 3.5 tons; fan motor should be less than 1/2hp | QA Checklist | Inspection report should indicate the size of the HVAC system and the manufacturer and model number can be used to identify the fan motor size | HVAC system should have a capacity of less than or equal to 3.5 tons; fan motor should be less than 1/2hp |  | 2021-11-23 | Kenny Liljestrom |  |  | 162
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any | EECP | 11 | The measure applies to units with shaded pole (SHP) or permanent split capacitor (PSC) motors currently installed. As stated previously, the replacement motor is to be a brushless direct current motor with selectable speed control designed to replace a PSC motor in a residential direct drive fan application. | Yes | Replacement | Is the measure replacing a shaded pole or permanent split capacitor (PSC) motor with a brushless direct current motor with selectable speed control? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | An installation report can list the existing equipment and specifications | the existing equipment make and model can be searched online to show if it is a shaded pole or permanent split capacitor motor | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 148
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph of thermostat, if manufacturer number is visible document or photograph | Manufacturer on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph of thermostat, if model number is visible document or photograph | Model number on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any | EECP | 3 | The customer must use the thermostat to control heating and/or cooling equipment supplied by fuels provided by the program administrator: • For single-fuel utilities (or dual-fuel utilities in a portion of their service area where they only supply one fuel), only savings for the applicable delivered fuel may be claimed • Eligible heating equipment: gas forced-air furnace, electric forced-air furnace, heat pump • Eligible cooling equipment: central air conditioning | Yes | Eligible Home | Was the measure installed in an eligible home and attached to the type of HVAC equipment that is being incentivized? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Photograph of the heating system nameplate to capture the Manufacturer and Model Number, or look for any electric or gas lines going to the equipment | Measures for gas furnaces (natural gas heated equipment) include 465983 and 467953 Measures for Heat Pump (electric heated equipment) include 467954 and 467955 | QA Checklist | An installation report can show what type of HVAC equipment the smart thermostat was installed on; Eligible heating equipment: gas forced-air furnace, electric forced-air furnace, heat pump; Eligible cooling equipment: central air conditioning | The measure must be installed in an eligible home and attached to the type of HVAC equipment that is being incentivized |  | 2021-06-21 | Kenny Liljestrom |  | Add | 116
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any | EECP | 4 | Unknown | Yes | Purchase Date | Purchase date of newly installed thermostat | Date | [8 empty] | QA Checklist | Cross check EECP data against submitted invoice | The purchase date on the receipt or invoice should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any | EECP | 5 | Unknown | Yes | Receipt | Was a copy of the purchase receipt submitted? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Check EECP to see if a copy of the invoice or sales receipt was uploaded in the enrollment | Ensure Invoice was submitted and uploaded to EECP | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any | EECP | 6 | The smart thermostat must be in full compliance with the ENERGYSTAR® Program Requirements and Product Specification for Connected Thermostats products Version 1.0 or later. R950 | Yes | Energy Star | Is the installed smart thermostat in full compliance with the ENERGYSTAR Program Requirements and Product Specification for Connected Thermostats Products Version 1.0 or later? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Using the make and model, cross reference the EnergyStar database to ensure the model is listed | The listed make and model in EECP should be included in the EnergyStar database | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 176
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any | QA Checklist | 7 | The program administrator (PA) shall employ QA/QC procedures to ensure that the thermostat is installed in an eligible home and is attached to the type of HVAC equipment that is being incentivized, whether it is for natural gas or electricity savings. | Yes |  | The program administrator (PA) shall employ QA/QC procedures to ensure that the thermostat is installed in an eligible home and is attached to the type of HVAC equipment that is being incentivized, whether it is for natural gas or electricity savings. | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Check the home to ensure it is eligible to receive a rebate and ensure the measure is being applied to the correct piece of heating equipment (Gas Furnace or Heat Pump) | The home should not be flagged in EECP as a double dipper for smart thermostats and meet all program eligibility requirements and the HVAC type should match with the measure description | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-07-20 | Kenny Liljestrom |  | Add | 251
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any | QA Checklist | 8 | The PA shall confirm that the customer has a newly purchased smart thermostat. At minimum, the PA shall obtain a copy of the thermostat sales receipt and the PA shall confirm the purchase date is on or after the program start date. | Yes |  | PA shall confirm that the customer has a newly purchased smart thermostat. At minimum, the PA shall obtain a copy of the thermostat sales receipt and the PA shall confirm the purchase date is on or after the program start date. | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Implementer should provide a copy of the sales receipt in the submittal package | The receipt should list the purchase date and that purchase date should not be prior to the program start-up date | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 227
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any | QA Checklist | 9 | The PA shall determine customer eligibility prior to rebate payment. Upon request, all data associated with determining eligibility shall be provided to Energy Division of the California Public Utilities Commission (CPUC). All PAs shall extend this requirement to all third-party vendors that assist PAs with determining customer eligibility. To the extent that they are used to determine eligibility, data regarding dates of purchase, location of home, customer HVAC equipment type, pre-installation HVAC energy use, etc. shall be made available. | Yes |  | The PA shall determine customer eligibility prior to rebate payment. Upon request, all data associated with determining eligibility shall be provided to Energy Division of the California Public Utilities Commission (CPUC). All PAs shall extend this requirement to all third-party vendors that assist PAs with determining customer eligibility. To the extent that they are used to determine eligibility, data regarding dates of purchase, location of home, customer HVAC equipment type, pre-installation HVAC energy use, etc. shall be made available. | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Verify customer eligibility | The PA shall determine customer eligibility prior to rebate payment. Upon request, all data associated with determining eligibility shall be provided to Energy Division of the California Public Utilities Commission (CPUC). All PAs shall extend this requirement to all third-party vendors that assist PAs with determining customer eligibility. To the extent that they are used to determine eligibility, data regarding dates of purchase, location of home, customer HVAC equipment type, pre-installation HVAC energy use, etc. shall be made available. | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 547
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | UpDeemed | EECP | 0 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 7
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | UpDeemed | EECP | 5 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 12
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | Any | EECP | 10 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer in EECP should match what is listed in the invoice or installation report |  | 2022-06-10 | Kenny Liljestrom |  |  | 12
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | Any | EECP | 15 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number in EECP should match what is listed in the invoice or installation report |  | 2022-06-10 | Kenny Liljestrom |  |  | 5
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | UpDeemed | EECP | 20 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number in EECP should match what is listed in the invoice or installation report |  | 2022-06-10 | Kenny Liljestrom |  |  | 13
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | Any | EECP | 30 | The smart thermostat must be in full compliance with the ENERGYSTAR® Program Requirements and Product Specification for Connected Thermostats products Version 1.0 or later. | Yes | Energy Star ID | Energy Star unique ID | Text Box | [8 empty] | QA Checklist | Review the EnergyStar database to check for the make and model of the installed equipment | The equipment in EECP should be locatable on the EnergyStar database as being a certified product and should match the make and model of the equipment | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Can we have this qualify via Energy Star within CPSS and not entered yes/no by the 3P? | 2022-06-10 |  |  |  | 21
1 | SWHC039 | 4 | Smart Thermostat, Residential | C | Any | Any | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Building type. For upstream or midstream measures where building type is not available, the “Res” building type shall be assumed. Climate zone Existing HVAC system type In any event, data collection shall fully comply with both general and device eligibility requirements. | Yes | Existing Equipment Type | Existing air conditioning equipment type | Drop Down List | AC;HP; | Equal | AC |  |  |  |  | Must be AC | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 40
1 | SWHC039 | 4 | Smart Thermostat, Residential | D | Any | Any | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Building type. For upstream or midstream measures where building type is not available, the “Res” building type shall be assumed. Climate zone Existing HVAC system type In any event, data collection shall fully comply with both general and device eligibility requirements. | Yes | Existing Equipment Type | Existing air conditioning equipment type | Drop Down List | AC;HP; | Equal | HP |  |  |  |  | Must be HP | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 40
1 | SWHC039 | 4 | Smart Thermostat, Residential | E | Any | Any | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Building type. For upstream or midstream measures where building type is not available, the “Res” building type shall be assumed. Climate zone Existing HVAC system type In any event, data collection shall fully comply with both general and device eligibility requirements. | Yes | Existing Equipment Type | Existing air conditioning equipment type | Drop Down List | AC;HP; | Equal | AC |  |  |  |  | Must be AC | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 40
1 | SWHC039 | 4 | Smart Thermostat, Residential | F | Any | Any | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Building type. For upstream or midstream measures where building type is not available, the “Res” building type shall be assumed. Climate zone Existing HVAC system type In any event, data collection shall fully comply with both general and device eligibility requirements. | Yes | Existing Equipment Type | Existing air conditioning equipment type | Drop Down List | AC;HP; | Equal | HP |  |  |  |  | Must be HP | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 40
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | DnDeemDI | EECP | 40 | Per Impact Evaluation of Smart Thermostats. Residential Sector - Program Year 2019 guidance, direct install projects already equipped with smart thermostat technology and/or included the installation of smart thermostat technology shall not be bundled with (or include the installation of) fan control technology to avoid potential double counting of energy savings attributions from both technologies. R1587 (Table 6-1) Program exclusions are expected to be re-evaluated since future impact evaluations will include savings attributions from bundled measures. | Yes | Fan Delay | Does the customer already have a smart thermostat or fan delay controller installed? | Drop Down List | Yes;No; | Equal | No |  |  |  |  | Must be No | QA Checklist | Use the EECP double dip report to check for previously installed smart thermostat and fan delay controller measures; also check in the installation report to determine if the report mentions a fan delay controller | There must not be an existing smart thermostat at the property; there must not be a fan delay controller already installed or bundled with this measure. | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-06-10 | Kenny Liljestrom |  |  | 85
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | UpDeemed | EECP | 190 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value |  |  |  | General |  |  | 0 |  | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 8
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | UpDeemed | EECP | 195 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 15
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | Any | QA Checklist | 205 | The program administrator (PA) shall employ QA/QC procedures to ensure that the thermostat is installed in an eligible home and is attached to the type of HVAC equipment that is being incentivized, whether it is for natural gas or electricity savings. | Yes | - | The program administrator (PA) shall employ QA/QC procedures to ensure that the thermostat is installed in an eligible home and is attached to the type of HVAC equipment that is being incentivized, whether it is for natural gas or electricity savings. | None | [8 empty] | QA Checklist | Check the home to ensure it is eligible to receive a rebate and ensure the measure is being applied to the correct piece of heating equipment (Gas Furnace or Heat Pump) | The home should not be flagged in EECP as a double dipper for smart thermostats and meet all program eligibility requirements and the HVAC type should match with the measure description | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 251
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | Any | QA Checklist | 210 | The PA shall confirm that the customer has a newly purchased smart thermostat. At minimum, the PA shall obtain a copy of the thermostat sales receipt and the PA shall confirm the purchase date is on or after the program start date | Yes | - | The PA shall confirm that the customer has a newly purchased smart thermostat. At minimum, the PA shall obtain a copy of the thermostat sales receipt and the PA shall confirm the purchase date is on or after the program start date. | None | [8 empty] | QA Checklist | Check the enrollment uploads to determine if the sales receipt lists the Smart Thermostat | Confirm the invoice or sales receipt for the thermostats is included with the enrollments and has a line item for Smart Thermostats | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 231
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | Any | QA Checklist | 215 | The PA shall determine customer eligibility prior to rebate payment. Upon request, all data associated with determining eligibility shall be provided to Energy Division of the California Public Utilities Commission (CPUC). All PAs shall extend this requirement to all third-party vendors that assist PAs with determining customer eligibility. To the extent that they are used to determine eligibility, data regarding dates of purchase, location of home, customer HVAC equipment type, pre-installation HVAC energy use, etc. shall be made available. | Yes | - | The PA shall determine customer eligibility prior to rebate payment. Upon request, all data associated with determining eligibility shall be provided to Energy Division of the California Public Utilities Commission (CPUC). All PAs shall extend this requirement to all third-party vendors that assist PAs with determining customer eligibility. To the extent that they are used to determine eligibility, data regarding dates of purchase, location of home, customer HVAC equipment type, pre-installation HVAC energy use, etc. shall be made available. | None | [8 empty] | QA Checklist | Verify customer eligibility | The PA shall determine customer eligibility prior to rebate payment. Upon request, all data associated with determining eligibility shall be provided to Energy Division of the California Public Utilities Commission (CPUC). All PAs shall extend this requirement to all third-party vendors that assist PAs with determining customer eligibility. To the extent that they are used to determine eligibility, data regarding dates of purchase, location of home, customer HVAC equipment type, pre-installation HVAC energy use, etc. shall be made available. | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 547
0 | SWHC041 | 1 | Software-Controlled Switch Reluctance Motor | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-05-28 | Kenny Liljestrom |  | Add | 12
0 | SWHC041 | 1 | Software-Controlled Switch Reluctance Motor | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-05-28 | Kenny Liljestrom |  | Add | 5
0 | SWHC041 | 1 | Software-Controlled Switch Reluctance Motor | Any | Any | Any | EECP | 3 | This measure is not eligible for supply fan motors rated < 1 hp and > 3 hp (nominal). This measure is not eligible for other fans, such as the return fan or outdoor air fan of a packaged HVAC unit. | Yes | Supply Fan Replacement | Was the motor installed to replace a supply fan (not a return fan or outdoor air fan) of a packaged HVAC unit? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-05-28 | Kenny Liljestrom |  | Add | 110
0 | SWHC041 | 1 | Software-Controlled Switch Reluctance Motor | Any | Any | Any | EECP | 4 | This measure must replace the existing 1 to 3 hp supply fan motor in a packaged HVAC system. | Yes | Existing Fan Power | Existing packaged HVAC supply fan motor power (hp) | Numeric Value | [7 empty] | Must be >=1 and <=3 | QA Checklist | An installation report should capture the existing conditions and the power (hp) of the existing supply fan motor | The existing motor must be >= 1 and <= 3 hp | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-05-28 | Kenny Liljestrom |  | Add | 50
0 | SWHC041 | 1 | Software-Controlled Switch Reluctance Motor | Any | Any | Any | EECP | 5 | The new motor and controls must be UL Listed. | Yes | UL Listed Motor | Are the new motor and controls UL Listed? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Photograph of the motor nameplate and motor casing to look for the 'UL' sticker | A UL sticker or logo should be present on the motor or casing indicating it is a qualified UL listed motor | QA Checklist | Check the motor manufacturer and model number against the UL database of motors or have the implementer provide a screenshot of the manufacturer and model number on the UL database | The motor must be listed as being UL qualified |  | 2021-05-28 | Kenny Liljestrom |  | Add | 41
0 | SWHC041 | 1 | Software-Controlled Switch Reluctance Motor | Any | Any | Any | EECP | 6 | The installation of this measure shall meet all applicable regulations, including but not limited to the current California Building Energy Efficiency Standards (Title 24), federal code, and the National Electrical Code® (NEC). | Yes | Codes and Regulations | Does the installation comply with all applicable regulations, including but not limited to the current California Building Energy Efficiency Standards (Title 24), federal code, and the National Electrical Code® (NEC)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | - | - | - | - | - | - |  | 2021-05-28 | Kenny Liljestrom | Removed, implementer must file for permit for measure, not useful to capture unless permit is collected at enrollment | Add | 217
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | UpDeemed | EECP | 1 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | UpDeemed | EECP | 2 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | Any | EECP | 3 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-11 | Kenny Liljestrom |  |  | 12
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | Any | EECP | 4 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-11 | Kenny Liljestrom |  |  | 5
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | UpDeemed | EECP | 5 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | UpDeemed | EECP | 6 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | UpDeemed | EECP | 7 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | UpDeemed | EECP | 8 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | Any | EECP | 9 | This measure is not eligible for supply fan motors rated < 1 hp and > 3 hp (nominal). This measure is not eligible for other fans, such as the return fan or outdoor air fan of a packaged HVAC unit. | Yes | Supply Fan Replacement | Was the motor installed to replace a supply fan (not a return fan or outdoor air fan) of a packaged HVAC unit? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-11-11 | Kenny Liljestrom |  |  | 110
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | Any | EECP | 10 | This measure must replace the existing 1 to 3 hp supply fan motor in a packaged HVAC system. | Yes | Existing Fan Power | Existing packaged HVAC supply fan motor power (hp) | Numeric Value | [7 empty] | Must be >=1 and <=3 | QA Checklist | An installation report should capture the existing conditions and the power (hp) of the existing supply fan motor | The existing motor must be >= 1 and <= 3 hp | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-11-11 | Kenny Liljestrom |  |  | 50
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | Any | EECP | 11 | The new motor and controls must be UL Listed. | Yes | UL Listed Motor | Are the new motor and controls UL Listed? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Photograph of the motor nameplate and motor casing to look for the 'UL' sticker | A UL sticker or logo should be present on the motor or casing indicating it is a qualified UL listed motor | QA Checklist | Check the motor manufacturer and model number against the UL database of motors or have the implementer provide a screenshot of the manufacturer and model number on the UL database | The motor must be listed as being UL qualified |  | 2021-11-11 | Kenny Liljestrom |  |  | 41
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | Any | - | 12 | The installation of this measure shall meet all applicable regulations, including but not limited to the current California Building Energy Efficiency Standards (Title 24), federal code, and the National Electrical Code® (NEC). | No | Codes and Regulations | Does the installation comply with all applicable regulations, including but not limited to the current California Building Energy Efficiency Standards (Title 24), federal code, and the National Electrical Code® (NEC)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | - | - | - | - | - | - |  | 2021-11-11 | Kenny Liljestrom | Program ops request to remove property since contractors are held liable in their contracts to install equipment in accordance with all safety and energy codes |  | 217
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | Any | EECP | 13 | In support of the next revision to this workpaper, additional data should to be gathered to determine if motors with horsepower ratings greater than 3 HP can be included as measure offerings. This includes the following: • The application for software-controlled SRMs highlighted by the 2018 ET study is in air conditioning supply fans. Other applications may be studied for suitability. • Based on the initially available set of datasheets, the 5 HP SRM falls below the NEMA Premium® rating of 89.5% for a 4-pole (1800 RPM) induction motor. As additional SRM products become available, efficiency rating tests (following the appropriate standard test procedures identified by the manufacturer) as well as data on full-load VSD losses for the comparable baseline equipment should be collected. | Yes | SoftwareSRM | Software used to control SRM | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | New property | 2021-11-11 | Kenny Liljestrom |  |  | 28
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | Any | EECP | 14 | In support of the next revision to this workpaper, additional data should to be gathered to determine if motors with horsepower ratings greater than 3 HP can be included as measure offerings. This includes the following: • The application for software-controlled SRMs highlighted by the 2018 ET study is in air conditioning supply fans. Other applications may be studied for suitability. • Based on the initially available set of datasheets, the 5 HP SRM falls below the NEMA Premium® rating of 89.5% for a 4-pole (1800 RPM) induction motor. As additional SRM products become available, efficiency rating tests (following the appropriate standard test procedures identified by the manufacturer) as well as data on full-load VSD losses for the comparable baseline equipment should be collected. | Yes | Total hp | Total hp that can benefit from this measure above the max power rating offered by the measure (>3hp) | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | New property | 2021-11-11 | Kenny Liljestrom |  |  | 100
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 12
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 5
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any | EECP | 3 | This measure is applicable for the nonresidential buildings served by unitary direct expansion (DX) systems listed below. This measure applies to existing building vintages. Assembly Asm Community College ECC University EUn Grocery Gro Hospital Hsp Nursing Home Nrs Hotel Htl Bio/Tech Manufacturing MBT Light Industrial Manufacturing MLI Large Office OfL Small Office OfS Sit-Down Restaurant RSD Fast-Food Restaurant RFF Department Store Rt3 Big Box Retail RtL Small Retail RtS Conditioned Storage SCn Refrigerated Warehouse WRf | Yes |  | Building type | Drop Down List | Assembly (Asm);Community College (ECC);University (EUn);Grocery (Gro);Hospital (Hsp);Nursing Home (Nrs);Hotel (Htl);Bio/Tech Manufacturing (MBT);Light Industrial Manufacturing (MLI);Large Office (OfL);Small Office (OfS);Sit-Down Restaurant (RSD);Fast-Food Restaurant (RFF);Department Store (Rt3);Big Box Retail (RtL);Small Retail (RtS);Conditioned Storage (SCn);Refrigerated Warehouse (WRf); | [7 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use an installation report to determine the building type | The building type should match what is listed in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 13
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any | EECP | 4 | This measure is applicable only in Climate Zones 12, 13, and 15. | Yes |  | Climate Zone | Drop Down List | CZ12;CZ13;CZ15; | [7 empty] | QA Checklist | Use an installation report or invoice to determine the zip code or climate zone where the equipment was purchased or installed | The installation address must reside in CZ12, CZ13, or CZ15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property can be configured at the enrollment level if the zip code is being captured and converted to CA CZ | 2021-12-29 | Kenny Liljestrom |  |  | 12
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any | EECP | 5 | The HVAC packaged units and the evaporative pre-cooler system and controls must meet the following requirements: • Host packaged unit must have a cooling capacity at least 20 tons • For the Add-on Equipment (AOE) measure, the existing packaged unit on which the evaporative pre-cooler system will be installed must be less than 10 years old • A water treatment system must be used in conjunction with the evaporative pre-cooler system to maintain water quality and performance • Real time monitoring of the evaporative pre-cooler system must be implemented to ensure the system is working properly • As a standard procedure, the contractor must perform condenser coil cleaning prior to installation of the pre-cooler system. | Yes |  | Cooling Capacity (tons) | Numeric Value | [7 empty] | Must be >= 20 | Inspections | Photograph the nameplate of the HVAC unit to capture the make, model, and cooling capacity (tons or Btu/hr) | The cooling capacity must be greater than 240,000 Btu/hr or 20 tons | QA Checklist | Using the make and model of the existing HVAC equipment, or the cooling capacity in tons or Btu/hr, to determine the cooling capacity of the HVAC system | The cooling capacity must be greater than 240,000 Btu/hr or 20 tons | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 23
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any | EECP | 6 | The HVAC packaged units and the evaporative pre-cooler system and controls must meet the following requirements: • Host packaged unit must have a cooling capacity at least 20 tons • For the Add-on Equipment (AOE) measure, the existing packaged unit on which the evaporative pre-cooler system will be installed must be less than 10 years old • A water treatment system must be used in conjunction with the evaporative pre-cooler system to maintain water quality and performance • Real time monitoring of the evaporative pre-cooler system must be implemented to ensure the system is working properly • As a standard procedure, the contractor must perform condenser coil cleaning prior to installation of the pre-cooler system. | Yes |  | Existing equipment manufacture date | Date | [7 empty] | Date must be <= 10 Years from Today | QA Checklist | Using the serial number of the HVAC equipment, determine the date the system was manufactured (or a photo of the equipment nameplate showing the manufacture date) | The equipment must be less than 10 years old to qualify | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 35
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any | EECP | 7 | The HVAC packaged units and the evaporative pre-cooler system and controls must meet the following requirements: • Host packaged unit must have a cooling capacity at least 20 tons • For the Add-on Equipment (AOE) measure, the existing packaged unit on which the evaporative pre-cooler system will be installed must be less than 10 years old • A water treatment system must be used in conjunction with the evaporative pre-cooler system to maintain water quality and performance • Real time monitoring of the evaporative pre-cooler system must be implemented to ensure the system is working properly • As a standard procedure, the contractor must perform condenser coil cleaning prior to installation of the pre-cooler system. | Yes |  | Is a water treatment system used with the evaporative pre-cooler system? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use an installation report or invoice to determine if a water treatment system was installed or in use with the evaporative pre-cooler | A water treatment system must be used to treat the water before entering the evaporative pre-cooler | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 72
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any | EECP | 8 | The HVAC packaged units and the evaporative pre-cooler system and controls must meet the following requirements: • Host packaged unit must have a cooling capacity at least 20 tons • For the Add-on Equipment (AOE) measure, the existing packaged unit on which the evaporative pre-cooler system will be installed must be less than 10 years old • A water treatment system must be used in conjunction with the evaporative pre-cooler system to maintain water quality and performance • Real time monitoring of the evaporative pre-cooler system must be implemented to ensure the system is working properly • As a standard procedure, the contractor must perform condenser coil cleaning prior to installation of the pre-cooler system. | Yes |  | Has real time monitoring been implemented to ensure proper operation of the system? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use an installation report or invoice to determine if a real time monitoring system was installed or used with the evaporative pre-cooler | A real time monitoring system must have been installed or in use with the evaporative pre-cooler | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 83
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any | EECP | 9 | The HVAC packaged units and the evaporative pre-cooler system and controls must meet the following requirements: • Host packaged unit must have a cooling capacity at least 20 tons • For the Add-on Equipment (AOE) measure, the existing packaged unit on which the evaporative pre-cooler system will be installed must be less than 10 years old • A water treatment system must be used in conjunction with the evaporative pre-cooler system to maintain water quality and performance • Real time monitoring of the evaporative pre-cooler system must be implemented to ensure the system is working properly • As a standard procedure, the contractor must perform condenser coil cleaning prior to installation of the pre-cooler system. | Yes |  | Has the contractor performed condenser coil cleaning prior to installation of the pre-cooler system? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 100
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | Any | EECP | 1 | 1 Asm Assembly 2 Com Commercial 3 ECC Education - Community College 4 EPr Education - Primary School 5 ERC Education - Relocatable Classroom 6 ESe Education - Secondary School 7 EUn Education - University 8 Gro Grocery 9 Hsp Health/Medical - Hospital 10 Htl Lodging - Hotel 11 MBT Manufacturing Biotech 12 MLI Manufacturing Light Industrial 13 Mtl Lodging - Motel 14 Nrs Health/Medical - Nursing Home 15 OfL Office - Large 16 OfS Office - Small 17 RFF Restaurant - Fast-Food 18 RSD Restaurant - Sit-Down 19 Rt3 Retail - Multistory Large 20 RtL Retail - Single-Story Large 21 RtS Retail - Small 22 SCn Storage - Conditioned 23 WRf Refrigerated Warehouse | Yes | - | Building Type | Drop Down List | Asm;Com;ECC;EPr;ERC;EUn;Gro;Hsp;Htl;MBT;MLI;Mtl;Nrs;OfL;OfS;RFF;RSD;Rt3;RtL;RtS;SCn;WRf; | [7 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report to determine the building type of the customer | The building type should match what is listed in EECP | Property can be configured at the enrollment level | 2022-02-09 | Kenny Liljestrom |  |  | 13
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed | EECP | 2 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed | EECP | 3 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed | EECP | 4 | E-5152 Data Collection Requirements | Yes | Measure Size Category | Measure Size Category | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | Any | EECP | 5 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The manufacturer listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2022-02-09 | Kenny Liljestrom |  |  | 12
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | Any | EECP | 6 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The model number listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the model number | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2022-02-09 | Kenny Liljestrom |  |  | 5
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed | EECP | 7 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 13
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed | EECP | 8 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 21
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed | EECP | 9 | Required for UpDeemed Programs | No | Refrigerant Type | Refrigerant Type | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the refrigerant type | The listed refrigerant in EECP should match the nameplate | QA Checklist | Use the make and model number to locate the refrigerant type | The refrigerant type should be listed on the manufacturer specfication sheet or can be validated with nameplate data | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 16
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed | EECP | 10 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 12
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed | EECP | 11 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 8
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed | EECP | 12 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 15
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | Any | EECP | 13 | E-5152 Data Collection Requirements | Yes | Capacity | Cooling Capacity (kBtu/hr) | Numeric Value | [8 empty] | Inspections | Photograph the equipment nameplate to capture the cooling capacity (tons or Btu/hr) | The Cooling Capacity on the nameplate, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) | QA Checklist | Use the submitted invoice or installation report to validate the cooling capacity (btu/hr or tons) | The Cooling Capacity on the specification sheet, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) |  | 2022-02-09 | Kenny Liljestrom |  |  | 26
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | Any | EECP | 14 | For units from 65,000 Btu/h to less than 135,000 Btu/h rated capacity: • ≥12.0 EER • ≥19.0 IEER | Yes | EER | EER | Numeric Value | [7 empty] | Must be >= 12 | Inspections | Photograph the equipment nameplate to capture the EER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the EER | The EER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 3
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | A | Any | Any | EECP | 15 | For units from 65,000 Btu/h to less than 135,000 Btu/h rated capacity: • ≥12.0 EER • ≥19.0 IEER | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 19 | Inspections | Photograph the equipment nameplate to capture the EER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | B | Any | Any | EECP | 16 | For units from 135,000 Btu/h to less than 240,000 Btu/h rated capacity: • ≥12.0 EER • ≥17.5 IEER | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 17.5 | Inspections | Photograph the equipment nameplate to capture the EER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | Any | EECP | 17 | For both size categories: • Must contain advanced compressor capacity control (either a variable speed compressor, tandem compressors on a single refrigeration circuit, or multiple-step compressors) • Must contain a multi-speed (three steps or greater) indoor fan • Gas-furnace heating section (no requirements on thermal efficiency) • Must be a commercial unitary air conditioner subject to 10 CFR §431.97 | Yes | CompressorControl | Compressor(s) control type | Drop Down List | Variable speed compressor(s);Multiple-step compressor(s);Multiple compressors operating on a single refrigeration circuit (tandem compressors); | [7 empty] | QA Checklist | Use the manufacturer specification sheet to determine the type of cooling compressor type and control strategy | The compressor type and control strategy listed in the specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 26
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | Any | EECP | 18 | For both size categories: • Must contain advanced compressor capacity control (either a variable speed compressor, tandem compressors on a single refrigeration circuit, or multiple-step compressors) • Must contain a multi-speed (three steps or greater) indoor fan • Gas-furnace heating section (no requirements on thermal efficiency) • Must be a commercial unitary air conditioner subject to 10 CFR §431.97 | Yes | MultiSpeed | Unit has multi-speed indoor fan and gas furnace heating? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer specification sheet to determine the type of indoor fan control strategy and if the unit has a gas furnace heating coil or section | The indoor fan must have variable or multi-speed controls and the unit must be heated by a gas furnace | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 56
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | Any | EECP | 19 | Central chilled water hydronic systems and domestic hot water systems are not eligible. | Yes | ChilledWater | System is served by chilled water or serves domestic hot water? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 63
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Heat Pump Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2022-02-09 | Kenny Liljestrom |  |  | 22
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Heat Pump Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2022-02-09 | Kenny Liljestrom |  |  | 15
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed | EECP | 3 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes |  | Building type | Drop Down List | Single Family Home;Mobile Home;Multifamily Dwelling; | [7 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report to determine the customer building type | The building type should match what is listed in EECP | This property is acceptable to configure at the enrollment level | 2022-02-09 | Kenny Liljestrom |  |  | 13
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI | EECP | 4 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes |  | Building type | Drop Down List | Single Family Home;Mobile Home;Multifamily Dwelling; | [7 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report to determine the customer building type | The building type should match what is listed in EECP | This property is acceptable to configure at the enrollment level | 2022-02-09 | Kenny Liljestrom |  |  | 13
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | Any | EECP | 5 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single family, multi-family or mobile homes), and cooling and heating efficiency. | Yes |  | Rated equipment capacity (kBtu/hr) | Numeric Value | [8 empty] | Inspections | Photograph the equipment nameplate to capture the cooling capacity (tons or Btu/hr) | The Cooling Capacity on the nameplate, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) | QA Checklist | Use the submitted invoice or installation report to validate the cooling capacity (btu/hr or tons) | The Cooling Capacity on the specification sheet, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) the calculated value should align with the measure case description |  | 2022-02-09 | Kenny Liljestrom |  |  | 34
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | A | Any | Any | EECP | 6 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [7 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | A | Any | Any | EECP | 7 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | B | Any | Any | EECP | 8 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [7 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | B | Any | Any | EECP | 9 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | C | Any | Any | EECP | 10 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [7 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | C | Any | Any | EECP | 11 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | D | Any | Any | EECP | 12 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [7 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | D | Any | Any | EECP | 13 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | E | Any | Any | EECP | 14 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [7 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | E | Any | Any | EECP | 15 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | F | Any | Any | EECP | 16 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [7 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | F | Any | Any | EECP | 17 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | G | Any | Any | EECP | 18 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [7 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | G | Any | Any | EECP | 19 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | H | Any | Any | EECP | 20 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [7 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | H | Any | Any | EECP | 21 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | I | Any | Any | EECP | 22 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [7 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | I | Any | Any | EECP | 23 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | J | Any | Any | EECP | 24 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [7 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | J | Any | Any | EECP | 25 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | K | Any | Any | EECP | 26 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [7 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | K | Any | Any | EECP | 27 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | L | Any | Any | EECP | 28 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [7 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | L | Any | Any | EECP | 29 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | M | Any | Any | EECP | 30 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [7 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | M | Any | Any | EECP | 31 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | N | Any | Any | EECP | 32 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [7 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | N | Any | Any | EECP | 33 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | O | Any | Any | EECP | 34 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [7 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | O | Any | Any | EECP | 35 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | P | Any | Any | EECP | 36 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [7 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | P | Any | Any | EECP | 37 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed | EECP | 38 | For midstream delivery the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions, and the program administrator shall adjust claimed savings based upon these survey results. | Yes |  | Customer existing baseline fuel type | Drop Down List | Gas;Electric; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 36
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed | EECP | 39 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single family, multi-family or mobile homes), and cooling and heating efficiency. | Yes |  | Retailor or distributor zip code | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | This property can be neglected if the zip code is captured at the enrollment level and it is translated into a CZ | 2022-02-09 | Kenny Liljestrom |  |  | 32
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed | EECP | 40 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes |  | List other electrification measures installed | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 45
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed | QA Checklist | 41 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes |  | Itemized invoices submitted with upgrade costs for additional electrification measures? | Drop Down List | Yes;N/A; | [7 empty] | QA Checklist | Review the submitted files in EECP or the installation report for an itemized invoice showing any additional electrical infrastructure costs | If any electrification measures are listed, ensure an itemized invoice of the costs is submitted as well | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 87
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed | QA Checklist | 42 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes |  | Photograph(s) of existing cooling and heating equipment submitted? | Drop Down List | Yes; | [7 empty] | QA Checklist | Review EECP for photographs of the existing cooling and heating equipment | Check the measure case description to see if photographs of the cooling and heating equipment (if applicable) have been submitted | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 66
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI | EECP | 43 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes |  | List other electrification measures installed | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 45
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI | QA Checklist | 44 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes |  | Itemized invoices submitted with upgrade costs for additional electrification measures? | Drop Down List | Yes;N/A; | [7 empty] | QA Checklist | Review the submitted files in EECP or the installation report for an itemized invoice showing any additional electrical infrastructure costs | If any electrification measures are listed, ensure an itemized invoice of the costs is submitted as well | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 87
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI | QA Checklist | 45 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes |  | Photograph of existing heating equipment submitted? | Drop Down List | Yes; | [7 empty] | QA Checklist | Review EECP for photographs of the existing cooling and heating equipment | Check the measure case description to see if photographs of the cooling and heating equipment (if applicable) have been submitted | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 51
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | Any | EECP | 46 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Existing equipment removed and disposed of rather than refurbished and sold? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 76
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | Any | QA Checklist | 47 | This measure is not eligible when there is no natural gas to electricity fuel substitution for heating and/or when the measures include a non-regulated fuel. New construction measures are only eligible under certain conditions listed in the above section. Ground up constructions are not eligible. | Yes |  | This measure is not eligible when there is no natural gas to electricity fuel substitution for heating and/or when the measures include a non-regulated fuel. New construction measures are only eligible under certain conditions listed in the above section. Ground up constructions are not eligible. | Text Box | [8 empty] | QA Checklist | Use EECP to verify the customer has an active natural gas account | The customer must have a natural gas account to prove they are not using a non-regulated fuel (propane) as the base case equipment | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 298
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed | EECP | 48 | Per CPUC Decision 19-08-009 , building infrastructure costs which include panel upgrades or gas line installations/upgrades required to facilitate these fuel substitution measures shall be collected for 10% of each downstream and direct install measures. | Yes |  | Building infrastructure costs (i.e. panel upgrades or gas installation/upgrades) | Numeric Value | [8 empty] | QA Checklist | Use the submitted invoice or installation report to locate any infrastructure upgrade costs | The infrastructure costs should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 80
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI | EECP | 49 | Per CPUC Decision 19-08-009 , building infrastructure costs which include panel upgrades or gas line installations/upgrades required to facilitate these fuel substitution measures shall be collected for 10% of each downstream and direct install measures. | Yes |  | Building infrastructure costs (i.e. panel upgrades or gas installation/upgrades) | Numeric Value | [8 empty] | QA Checklist | Use the submitted invoice or installation report to locate any infrastructure upgrade costs | The infrastructure costs should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 80
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed | EECP | 1 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | - | Building Type | Drop Down List | SFm;MFm;DMo; | [7 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report to determine the building type of the customer | The building type should match what is listed in EECP | Property can be configured at the enrollment level | 2022-02-09 | Kenny Liljestrom |  |  | 13
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI | EECP | 2 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | - | Building Type | Drop Down List | SFm;MFm;DMo; | [7 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report to determine the building type of the customer | The building type should match what is listed in EECP | Property can be configured at the enrollment level | 2022-02-09 | Kenny Liljestrom |  |  | 13
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | UpDeemed | EECP | 3 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | UpDeemed | EECP | 4 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | UpDeemed | EECP | 5 | E-5152 Data Collection Requirements | Yes | Measure Size Category | Measure Size Category | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | Any | EECP | 6 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The manufacturer listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2022-02-09 | Kenny Liljestrom |  |  | 12
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | Any | EECP | 7 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The model number listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the model number | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2022-02-09 | Kenny Liljestrom |  |  | 5
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | UpDeemed | EECP | 8 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | UpDeemed | EECP | 9 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | UpDeemed | EECP | 10 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | UpDeemed | EECP | 11 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | ZC | Zip Code | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | UpDeemed | EECP | 12 |  | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | Any | EECP | 13 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | Capacity | Cooling Capacity (kBtu/hr) | Numeric Value | [8 empty] | Inspections | Photograph the equipment nameplate to capture the cooling capacity (tons or Btu/hr) | The Cooling Capacity on the nameplate, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) | QA Checklist | Use the submitted invoice or installation report to validate the cooling capacity (btu/hr or tons) | The Cooling Capacity on the specification sheet, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) |  | 2022-02-09 | Kenny Liljestrom |  |  | 26
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | A | Any | Any | EECP | 14 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | A | Any | Any | EECP | 15 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | B | Any | Any | EECP | 16 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | B | Any | Any | EECP | 17 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | C | Any | Any | EECP | 18 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | C | Any | Any | EECP | 19 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | D | Any | Any | EECP | 20 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | D | Any | Any | EECP | 21 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | E | Any | Any | EECP | 22 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | E | Any | Any | EECP | 23 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | F | Any | Any | EECP | 24 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | F | Any | Any | EECP | 25 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | G | Any | Any | EECP | 26 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | G | Any | Any | EECP | 27 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | H | Any | Any | EECP | 28 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | H | Any | Any | EECP | 29 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | AR | Any | EECP | 30 | In addition, preponderance of evidence (POE) must be documented for accelerated replacement measure application types. Notably, programs shall document if the existing equipment (AR) was replaced as a direct result of information, recommendations, and support provided by the program administrator (PA), and programs shall require the collection and submission of documentation to ensure proper conformance with eligibility and implementation requirements. The following are the types of information that will be required for all projects: Customer/site information Specifications of existing equipment Proof that the existing air conditioner and gas furnace are still operating as intended Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life Replacement central heat pump information | Yes |  | Has all the preponderance of evidence required by the measure package been uploaded in EECP? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Check EECP for any POE related documents | Preponderance of evidence (POE) must be documented including: • Customer/site information • Specifications of existing equipment • Proof that the existing air conditioner and gas furnace are still operating as intended • Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life • Replacement central heat pump information | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 92
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed | EECP | 31 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Customer existing baseline fuel type | Drop Down List | Gas;Electric; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 36
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed | EECP | 32 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | List other electrification measures installed | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 45
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed | QA Checklist | 33 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Itemized invoices submitted with upgrade costs for additional electrification measures? | Drop Down List | Yes;N/A; | [7 empty] | QA Checklist | Review the submitted files in EECP or the installation report for an itemized invoice showing any additional electrical infrastructure costs | If any electrification measures are listed, ensure an itemized invoice of the costs is submitted as well | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 87
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed | QA Checklist | 34 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Photograph(s) of existing cooling and heating equipment submitted? | Drop Down List | Yes; | [7 empty] | QA Checklist | Review EECP for photographs of the existing cooling and heating equipment | Check the measure case description to see if photographs of the cooling and heating equipment (if applicable) have been submitted | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 66
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed | EECP | 35 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Building infrastructure costs (i.e. panel upgrades or gas installation/upgrades) | Numeric Value | [8 empty] | QA Checklist | Use the submitted invoice or installation report to locate any infrastructure upgrade costs | The infrastructure costs should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 80
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI | EECP | 36 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Customer existing baseline fuel type | Drop Down List | Gas;Electric; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 36
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI | EECP | 37 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | List other electrification measures installed | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 45
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI | QA Checklist | 38 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Itemized invoices submitted with upgrade costs for additional electrification measures? | Drop Down List | Yes;N/A; | [7 empty] | QA Checklist | Review the submitted files in EECP or the installation report for an itemized invoice showing any additional electrical infrastructure costs | If any electrification measures are listed, ensure an itemized invoice of the costs is submitted as well | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 87
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI | QA Checklist | 39 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Photograph(s) of existing cooling and heating equipment submitted? | Drop Down List | Yes; | [7 empty] | QA Checklist | Review EECP for photographs of the existing cooling and heating equipment | Check the measure case description to see if photographs of the cooling and heating equipment (if applicable) have been submitted | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 66
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI | EECP | 40 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Building infrastructure costs (i.e. panel upgrades or gas installation/upgrades) | Numeric Value | [8 empty] | QA Checklist | Use the submitted invoice or installation report to locate any infrastructure upgrade costs | The infrastructure costs should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 80
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | Any | - | 41 | This measure involves fuel substitution and the implementer must replace an existing central air conditioner and a natural gas furnace. Care must be taken that the existing gas lines are capped off and meet the local code requirements. | No |  | - | None | - | [6 empty] | - | - | - | - | - | - | - | No property required, written in 3PI contracts | 2022-02-09 | Kenny Liljestrom |  |  | 1
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed | EECP | 42 | This measure is not applicable for new construction installations. However new services, as defined in Fuel Substitution Technical Guidance for Energy Efficiency, are eligible. R1087 (Page 3) New service measures are only eligible for downstream and direct install delivery types when: Measures are installed in new areas of an existing building, Measures are installed in a major renovation of an existing building, or Measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. | Yes |  | Installation is part of a new service defined in Fuel Substitution Technical Guidance for EE? | Text Box | Yes;No; | [7 empty] | QA Checklist | If this answer is 'Yes' the 3PI needs to meet certain criteria and provide proof of the following: • Measures are installed in new areas of an existing building, • Measures are installed in a major renovation of an existing building, or • Measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. | A photograph or other type of proof can be submitted to prove one of the three scenarios when a new service measure is eligible | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 93
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI | EECP | 43 | This measure is not applicable for new construction installations. However new services, as defined in Fuel Substitution Technical Guidance for Energy Efficiency, are eligible. R1087 (Page 3) New service measures are only eligible for downstream and direct install delivery types when: Measures are installed in new areas of an existing building, Measures are installed in a major renovation of an existing building, or Measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. | Yes |  | Installation is part of a new service defined in Fuel Substitution Technical Guidance for EE? | Text Box | Yes;No; | [7 empty] | QA Checklist | If this answer is 'Yes' the 3PI needs to meet certain criteria and provide proof of the following: • Measures are installed in new areas of an existing building, • Measures are installed in a major renovation of an existing building, or • Measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. | A photograph or other type of proof can be submitted to prove one of the three scenarios when a new service measure is eligible | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 93
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed | EECP | 1 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed | EECP | 2 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | Any | EECP | 3 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The manufacturer listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2022-02-10 | Kenny Liljestrom |  |  | 12
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | Any | EECP | 4 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The model number listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the model number | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2022-02-10 | Kenny Liljestrom |  |  | 5
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed | EECP | 5 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed | EECP | 6 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed | EECP | 7 | E-5152 Data Collection Requirements | Yes | Measure Size Category | Measure Size Category | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed | EECP | 8 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed | EECP | 9 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed | EECP | 10 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | Any | EECP | 11 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | Capacity | Cooling Capacity (kBtu/hr) | Numeric Value | [8 empty] | Inspections | Photograph the equipment nameplate to capture the cooling capacity (tons or Btu/hr) | The Cooling Capacity on the nameplate, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) | QA Checklist | Use the submitted invoice or installation report to validate the cooling capacity (btu/hr or tons) | The Cooling Capacity on the specification sheet, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) |  | 2022-02-10 | Kenny Liljestrom |  |  | 26
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | A | Any | Any | EECP | 12 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | A | Any | Any | EECP | 13 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.2 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | O | Any | Any | EECP | 14 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | O | Any | Any | EECP | 15 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.2 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AC | Any | Any | EECP | 16 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AC | Any | Any | EECP | 17 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.2 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | B | Any | Any | EECP | 18 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | B | Any | Any | EECP | 19 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.2 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | P | Any | Any | EECP | 20 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | P | Any | Any | EECP | 21 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.2 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AD | Any | Any | EECP | 22 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AD | Any | Any | EECP | 23 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.2 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | C | Any | Any | EECP | 24 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | C | Any | Any | EECP | 25 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.5 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Q | Any | Any | EECP | 26 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Q | Any | Any | EECP | 27 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.5 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AE | Any | Any | EECP | 28 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AE | Any | Any | EECP | 29 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.5 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | D | Any | Any | EECP | 30 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | D | Any | Any | EECP | 31 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | R | Any | Any | EECP | 32 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | R | Any | Any | EECP | 33 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AF | Any | Any | EECP | 34 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AF | Any | Any | EECP | 35 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | E | Any | Any | EECP | 36 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | E | Any | Any | EECP | 37 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | S | Any | Any | EECP | 38 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | S | Any | Any | EECP | 39 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AG | Any | Any | EECP | 40 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AG | Any | Any | EECP | 41 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | F | Any | Any | EECP | 42 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | F | Any | Any | EECP | 43 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | T | Any | Any | EECP | 44 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | T | Any | Any | EECP | 45 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AH | Any | Any | EECP | 46 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AH | Any | Any | EECP | 47 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | G | Any | Any | EECP | 48 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | G | Any | Any | EECP | 49 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | U | Any | Any | EECP | 50 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | U | Any | Any | EECP | 51 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AI | Any | Any | EECP | 52 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AI | Any | Any | EECP | 53 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | H | Any | Any | EECP | 54 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | H | Any | Any | EECP | 55 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | V | Any | Any | EECP | 56 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | V | Any | Any | EECP | 57 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AJ | Any | Any | EECP | 58 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [7 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AJ | Any | Any | EECP | 59 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | I | Any | Any | EECP | 60 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 14.4 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | I | Any | Any | EECP | 61 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | W | Any | Any | EECP | 62 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 14.4 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | W | Any | Any | EECP | 63 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AK | Any | Any | EECP | 64 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 14.4 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AK | Any | Any | EECP | 65 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | J | Any | Any | EECP | 66 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 15.4 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | J | Any | Any | EECP | 67 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | X | Any | Any | EECP | 68 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 15.4 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | X | Any | Any | EECP | 69 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AL | Any | Any | EECP | 70 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 15.4 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AL | Any | Any | EECP | 71 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | K | Any | Any | EECP | 72 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 12.3 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | K | Any | Any | EECP | 73 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Y | Any | Any | EECP | 74 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 12.3 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Y | Any | Any | EECP | 75 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AM | Any | Any | EECP | 76 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 12.3 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AM | Any | Any | EECP | 77 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | L | Any | Any | EECP | 78 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 12.8 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | L | Any | Any | EECP | 79 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Z | Any | Any | EECP | 80 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 12.8 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Z | Any | Any | EECP | 81 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AN | Any | Any | EECP | 82 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 12.8 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AN | Any | Any | EECP | 83 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | M | Any | Any | EECP | 84 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 14.1 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | M | Any | Any | EECP | 85 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.4 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AA | Any | Any | EECP | 86 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 14.1 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AA | Any | Any | EECP | 87 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.4 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AO | Any | Any | EECP | 88 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 14.1 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AO | Any | Any | EECP | 89 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.4 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | N | Any | Any | EECP | 90 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 14.8 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | N | Any | Any | EECP | 91 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.4 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AB | Any | Any | EECP | 92 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 14.8 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AB | Any | Any | EECP | 93 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.4 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AP | Any | Any | EECP | 94 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [7 empty] | Must be >= 14.8 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AP | Any | Any | EECP | 95 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [7 empty] | Must be >= 3.4 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed | EECP | 96 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | No | - | Retailor or distributor zip code | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | This property can be neglected if the zip code is captured at the enrollment level and it is translated into a CZ | 2022-02-10 | Kenny Liljestrom | Property removed in leiu of CZ field |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | Any | EECP | 97 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | - | Building Type | Drop Down List | Asm;Com;ECC;EPr;ERC;ESe;EUn;Gro;HGR;Hsp;Htl;MBT;MLI;Mtl;Nrs;OfL;OfS;RFF;RSD;Rt3;RtL;RtS;SCn;SUn;WRf; | [7 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report to determine the building type of the customer | The building type should match what is listed in EECP | Property can be configured at the enrollment level | 2022-02-10 | Kenny Liljestrom |  |  | 13
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | AR | Any | EECP | 98 | Preponderance of evidence (POE) must be documented. Notably, programs shall document if measure was replaced as a direct result of information, recommendations, and support provided by the Program Administrator, and programs shall require the collection and submission of documentation to ensure proper conformance to eligibility and implementation requirements. The following are the types of information that will be required for all projects: − Customer/site information − Specifications of existing equipment − Proof that the existing air conditioner and gas furnace are still operating as intended − Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life − Replacement central heat pump information To document POE, the provided Preponderance of Evidence (POE) survey12 or similar, should be completed. | Yes |  | Has all the preponderance of evidence required by the measure package been uploaded in EECP? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Check EECP for any POE related documents | Preponderance of evidence (POE) must be documented including: − Customer/site information − Specifications of existing equipment − Proof that the existing air conditioner and gas furnace are still operating as intended − Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life − Replacement central heat pump information | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-10 | Kenny Liljestrom |  |  | 92
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | NC | Any | EECP | 99 | Implementer should confirm and provide required documentation to verify that measure implementation meets one of the following conditions: • measures are installed in new areas of an existing building, • measures are installed in a major renovation of an existing building, or • measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. Required documentation can include ONE of the following: • Existing utility bills for the building, • City approved permitting, • City approved Mechanical, or Electrical, or Architecture site drawings, or • Title-24 compliance report | Yes |  | Required NC document(s) submitted as outlined in the measure package? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Check EECP for any New Construction related documents | Implementer should confirm and provide required documentation to verify that measure implementation meets one of the following conditions: • measures are installed in new areas of an existing building, • measures are installed in a major renovation of an existing building, or • measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. Required documentation can include ONE of the following: • Existing utility bills for the building, • City approved permitting, • City approved Mechanical, or Electrical, or Architecture site drawings, or • Title-24 compliance report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-10 | Kenny Liljestrom |  |  | 69
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | DnDeemed | EECP | 100 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Customer existing baseline fuel type | Drop Down List | Gas;Electric; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-10 | Kenny Liljestrom |  |  | 36
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | DnDeemed | EECP | 101 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | List other electrification measures installed | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-10 | Kenny Liljestrom |  |  | 45
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | DnDeemed | QA Checklist | 102 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Itemized invoices submitted with upgrade costs for additional electrification measures? | Drop Down List | Yes;N/A; | [7 empty] | QA Checklist | Review the submitted files in EECP or the installation report for an itemized invoice showing any additional electrical infrastructure costs | If any electrification measures are listed, ensure an itemized invoice of the costs is submitted as well | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-10 | Kenny Liljestrom |  |  | 87
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | DnDeemed | QA Checklist | 103 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Photograph(s) of existing cooling and heating equipment submitted? | Drop Down List | Yes; | [7 empty] | QA Checklist | Review EECP for photographs of the existing cooling and heating equipment | Check the measure case description to see if photographs of the cooling and heating equipment (if applicable) have been submitted | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-10 | Kenny Liljestrom |  |  | 66
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | DnDeemDI | EECP | 104 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Customer existing baseline fuel type | Drop Down List | Gas;Electric; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-10 | Kenny Liljestrom |  |  | 36
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | DnDeemDI | EECP | 105 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | List other electrification measures installed | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-10 | Kenny Liljestrom |  |  | 45
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | DnDeemDI | QA Checklist | 106 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Itemized invoices submitted with upgrade costs for additional electrification measures? | Drop Down List | Yes;N/A; | [7 empty] | QA Checklist | Review the submitted files in EECP or the installation report for an itemized invoice showing any additional electrical infrastructure costs | If any electrification measures are listed, ensure an itemized invoice of the costs is submitted as well | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-10 | Kenny Liljestrom |  |  | 87
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | DnDeemDI | QA Checklist | 107 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Photograph(s) of existing cooling and heating equipment submitted? | Drop Down List | Yes; | [7 empty] | QA Checklist | Review EECP for photographs of the existing cooling and heating equipment | Check the measure case description to see if photographs of the cooling and heating equipment (if applicable) have been submitted | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-10 | Kenny Liljestrom |  |  | 66
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | Any | EECP | 108 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | InfraCosts | Building infrastructure costs (i.e. panel upgrades or gas installation/upgrades) | Numeric Value | [8 empty] | QA Checklist | Use the submitted invoice or installation report to locate any infrastructure upgrade costs | The infrastructure costs should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-10 | Kenny Liljestrom |  |  | 80
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | Any | EECP | 1 | This measure requires the installation of an air-to-water RTU air conditioner unit for a fast food restaurant that is capable of utilizing waste heat to preheat incoming water from the main. See Measure Case Description. | Yes | - | Building is a fast food restaurant (RFF)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report to determine the building type of the customer | The building type should match what is listed in EECP | This property can be configured at the enrollment level | 2022-02-10 | Kenny Liljestrom |  |  | 41
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | UpDeemed | EECP | 2 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | UpDeemed | EECP | 3 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | UpDeemed | EECP | 4 | E-5152 Data Collection Requirements | Yes | Measure Size Category | Measure Size Category | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | Any | EECP | 5 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The manufacturer listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2022-02-10 | Kenny Liljestrom |  |  | 12
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | Any | EECP | 6 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The model number listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the model number | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2022-02-10 | Kenny Liljestrom |  |  | 5
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | UpDeemed | EECP | 7 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | UpDeemed | EECP | 8 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | UpDeemed | EECP | 9 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | UpDeemed | EECP | 10 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | UpDeemed | EECP | 11 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | Any | EECP | 12 | This measure requires the installation of an air-to-water RTU air conditioner unit for a fast food restaurant that is capable of utilizing waste heat to preheat incoming water from the main. See Measure Case Description. | Yes | HeatUse | Heat used to preheat service hot water (not domestic hot water)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-10 | Kenny Liljestrom |  |  | 64
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-17 | Kenny Liljestrom |  | Add | 12
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-17 | Kenny Liljestrom |  | Add | 5
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | Any | EECP | 3 | Only those air conditioning and heat pump systems covered by AHRI 210/240 2008 are eligible. Efficiency values must be certified by Air-conditioning Heating and Refrigeration Institute (AHRI) as verified by the AHRI certification number. | Yes |  | AHRI certification number | Text Box | [8 empty] | QA Checklist | Use the submitted AHRI number from EECP to cross-check the AHRI database | The AHRI database should be able to match the certification number to the make and model above | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-18 | Kenny Liljestrom |  | Add | 25
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | Any | EECP | 4 | - | Yes | Building vintage | Building Vintage | Drop Down List | Existing;New Construction; | [7 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | Can be removed; data in measure description | 2021-08-17 | Kenny Liljestrom |  | Add | 16
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | Any | EECP | 5 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Building type | Drop Down List | Single Family;Multifamily;Mobile home; | [7 empty] | Inspections | Document the type of residence the unit was installed in (Single Family Home, Multifamily, or Mobile Home) | The building type listed in EECP should match the building type during the inspection | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP | Not configured in original upload | 2021-08-18 | Kenny Liljestrom |  | Add | 13
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | UpDeemed | EECP | 6 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes | ZC | Zip Code | Numeric Value | [8 empty] | QA Checklist | Evaluate the zip code in EECP for accuracy | Ensure zip code is real and locatable | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-17 | Kenny Liljestrom |  | Add | 8
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | UpDeemed | EECP | 7 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes | ClimateZone | CA Climate Zone | Formula | [7 empty] | Lookup formula based on Zip Code | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-08-17 | Kenny Liljestrom |  | Add | 15
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | AR | Any | EECP | 8 | Preponderance of evidence (POE) must be documented. Notably, programs shall document if measure was replaced as a direct result of information, recommendations, and support provided by the Program Administrator, and programs shall require the collection and submission of documentation to ensure proper conformance to eligibility and implementation requirements. The following are the types of information that will be required for all projects: Customer/site information Specifications of existing equipment Proof that the existing air conditioner and gas furnace are still operating as intended Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life Replacement central heat pump information To document POE, the provided Preponderance of evidence (POE) survey, or similar, should be completed | Yes |  | Has all POE documentation been submitted as defined in the workpaper? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Check the EECP documentation for any Preponderance of Evidence (POE) | Preponderance of evidence (POE) must be documented. Notably, programs shall document if measure was replaced as a direct result of information, recommendations, and support provided by the Program Administrator, and programs shall require the collection and submission of documentation to ensure proper conformance to eligibility and implementation requirements. The following are the types of information that will be required for all projects: Customer/site information Specifications of existing equipment Proof that the existing air conditioner and gas furnace are still operating as intended Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life Replacement central heat pump information To document POE, the provided Preponderance of evidence (POE) survey, or similar, should be completed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 69
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | Any | EECP | 9 | For split systems the certification will specify an evaporator coil model and may specify additional components. In some cases, a furnace is specified in the certificate. In this case since the furnace is specified as part of the AC system it will not be eligible for a separate incentive. | Yes |  | Does the split system have a furnace in the AHRI certification that has already received a rebate? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | QA Checklist | Use the EECP double dip report to check for previously installed measures; also check in the installation report to determine if the report mentions a furnace rebate | For split systems the certification will specify an evaporator coil model and may specify additional components. In some cases, a furnace is specified in the certificate. In this case since the furnace is specified as part of the AC system it will not be eligible for a separate incentive. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 98
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | Any | EECP | 10 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the capacity (Btu/hr or kBtu/hr) is listed | The capacity (Btu/hr) in EECP must match what is listed in the spec sheet or installation report; if the value is listed in Btu/hr use the following formula to match EECP: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 24
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | A | Any | Any | EECP | 11 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | B | Any | Any | EECP | 12 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | C | Any | Any | EECP | 13 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | D | Any | Any | EECP | 14 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | E | Any | Any | EECP | 15 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | F | Any | Any | EECP | 16 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | G | Any | Any | EECP | 17 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | H | Any | Any | EECP | 18 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | I | Any | Any | EECP | 19 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | J | Any | Any | EECP | 20 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | K | Any | Any | EECP | 21 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | L | Any | Any | EECP | 22 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | M | Any | Any | EECP | 23 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | N | Any | Any | EECP | 24 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | O | Any | Any | EECP | 25 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | O | Any | Any | EECP | 26 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 8.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | P | Any | Any | EECP | 27 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | P | Any | Any | EECP | 28 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Q | Any | Any | EECP | 29 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Q | Any | Any | EECP | 30 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | R | Any | Any | EECP | 31 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | R | Any | Any | EECP | 32 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | S | Any | Any | EECP | 33 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | T | Any | Any | EECP | 34 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | U | Any | Any | EECP | 35 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | V | Any | Any | EECP | 36 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | W | Any | Any | EECP | 37 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | X | Any | Any | EECP | 38 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Y | Any | Any | EECP | 39 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Z | Any | Any | EECP | 40 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AA | Any | Any | EECP | 41 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AB | Any | Any | EECP | 42 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AC | Any | Any | EECP | 43 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AD | Any | Any | EECP | 44 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AE | Any | Any | EECP | 45 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AF | Any | Any | EECP | 46 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AG | Any | Any | EECP | 47 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AG | Any | Any | EECP | 48 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 8.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AH | Any | Any | EECP | 49 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AH | Any | Any | EECP | 50 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AI | Any | Any | EECP | 51 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AI | Any | Any | EECP | 52 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AJ | Any | Any | EECP | 53 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AJ | Any | Any | EECP | 54 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AK | Any | Any | EECP | 55 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AL | Any | Any | EECP | 56 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AM | Any | Any | EECP | 57 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AN | Any | Any | EECP | 58 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AO | Any | Any | EECP | 59 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AP | Any | Any | EECP | 60 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AQ | Any | Any | EECP | 61 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AR | Any | Any | EECP | 62 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AS | Any | Any | EECP | 63 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AT | Any | Any | EECP | 64 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AU | Any | Any | EECP | 65 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AV | Any | Any | EECP | 66 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AW | Any | Any | EECP | 67 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AX | Any | Any | EECP | 68 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AY | Any | Any | EECP | 69 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AY | Any | Any | EECP | 70 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 8.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AZ | Any | Any | EECP | 71 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AZ | Any | Any | EECP | 72 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | BA | Any | Any | EECP | 73 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | BA | Any | Any | EECP | 74 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | BB | Any | Any | EECP | 75 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | BB | Any | Any | EECP | 76 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-23 | Kenny Liljestrom |  |  | 12
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-23 | Kenny Liljestrom |  |  | 5
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | Any | EECP | 3 | Only those air conditioning and heat pump systems covered by AHRI 210/240 2008 are eligible. Efficiency values must be certified by Air-conditioning Heating and Refrigeration Institute (AHRI) as verified by the AHRI certification number. | Yes |  | AHRI certification number | Text Box | [8 empty] | QA Checklist | Use the submitted AHRI number from EECP to cross-check the AHRI database | The AHRI database should be able to match the certification number to the make and model above | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 25
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | Any | EECP | 4 | - | Yes | Building vintage | Building Vintage | Drop Down List | Existing;New Construction; | [7 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | Can be removed; data in measure description | 2021-11-23 | Kenny Liljestrom |  |  | 16
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | Any | EECP | 5 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Building type | Drop Down List | Single Family;Multifamily;Mobile home; | [7 empty] | Inspections | Document the type of residence the unit was installed in (Single Family Home, Multifamily, or Mobile Home) | The building type listed in EECP should match the building type during the inspection | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 13
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | UpDeemed | EECP | 6 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes | ZC | Zip Code | Numeric Value | [8 empty] | QA Checklist | Evaluate the zip code in EECP for accuracy | Ensure zip code is real and locatable | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 8
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | UpDeemed | EECP | 7 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes | ClimateZone | CA Climate Zone | Formula | [7 empty] | Lookup formula based on Zip Code | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 15
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | AR | Any | EECP | 8 | Preponderance of evidence (POE) must be documented. Notably, programs shall document if measure was replaced as a direct result of information, recommendations, and support provided by the Program Administrator, and programs shall require the collection and submission of documentation to ensure proper conformance to eligibility and implementation requirements. The following are the types of information that will be required for all projects: Customer/site information Specifications of existing equipment Proof that the existing air conditioner and gas furnace are still operating as intended Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life Replacement central heat pump information To document POE, the provided Preponderance of evidence (POE) survey, or similar, should be completed | Yes |  | Has all POE documentation been submitted as defined in the workpaper? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Check the EECP documentation for any Preponderance of Evidence (POE) | Preponderance of evidence (POE) must be documented. Notably, programs shall document if measure was replaced as a direct result of information, recommendations, and support provided by the Program Administrator, and programs shall require the collection and submission of documentation to ensure proper conformance to eligibility and implementation requirements. The following are the types of information that will be required for all projects: Customer/site information Specifications of existing equipment Proof that the existing air conditioner and gas furnace are still operating as intended Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life Replacement central heat pump information To document POE, the provided Preponderance of evidence (POE) survey, or similar, should be completed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 69
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | Any | EECP | 9 | For split systems the certification will specify an evaporator coil model and may specify additional components. In some cases, a furnace is specified in the certificate. In this case since the furnace is specified as part of the AC system it will not be eligible for a separate incentive. | Yes |  | Does the split system have a furnace in the AHRI certification that has already received a rebate? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | QA Checklist | Use the EECP double dip report to check for previously installed measures; also check in the installation report to determine if the report mentions a furnace rebate | For split systems the certification will specify an evaporator coil model and may specify additional components. In some cases, a furnace is specified in the certificate. In this case since the furnace is specified as part of the AC system it will not be eligible for a separate incentive. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 98
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | Any | EECP | 10 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the capacity (Btu/hr or kBtu/hr) is listed | The capacity (Btu/hr) in EECP must match what is listed in the spec sheet or installation report; if the value is listed in Btu/hr use the following formula to match EECP: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | A | Any | Any | EECP | 11 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | B | Any | Any | EECP | 12 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | C | Any | Any | EECP | 13 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | D | Any | Any | EECP | 14 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | E | Any | Any | EECP | 15 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | F | Any | Any | EECP | 16 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | G | Any | Any | EECP | 17 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | H | Any | Any | EECP | 18 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | I | Any | Any | EECP | 19 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | J | Any | Any | EECP | 20 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | K | Any | Any | EECP | 21 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | L | Any | Any | EECP | 22 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | M | Any | Any | EECP | 23 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | N | Any | Any | EECP | 24 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | O | Any | Any | EECP | 25 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | O | Any | Any | EECP | 26 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 8.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | P | Any | Any | EECP | 27 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | P | Any | Any | EECP | 28 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Q | Any | Any | EECP | 29 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Q | Any | Any | EECP | 30 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | R | Any | Any | EECP | 31 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | R | Any | Any | EECP | 32 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | S | Any | Any | EECP | 33 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | T | Any | Any | EECP | 34 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | U | Any | Any | EECP | 35 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | V | Any | Any | EECP | 36 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | W | Any | Any | EECP | 37 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | X | Any | Any | EECP | 38 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Y | Any | Any | EECP | 39 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Z | Any | Any | EECP | 40 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AA | Any | Any | EECP | 41 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AB | Any | Any | EECP | 42 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AC | Any | Any | EECP | 43 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AD | Any | Any | EECP | 44 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AE | Any | Any | EECP | 45 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AF | Any | Any | EECP | 46 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AG | Any | Any | EECP | 47 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AG | Any | Any | EECP | 48 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 8.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AH | Any | Any | EECP | 49 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AH | Any | Any | EECP | 50 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AI | Any | Any | EECP | 51 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AI | Any | Any | EECP | 52 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AJ | Any | Any | EECP | 53 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AJ | Any | Any | EECP | 54 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AK | Any | Any | EECP | 55 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AL | Any | Any | EECP | 56 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AM | Any | Any | EECP | 57 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AN | Any | Any | EECP | 58 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AO | Any | Any | EECP | 59 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AP | Any | Any | EECP | 60 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AQ | Any | Any | EECP | 61 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AR | Any | Any | EECP | 62 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AS | Any | Any | EECP | 63 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AT | Any | Any | EECP | 64 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AU | Any | Any | EECP | 65 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AV | Any | Any | EECP | 66 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AW | Any | Any | EECP | 67 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AX | Any | Any | EECP | 68 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AY | Any | Any | EECP | 69 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AY | Any | Any | EECP | 70 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 8.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 8.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AZ | Any | Any | EECP | 71 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AZ | Any | Any | EECP | 72 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | BA | Any | Any | EECP | 73 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | BA | Any | Any | EECP | 74 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | BB | Any | Any | EECP | 75 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [7 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | BB | Any | Any | EECP | 76 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [7 empty] | Must be >= 9.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | Any | EECP | 0 | For midstream and upstream delivery types, when possible, the program administrator (PA) shall claim the “specific building type savings” in which the equipment will be installed and submit that information at claims level on CEDARS website. In cases where there is no “building type” information available for a given project, program administrator shall claim the weighted savings of “Com” building type. | No | - | Building Type | Drop Down List | Asm;Com;ECC;EPr;ERC;ESe;EUn;Gro;HGR;Hsp;Htl;MBT;MLI;Mtl;Nrs;OfL;OfS;RFF;RSD;Rt3;RtL;RtS;SCn;SUn;WRf; | [7 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report to determine the building type of the customer | The building type should match what is listed in EECP | Property can be configured at the enrollment level | 2022-02-10 | Kenny Liljestrom |  |  | 13
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | UpDeemed | EECP | 0 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | UpDeemed | EECP | 5 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | Any | EECP | 10 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The manufacturer listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2022-02-10 | Kenny Liljestrom |  |  | 12
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | Any | EECP | 15 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The model number listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the model number | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2022-02-10 | Kenny Liljestrom |  |  | 5
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | UpDeemed | EECP | 20 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number in EECP should match what is listed in the invoice or installation report |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | UpDeemed | EECP | 25 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [8 empty] | QA Checklist | Review the AHRI database to check for the make and model of the installed equipment | The equipment in EECP should be locatable on the AHRI database as being a certified product and should match the make and model of the equipment | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | UpDeemed | EECP | 30 | E-5152 Data Collection Requirements | Yes | Measure Size Category | Measure Size Category | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | UpDeemed | EECP | 35 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value |  |  |  | Currency |  |  | 2 |  | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | UpDeemed | EECP | 190 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value |  |  |  | General |  |  | 0 |  | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | UpDeemed | EECP | 195 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | Any | EECP | 40 | The energy and demand impacts of this measure are applicable only to commercial building applications with chiller equipment serving space conditioning. Chiller serving non-space comfort and/or processes and/or industrial applications is not eligible. | Yes | ChillerPurpose | Chiller used for space conditioning, not for processes or industrial applications? | Drop Down List | Yes;No; | Equal | Yes |  |  |  |  | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-10 | Kenny Liljestrom |  |  | 82
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | A | Any | Any | EECP | 45 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | Capacity (Tons) | Cooling Capacity (tons) | Numeric Value |  |  |  | General | 0 | 149 | 0 | Must be < 150 | Inspections | Photograph the equipment nameplate to capture the cooling capacity (tons or Btu/hr) | The Cooling Capacity on the nameplate, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to tons use the following formula: Cooling Capacity (Btu/hr) / 3,413 (Btu/ton) = Cooling Capacity (tons) | QA Checklist | Use the submitted invoice or installation report to validate the cooling capacity (btu/hr or tons) | The Cooling Capacity on the specification sheet, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) |  | 2022-02-10 | Kenny Liljestrom |  |  | 23
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | B | Any | Any | EECP | 45 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | Capacity (Tons) | Cooling Capacity (tons) | Numeric Value |  |  |  | General | 0 | 149 | 0 | Must be < 150 | Inspections | Photograph the equipment nameplate to capture the cooling capacity (tons or Btu/hr) | The Cooling Capacity on the nameplate, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to tons use the following formula: Cooling Capacity (Btu/hr) / 3,413 (Btu/ton) = Cooling Capacity (tons) | QA Checklist | Use the submitted invoice or installation report to validate the cooling capacity (btu/hr or tons) | The Cooling Capacity on the specification sheet, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) |  | 2022-02-10 | Kenny Liljestrom |  |  | 23
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | C | Any | Any | EECP | 45 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | Capacity (Tons) | Cooling Capacity (tons) | Numeric Value |  |  |  | General | 150 |  | 0 | Must be >= 150 | Inspections | Photograph the equipment nameplate to capture the cooling capacity (tons or Btu/hr) | The Cooling Capacity on the nameplate, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to tons use the following formula: Cooling Capacity (Btu/hr) / 3,413 (Btu/ton) = Cooling Capacity (tons) | QA Checklist | Use the submitted invoice or installation report to validate the cooling capacity (btu/hr or tons) | The Cooling Capacity on the specification sheet, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) |  | 2022-02-10 | Kenny Liljestrom |  |  | 23
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | D | Any | Any | EECP | 45 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | Capacity (Tons) | Cooling Capacity (tons) | Numeric Value |  |  |  | General | 150 |  | 0 | Must be >= 150 | Inspections | Photograph the equipment nameplate to capture the cooling capacity (tons or Btu/hr) | The Cooling Capacity on the nameplate, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to tons use the following formula: Cooling Capacity (Btu/hr) / 3,413 (Btu/ton) = Cooling Capacity (tons) | QA Checklist | Use the submitted invoice or installation report to validate the cooling capacity (btu/hr or tons) | The Cooling Capacity on the specification sheet, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) |  | 2022-02-10 | Kenny Liljestrom |  |  | 23
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | A | Any | Any | EECP | 50 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | EER | EER | Numeric Value |  |  |  | General | 10.4 |  | 1 | Must be >= 10.4 | Inspections | Photograph the equipment nameplate to capture the EER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the EER | The EER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 3
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | A | Any | Any | EECP | 55 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | IPLV | Integrated Part Load Value (IPLV) | Numeric Value |  |  |  | General | 17.7 |  | 1 | Must be >= 17.7 | Inspections | Photograph the equipment nameplate to capture the Integrated Part Load Value (IPLV) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IPLV on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Integrated Part Load Value (IPLV) | The IPLV listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 33
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | B | Any | Any | EECP | 50 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | EER | EER | Numeric Value |  |  |  | General | 10.4 |  | 1 | Must be >= 10.4 | Inspections | Photograph the equipment nameplate to capture the EER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the EER | The EER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 3
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | B | Any | Any | EECP | 55 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | IPLV | Integrated Part Load Value (IPLV) | Numeric Value |  |  |  | General | 19 |  | 1 | Must be >= 19.0 | Inspections | Photograph the equipment nameplate to capture the Integrated Part Load Value (IPLV) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IPLV on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Integrated Part Load Value (IPLV) | The IPLV listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 33
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | C | Any | Any | EECP | 50 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | EER | EER | Numeric Value |  |  |  | General | 10.4 |  | 1 | Must be >= 10.4 | Inspections | Photograph the equipment nameplate to capture the EER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the EER | The EER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 3
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | C | Any | Any | EECP | 55 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | IPLV | Integrated Part Load Value (IPLV) | Numeric Value |  |  |  | General | 18 |  | 1 | Must be >= 18.0 | Inspections | Photograph the equipment nameplate to capture the Integrated Part Load Value (IPLV) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IPLV on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Integrated Part Load Value (IPLV) | The IPLV listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 33
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | D | Any | Any | EECP | 50 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | EER | EER | Numeric Value |  |  |  | General | 10.4 |  | 1 | Must be >= 10.4 | Inspections | Photograph the equipment nameplate to capture the EER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the EER | The EER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 3
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | D | Any | Any | EECP | 55 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | IPLV | Integrated Part Load Value (IPLV) | Numeric Value |  |  |  | General | 19.3 |  | 1 | Must be >= 19.3 | Inspections | Photograph the equipment nameplate to capture the Integrated Part Load Value (IPLV) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IPLV on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Integrated Part Load Value (IPLV) | The IPLV listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 33
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph of the lamp nameplate showing manufacturer | Manufacturer on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-14 | Kenny Liljestrom |  | Add | 12
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | EECP | 2 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph of the lamp nameplate showing model number | Model number on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-14 | Kenny Liljestrom |  | Add | 12
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | EECP | 3 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Existing ballast manufacturer | Existing ballast manufacturer | Text Box | [8 empty] | Inspections | Photograph of the lighting fixture ballast showing the manufacturer and model number; if possible, look for any manufacturing dates on the ballast | Manufacturer on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-14 | Kenny Liljestrom |  | Add | 29
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | EECP | 4 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Existing ballast model number | Existing ballast model number | Text Box | [8 empty] | Inspections | Photograph of the lighting fixture ballast showing the manufacturer and model number | Model number on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-14 | Kenny Liljestrom |  | Add | 29
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | EECP | 5 | Due to testing considerations, only a product that can operate from an electronic instant start ballast is eligible. Re-ballast is not eligible. Replacement lamps designed to operate off of existing magnetic ballasts or off of other types of electronic ballasts are not eligible. | Yes |  | Is the ballast existing and an electronic instant start type? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the Ballast make and model listed in EECP to locate a manufacturer specification sheet; or use the inspection photos from the ballast nameplate to determine the Start Type and if possible, look for any manufacturing dates on the ballast | The ballast should NOT be brand new and have a start type listed as Instant Start on the ballast nameplate or manufacturer spec sheet | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 61
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | EECP | 6 | Title-24 Code Requirements for Lighting Alterations | Yes |  | Code Exemption for: Retrofitting < 10% in an enclosed space or <= 50 total per floor or tenant? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | Count the number of lighting fixtures retrofitted and the total number of fixtures | The total fixtures retrofitted should be less than 50 total or less than 10% of the total fixtures on the premise | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 95
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | AR | Any | QA Checklist | 7 | Even though POE is not explicitly required for approval by the California Public Utilities Commission (CPUC), all program administrators and third-party program implementers are required to collect data, as stated in the Date Collection Requirements section, that will satisfy POU requirements. R843 This technology is dependent upon the existing condition baseline, and the data collection requirements are intended to provide sufficient evidence of the disposal method and replacement of the existing products, including verification of the ballast and the compatibility. | Yes |  | Has all Preponderance of Evidence (POE) including existing system controls functionality with replacements, reasons for retrofitting to LED, and future plans without incentives been documented and submitted? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Review the Program Influence documents to ensure all POE requirements are met and adequate | Ensure the POE document includes existing system controls functionality with replacements, reasons for retrofitting to LED, and future plans without incentives | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 207
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | AR | Any | EECP | 8 | Good to have | No |  | Who was the party that filled out the POE documentation? | Drop Down List | Tenant;Owner;Owner Representative;Implementer; | [7 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | Not configured in original upload | 2021-10-20 | Kenny Liljestrom | Implementers responsible for POE documentation | Add | 56
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | EECP | 9 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Total number of fixture on site | Pre-Existing Conditions: Total number of fixtures on site | Numeric Value | [8 empty] | Inspections | The total quantity of lamps can be counted In lieu of verifying this field | No need to update data in EECP since this is for Pre-Existing conditions | QA Checklist | An installation report which shows down the total fixtures on site | There are no pass or fail criteria for the property, this is a data collection requirement | Update property label to include "Existing Conditions:" | 2021-06-14 | Kenny Liljestrom |  | Add | 57
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | EECP | 10 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Number of fixtures sampled | Pre-Existing Conditions: Number of Fixtures Sampled | Numeric Value | [8 empty] | Inspections | The total quantity of lamps can be counted In lieu of verifying this field | No need to update data in EECP since this is for Pre-Existing conditions | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Update property label to include "Pre-Existing Conditions:" | 2021-06-14 | Kenny Liljestrom |  | Add | 51
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | EECP | 11 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Number of lamps per fixture | Pre-Existing Conditions: Number of Lamps per Fixture | Numeric Value | [8 empty] | Inspections | The total quantity of lamps can be counted In lieu of verifying this field | No need to update data in EECP since this is for Pre-Existing conditions | QA Checklist | Review the installation report which should shows how many lamps are in each lighting fixture | The value should match what is listed in EECP | Update property label to include "Pre-Existing Conditions:" | 2021-06-14 | Kenny Liljestrom |  | Add | 52
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | EECP | 12 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Number of ballasts per fixture | Pre-Existing Conditions: Number of Ballasts per Fixture | Numeric Value | [8 empty] | Inspections | The total quantity of lamps can be counted In lieu of verifying this field | No need to update data in EECP since this is for Pre-Existing conditions | QA Checklist | An installation report which shows how many ballasts are in each lighting fixture | The value should match what is listed in EECP | Update property label to include "Pre-Existing Conditions:" | 2021-06-14 | Kenny Liljestrom |  | Add | 55
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | EECP | 13 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Existing fluorescent lamp wattage | Pre-Existing Conditions: Fluorescent Lamp Wattage (W) | Numeric Value | [8 empty] | Inspections | Look for any existing fluorescent tubes on site, record or document the existing lamp wattage | The value should match what is listed in EECP | QA Checklist | Installation report should indicate what the existing and proposed lighting wattages are | The value should match what is listed in EECP | Update property label to include "Pre-Existing Conditions:" | 2021-06-14 | Kenny Liljestrom |  | Add | 53
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | EECP | 14 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Disposal method of tubes | Disposal method of tube | Drop Down List | Abandoned in Place;Removed and Disposed of Properly;Other; | [6 empty] | Must be 'Removed and Disposed of Properly' | QA Checklist | Contractor or implementer should provide records of the lamps being disposed of | There must be proof of lamp disposal in one of the submitted documents | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-14 | Kenny Liljestrom |  | Add | 23
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | EECP | 15 | De-lamping is not eligible. | Yes |  | Have the fixtures been delamped? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 32
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | QA Checklist | 16 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes |  | Has the manufacturer cut sheet been submitted? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | Check the submitted documents in EECP for a manufacturer specification sheet | Ensure the manufacturer specification sheet was submitted to EECP | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 46
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | QA Checklist | 17 | The lamp must be listed under the Primary Use Category “Replacement Lamps (“plug and play”) (UL Type A)” or “Dual Mode Internal Driver (UL Type A and Type B)” on the current Design Lights Consortium qualified product list (https://www.designlights.org/search/). | Yes |  | Is the lamp listed on the most recent version of the DesignLights Consortium (DLC) list? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | On the DLC website, use the make and model of the lighting to see if the equipment exists in the database | The make and model from EECP should be present on the DLC database | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 88
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | QA Checklist | 18 | LED tube must be 4-foot and designated as UL Type A or UL Type A+B, but must be configured as a UL Type A. | Yes |  | 4-ft LED Tube Type | Drop Down List | UL Type A;UL Type B;UL Type C;ULType A + B; | [6 empty] | Must be 'UL Type A' or 'UL Type A + B' | QA Checklist | Use the DLC list using the make and model to check the "lamp designation" | The lamp must be listed as being UL Type A or UL Type A + B | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 18
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | QA Checklist | 19 | The lamp must be listed under the Primary Use Category “Replacement Lamps (“plug and play”) (UL Type A)” or “Dual Mode Internal Driver (UL Type A and Type B)” on the current Design Lights Consortium qualified product list (https://www.designlights.org/search/). | Yes |  | Primary Use Category | Drop Down List | Replacement Lamps (“plug and play”) (UL Type A);Dual Mode Internal Driver (UL Type A and Type B);Other; | [6 empty] | Must not be 'Other' | QA Checklist | Use the DLC list using the make and model to check the "Primary Use Category" | The Primary Use Category must be listed as Replacement Lamps (“plug and play”) (UL Type A); Dual Mode Internal Driver (UL Type A and Type B) | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 20
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | QA Checklist | 20 | TLEDs must be on the current DLC qualified products list and have a listed efficacy of 145 LPW or higher. | Yes |  | System Efficacy, Lumens/Watt (LPW) listed on DLC | Numeric Value | [7 empty] | Must be >= 145 | QA Checklist | Use the DLC list using the make and model to check the listed "efficacy" | The listed efficacy must be greater than or equal to 145 | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 48
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | QA Checklist | 21 | Program Requirements for LED T8 Lamps Table | Yes |  | CRI | Numeric Value | [7 empty] | Must be >= 80 | QA Checklist | Use the DLC list using the make and model to check the "CRI" | The CRI must be greater than or equal to 80 | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 3
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | QA Checklist | 22 | Program Requirements for LED T8 Lamps Table | Yes |  | Kelvin Correlated Color Temperature (CCT) | Numeric Value | [7 empty] | Must be >= 2200 and <= 6500 | QA Checklist | Use the DLC list using the make and model to check the "CCT" | Ensure the CCT is between 2200 and 6500 | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 41
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | QA Checklist | 23 | Program Requirements for LED T8 Lamps Table | Yes |  | Power Factor | Numeric Value | [7 empty] | Must be >= 0.90 | QA Checklist | Check the DLC list to ensure the Power Factor is greater than or equal to 0.90 | Check the DLC list to ensure the Power Factor is greater than or equal to 0.90 | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 12
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | QA Checklist | 24 | Program Requirements for LED T8 Lamps Table | Yes |  | Total Harmonic Distortion | Numeric Value | [7 empty] | Must be <= 20% | QA Checklist | Use the DLC list using the make and model to check the "Total Harmonic Distortion" | The Total Harmonic Distortion must be less than or equal to 20% | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 25
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | QA Checklist | 25 | Program Requirements for LED T8 Lamps Table | Yes |  | L70 Lumen Maintenance Hours | Numeric Value | [7 empty] | Must be >= 50000 | QA Checklist | All products listed on the DLC meet this requirement | No need to verify this requirement | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 27
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | QA Checklist | 26 | Program Requirements for LED T8 Lamps Table | Yes |  | Minimum Warranty | Drop Down List | >= 5 Years;< 5 Years; | [6 empty] | Must be >= 5 Years | QA Checklist | All products listed on the DLC meet this requirement | No need to verify this requirement | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 16
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any | QA Checklist | 27 | The LED T8 Lamp specification sheet must list all of the compatible ballast model numbers to ensure proper operation of the measure. | Yes |  | Does the submitted lamp specification sheet list the installed ballast model number showing it to be compatible with the installed lamp? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the existing ballast make and model listed in EECP and cross check the lamp manufacturer specification sheet | The existing ballast listed by the implementer should be listed on the specification sheet showing compatibility | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 136
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-08 | Kenny Liljestrom |  | Add | 12
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-08 | Kenny Liljestrom |  | Add | 5
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any | EECP | 3 | The measure must replace a lumen equivalent lamp/fixture of higher wattage. (See Measure Case Description). | Yes | Watts | Wattage | Numeric Value | [8 empty] | QA Checklist | Installation report should indicate what the proposed lighting wattages are | The value should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-08 | Kenny Liljestrom |  | Add | 7
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any | EECP | 4 | The measure must replace a lumen equivalent lamp/fixture of higher wattage. (See Measure Case Description). | Yes | Replace Higher Wattage | Does this fixture/retrofit kit replace a lumen equivalent lamp/fixture of higher wattage? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | Installation report should indicate what the existing and proposed fixtures wattages are | The existing wattage should be greater than or equal to the proposed wattage | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-08 | Kenny Liljestrom |  | Add | 89
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any | QA Checklist | 5 | The measure must be on the DesignLights Consortium (DLC) qualified product list (QPL) (https://www.designlights.org/search/). The product efficacy must meet or exceed the specified “measure case” efficacy based on the “rated” or “measured” efficacy in the DLC database. This requirement is to ensure the efficacy reported by the manufacturer has been confirmed by a third-party entity. | Yes |  | Replacement fixture/retrofit kit on the most recent version of the DLC qualified product list? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | On the DLC website, use the make and model of the lighting to see if the equipment exists in the database | The make and model from EECP should be present on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 94
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any | QA Checklist | 6 | Only premium fixtures will qualify for the measure case descriptions | Yes |  | Fixture/retrofit kit listing in the Technical Requirements table (V5) on DLC under Classification | Drop Down List | Standard;Premium;Other | [6 empty] | Must be Premium | QA Checklist | Use the DLC list using the make and model to check the "Classification" | The fixture must be listed as being Premium | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 97
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any | QA Checklist | 7 | The LED fixture or retrofit kit must be listed in the Technical Requirements table (V5) by the DLC under the General Category “High Bay” and under the Primary Use Designations as follows: R1300 • High-Bay Aisle Luminaires • High-Bay Luminaires for Commercial and Industrial Buildings • Low-Bay Luminaires for Commercial and Industrial Buildings • Retrofit Kits for High-Bay Luminaires for Commercial and Industrial Buildings • Retrofit Kits for Low-Bay Luminaires for Commercial and Industrial Buildings | Yes |  | Fixture/retrofit kit listing in the Technical Requirements table (V5) on DLC under Primary Use Designations? | Drop Down List | High-Bay Aisle Luminaires;High-Bay Luminaires for Commercial and Industrial Buildings;Low-Bay Luminaires for Commercial and Industrial Buildings;Retrofit Kits for High-Bay Luminaires for Commercial and Industrial Buildings;Retrofit Kits for Low-Bay Luminaires for Commercial and Industrial Buildings;Other; | [6 empty] | Must not be 'Other' | QA Checklist | Use the DLC list using the make and model to check the "Primary Use Designation" | The fixture must be listed as being one of the following options: High-Bay Aisle Luminaires; High-Bay Luminaires for Commercial and Industrial Buildings; Low-Bay Luminaires for Commercial and Industrial Buildings; Retrofit Kits for High-Bay Luminaires for Commercial and Industrial Buildings; Retrofit Kits for Low-Bay Luminaires for Commercial and Industrial Buildings; | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 108
0 | SWLG011 | 3 | LED, High or Low Bay | A | Any | Any | QA Checklist | 8 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 4500 and < 5400 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 4500 and < 5400 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | A | Any | Any | QA Checklist | 9 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 130 and < 150 | EECP | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | B | Any | Any | QA Checklist | 10 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 5400 and < 6500 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 5400 and < 6500 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | B | Any | Any | QA Checklist | 11 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | C | Any | Any | QA Checklist | 12 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 6500 and < 7800 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 6500 and < 7800 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | C | Any | Any | QA Checklist | 13 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | D | Any | Any | QA Checklist | 14 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 7800 and < 9400 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 7800 and < 9400 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | D | Any | Any | QA Checklist | 15 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | E | Any | Any | QA Checklist | 16 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 9400 and < 11800 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 9400 and < 11800 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | E | Any | Any | QA Checklist | 17 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | F | Any | Any | QA Checklist | 18 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 11800 and < 14800 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 11800 and < 14800 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | F | Any | Any | QA Checklist | 19 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | G | Any | Any | QA Checklist | 20 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 14800 and < 18500 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 14800 and < 18500 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | G | Any | Any | QA Checklist | 21 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | H | Any | Any | QA Checklist | 22 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 18500 and < 23100 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 18500 and < 23100 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | H | Any | Any | QA Checklist | 23 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | I | Any | Any | QA Checklist | 24 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 23100 and < 30000 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 23100 and < 30000 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | I | Any | Any | QA Checklist | 25 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | J | Any | Any | QA Checklist | 26 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 30000 and < 39000 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 30000 and < 39000 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | J | Any | Any | QA Checklist | 27 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | K | Any | Any | QA Checklist | 28 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 39000 and < 50700 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 39000 and < 50700 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | K | Any | Any | QA Checklist | 29 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | L | Any | Any | QA Checklist | 30 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 50700 and < 65900 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 50700 and < 65900 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | L | Any | Any | QA Checklist | 31 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | M | Any | Any | QA Checklist | 32 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 4500 and < 5400 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 4500 and < 5400 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | M | Any | Any | QA Checklist | 33 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | N | Any | Any | QA Checklist | 34 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 5400 and < 6500 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 5400 and < 6500 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | N | Any | Any | QA Checklist | 35 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | O | Any | Any | QA Checklist | 36 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 6500 and < 7800 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 6500 and < 7800 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | O | Any | Any | QA Checklist | 37 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | P | Any | Any | QA Checklist | 38 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 7800 and < 9400 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 7800 and < 9400 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | P | Any | Any | QA Checklist | 39 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | Q | Any | Any | QA Checklist | 40 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 9400 and < 11800 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 9400 and < 11800 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | Q | Any | Any | QA Checklist | 41 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | R | Any | Any | QA Checklist | 42 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 11800 and < 14800 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 11800 and < 14800 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | R | Any | Any | QA Checklist | 43 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | S | Any | Any | QA Checklist | 44 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 14800 and < 18500 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 14800 and < 18500 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | S | Any | Any | QA Checklist | 45 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | T | Any | Any | QA Checklist | 46 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 18500 and < 23100 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 18500 and < 23100 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | T | Any | Any | QA Checklist | 47 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | U | Any | Any | QA Checklist | 48 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 23100 and < 30000 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 23100 and < 30000 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | U | Any | Any | QA Checklist | 49 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | V | Any | Any | QA Checklist | 50 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 30000 and < 39000 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 30000 and < 39000 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | V | Any | Any | QA Checklist | 51 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | W | Any | Any | QA Checklist | 52 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 39000 and < 50700 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 39000 and < 50700 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | W | Any | Any | QA Checklist | 53 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | X | Any | Any | QA Checklist | 54 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [7 empty] | must be >= 50700 and < 65900 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 50700 and < 65900 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | X | Any | Any | QA Checklist | 55 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [6 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any | QA Checklist | 56 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Kelvin Correlated Color Temperature (CCT) | Numeric Value | [7 empty] | Must be <= 5700 | QA Checklist | Use the DLC list using the make and model to check the 'CCT' | The fixture CCT must be <= 5700 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 41
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any | QA Checklist | 57 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | What is the fixture Color Rendering Index (CRI)? | Numeric Value | [7 empty] | Must be >= 70 | QA Checklist | Use the DLC list using the make and model to check the 'CRI' | The fixture CCT must be >= 70 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 48
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any | QA Checklist | 58 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | L90 Lumen Maintenance Hours | Numeric Value | [7 empty] | Must be >= 36,000 | QA Checklist | All products listed on the DLC meet this requirement | No validation criteria | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph of the lamp nameplate showing manufacturer | Manufacturer on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-08 | Kenny Liljestrom |  | Add | 12
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph of the lamp nameplate showing model number | Model number on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-08 | Kenny Liljestrom |  | Add | 5
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | EECP | 5 | To ensure that code requirements for lighting power and controls are being met, the following data submission requirements must be met for all delivery types and measure application types. •Documentation showing that the retrofitted space has achieved a lighting power density that is < 80% of allowable Title 24 LPD for that space type. •Title 24 compliance documentation verifying the existence of required automated shut-off controls compliant with 2019 Title 24 §130.1(c)1-8 Auto-Shut-off Control. •Only for AR measures, the customer must confirm that existing automated control functionality remains intact after installation. (See Preponderance of Evidence Requirements below.) | Yes | Code Exemptions | Does this project meet one of the Code Exemptions: Retrofitting < 10% of luminaires in an enclosed space or retrofitting <= 50 total luminaires per floor or tenant space? | Drop Down List | Yes;No; | Equal | Yes |  |  |  |  | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-07-08 | Kenny Liljestrom |  | Add | 170
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | AR | Any | EECP | 6 | All program administrators and third-party program implementers are required to collect data as stated in the Date Collection Requirements section that will satisfy POE requirements. The data collection requirements are intended to provide establish programmatic evidence and include questions about existing system functionality, reasons for retrofitting to LED, and potential future plans without provided incentives. | Yes | POE Docs Submitted | Has all Preponderance of Evidence (POE) including existing system controls functionality with replacements, reasons for retrofitting to LED, and future plans without incentives been documented and submitted? | Drop Down List | Yes;No; | Equal | Yes |  |  |  |  | Must be 'Yes' | QA Checklist | Review the Program Influence documents to ensure all POE requirements are met and adequate | All program administrators and third-party program implementers are required to collect data as stated in the Date Collection Requirements section that will satisfy POE requirements. The data collection requirements are intended to provide establish programmatic evidence and include questions about existing system functionality, reasons for retrofitting to LED, and potential future plans without provided incentives. | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 7/30/20210 | Kenny Liljestrom |  | Add | 207
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | AR | Any | EECP | 7 | Good to have | No | POE Contact | Who was the party that filled out the POE documentation? | Drop Down List | Tenant;Owner;Owner Representative;Implementer; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-10-20 | Kenny Liljestrom | Implementers responsible for POE documentation | Add | 56
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | EECP | 8 | Existing lamps and ballasts must be fully demolished and properly disposed. “Abandon-in-place” demolition of existing ballasts is not eligible. | Yes | Disposal Method Tube | Disposal method of tube | Drop Down List | Abandoned in Place;Removed_Disposed of Properly;Other; | Equal | Removed_Disposed of Properly |  |  |  |  | Must be 'Removed and Disposed of Properly' | QA Checklist | The implementer should provide documentation or proof of the lamp disposal method | The lamps must be properly disposed of, not abandoned in place | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-07-08 | Kenny Liljestrom |  | Add | 23
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | EECP | 9 | The LED tube must be 4-foot and designated as UL Type B, UL Type A+B, or UL Type C. UL Type A+B (dual mode) lamps must be installed in a Type B configuration with the existing ballast removed. | Yes | UL Type Config | If UL Type A + B Configuration, was the existing ballast removed? | Drop Down List | Yes;No;N/A; | Not Equal | No |  |  |  |  | Conditional Field If LED Tube Type is 'UL Type A + B', answer must be Yes | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-07-08 | Kenny Liljestrom |  | Add | 65
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | EECP | 10 | The LED tube must be compatible with the installed system lighting controls. For example, if the lighting system includes dimming controls, the new LED tube must be dimmable and compatible with the installed dimming system. | Yes | Compatible with existing controls | Is the new lighting compatible with the existing lighting controls type (i.e. dimming controls with dimmable LED)? | Drop Down List | Yes;No; | Equal | Yes |  |  |  |  | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-07-08 | Kenny Liljestrom |  | Add | 114
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | EECP | 11 | De-lamping is not eligible. | Yes | Fixtures Delamped | Have the fixtures been delamped? | Drop Down List | Yes;No; | Equal | No |  |  |  |  | Must be 'No' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-07-08 | Kenny Liljestrom |  | Add | 32
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | AR | Any | EECP | 12 | The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Total number of fixtures on site | Pre-Existing Conditions: Total number of fixtures on site | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | The total quantity of lamps can be counted In lieu of verifying this field | No need to update data in EECP since this is for Pre-Existing conditions | QA Checklist | An installation report which shows down the total fixtures on site | There are no pass or fail criteria for the property, this is a data collection requirement | Update property label to include "Pre-Existing Conditions:" | 2021-07-08 | Kenny Liljestrom |  | Add | 57
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | AR | Any | EECP | 13 | The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Number of fixtures sampled | Pre-Existing Conditions: Number of Fixtures Sampled | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | The total quantity of lamps can be counted In lieu of verifying this field | No need to update data in EECP since this is for Pre-Existing conditions | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Update property label to include "Pre-Existing Conditions:" | 2021-07-08 | Kenny Liljestrom |  | Add | 51
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | AR | Any | EECP | 14 | The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Percent Sampled | Pre-Existing Conditions: Percent of Fixtures Sampled | Formula |  |  |  | Percentage | 10 | 100 |  | Must be >= 10% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | Update property label to include "Pre-Existing Conditions:" | 2021-07-08 | Kenny Liljestrom |  | Add | 52
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | AR | Any | EECP | 15 | The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Number of lamps per fixture | Pre-Existing Conditions: Number of Lamps per Fixture | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | The total quantity of lamps can be counted In lieu of verifying this field | No need to update data in EECP since this is for Pre-Existing conditions | QA Checklist | Review the installation report which should shows how many lamps are in each lighting fixture | The value should match what is listed in EECP | Update property label to include "Pre-Existing Conditions:" | 2021-07-08 | Kenny Liljestrom |  | Add | 52
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | AR | Any | EECP | 16 | The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Existing Watts | Pre-Existing Conditions: Fluorescent Lamp Wattage (W) | Numeric Value |  |  |  | General |  |  | 2 |  | Inspections | Look for any existing fluorescent tubes on site, record or document the existing lamp wattage | The value should match what is listed in EECP | QA Checklist | Installation report should indicate what the existing and proposed lighting wattages are | The value should match what is listed in EECP | Update property label to include "Pre-Existing Conditions:" | 2021-07-08 | Kenny Liljestrom |  | Add | 53
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | AR | Any | EECP | 17 | The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Auto Control Types | Pre-Existing Conditions: Automated controls type in retrofitted spaces | Drop Down List | Occupancy;Building Automation System (BAS);Time Clock;Other;None; | Not Equal | None |  |  |  |  | Must not be 'No Automated Controls' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | Update property label to include "Pre-Existing Conditions:" | 2021-07-30 | Kenny Liljestrom | Property updated to add additional drop-down item on 7/30/21 and update the validation criteria to make the property more clear | Add | 70
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | QA Checklist | 18 | Program Requirements for LED T8 Lamps Table | Yes |  | Is the lamp listed on the most recent version of the DesignLights Consortium (DLC) list? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | On the DLC website, use the make and model of the lighting to see if the equipment exists in the database | The make and model from EECP should be present on the DLC database | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 88
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | QA Checklist | 19 | The LED tube must be 4-foot and designated as UL Type B, UL Type A+B, or UL Type C. UL Type A+B (dual mode) lamps must be installed in a Type B configuration with the existing ballast removed. | Yes |  | LED Tube Type | Drop Down List | UL Type A;UL Type B;UL Type C;ULType A + B; | [6 empty] | Must be 'UL Type B', 'UL Type C' or 'UL Type A + B' | QA Checklist | Use the DLC list using the make and model to check the "lamp designation" | The lamp must be listed as being UL Type B, UL Type A + B, or UL Type C | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 13
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | QA Checklist | 20 | The lamp must be listed under the Primary Use Category “Internal Driver/Line Voltage (UL Type B) Lamps”, “Dual Mode Internal Driver (UL Type A and Type B)”, “2-Lamp External Driver (UL Type C) Lamps”, “3-Lamp External Driver (UL Type C) Lamps”, “4-Lamp External Driver (UL Type C) Lamps” on the current Design Lights Consortium qualified product list (https://www.designlights.org/search/). | Yes |  | Primary Use Category | Drop Down List | Internal Driver/Line Voltage (UL Type B) Lamps;Dual Mode Internal Driver (UL Type A and Type B);2-Lamp External Driver (UL Type C) Lamps;3-Lamp External Driver (UL Type C) Lamps;4-Lamp External Driver (UL Type C) Lamps;Other; | [6 empty] | Must not be 'Other' | QA Checklist | Use the DLC list using the make and model to check the "Primary Use Category" | The Primary Use Category must be listed as Internal Driver/Line Voltage (UL Type B) Lamps, Dual Mode Internal Driver (UL Type A and Type B), 2-Lamp External Driver (UL Type C) Lamps, 3-Lamp External Driver (UL Type C) Lamps, or 4-Lamp External Driver (UL Type C) Lamps. | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 20
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | QA Checklist | 21 | Must meet a minimum efficacy requirement stated in the Measure Case Description. | Yes |  | System Efficacy, Lumens/Watt (LPW) as listed on DLC | Numeric Value | [7 empty] | Must be >= 160 | QA Checklist | Use the DLC list using the make and model to check the listed "efficacy" | The listed efficacy must be greater than or equal to 160 | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 51
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | QA Checklist | 22 | Program Requirements for LED T8 Lamps Table | Yes |  | CRI | Numeric Value | [7 empty] | Must be >= 80 | QA Checklist | Use the DLC list using the make and model to check the "CRI" | The CRI must be greater than or equal to 80 | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 3
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | QA Checklist | 23 | Program Requirements for LED T8 Lamps Table | Yes |  | Kelvin Correlated Color Temperature (CCT) | Numeric Value | [7 empty] | Must be >= 2200 and <= 6500 | QA Checklist | Use the DLC list using the make and model to check the "CCT" | Ensure the CCT is between 2200 and 6500 | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 41
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | QA Checklist | 24 | Program Requirements for LED T8 Lamps Table | Yes |  | Power Factor | Numeric Value | [7 empty] | Must be >= 0.90 | QA Checklist | Check the DLC list to ensure the Power Factor is greater than or equal to 0.90 | Check the DLC list to ensure the Power Factor is greater than or equal to 0.90 | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 12
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | QA Checklist | 25 | Program Requirements for LED T8 Lamps Table | Yes |  | Total Harmonic Distortion | Numeric Value | [7 empty] | Must be <= 20% | QA Checklist | Use the DLC list using the make and model to check the "Total Harmonic Distortion" | The Total Harmonic Distortion must be less than or equal to 20% | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 25
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | QA Checklist | 26 | Program Requirements for LED T8 Lamps Table | Yes |  | L70 Lumen Maintenance Hours | Numeric Value | [7 empty] | Must be >= 50000 | QA Checklist | All products listed on the DLC meet this requirement | No need to verify this requirement | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 27
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any | QA Checklist | 27 | Program Requirements for LED T8 Lamps Table | Yes |  | Minimum Warranty | Drop Down List | >= 5 Years;< 5 Years; | [6 empty] | Must be >= 5 Years | QA Checklist | All products listed on the DLC meet this requirement | No need to verify this requirement | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 16
0 | SWPR001 | 1 | Ventilation Fan, Agriculture | Any | Any | Any | EECP | 1 | - | Pending | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the ventilation fan nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-21 | Kenny Liljestrom |  |  | 12
0 | SWPR001 | 1 | Ventilation Fan, Agriculture | Any | Any | Any | EECP | 2 | - | Pending | Model | Model | Text Box | [8 empty] | Inspections | Photograph the ventilation fan nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-21 | Kenny Liljestrom |  |  | 5
0 | SWPR001 | 1 | Ventilation Fan, Agriculture | Any | Any | Any | EECP | 3 | The measure is applicable for all existing agriculture facilities of any vintage. | Pending |  | Building type is existing Agricultural facility (any vintage)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | Observe the building type | The building type must be an existing agricultural facility | QA Checklist | Use the submitted installation report to determine the building type | The building type must be an existing agricultural facility | Property may be able to be configured at the enrollment level; if applicable, please configure at enrollment instead of measure level | 2021-09-21 | Kenny Liljestrom |  |  | 62
0 | SWPR001 | 1 | Ventilation Fan, Agriculture | A | Any | Any | EECP | 4 | A fan must have been tested by the Bioenvironmental and Structural Systems Laboratory (BESS Lab) ventilation fan testing facility at the University of Illinois to the specifications provided in the Base Case Description, and it must meet the minimum allowable cfm/W. (This value is a tradeoff between trying to encourage the highest practical efficiencies and still allowing most manufacturers to have at least one offering within the accepted range.) | Pending |  | Fan cfm/watt | Numeric Value | [7 empty] | Must be >= 14.0 | QA Checklist | Use the submitted manufacturer spec sheet (or make and model) to determine the fan efficiency (cfm/watt) | The fan efficiency should be >= 14 cfm/watt. This calculation can be completed by taking the flow rate (cfm) and dividing by the total input power (Watts) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 12
0 | SWPR001 | 1 | Ventilation Fan, Agriculture | B | Any | Any | EECP | 5 | A fan must have been tested by the Bioenvironmental and Structural Systems Laboratory (BESS Lab) ventilation fan testing facility at the University of Illinois to the specifications provided in the Base Case Description, and it must meet the minimum allowable cfm/W. (This value is a tradeoff between trying to encourage the highest practical efficiencies and still allowing most manufacturers to have at least one offering within the accepted range.) | Pending |  | Fan cfm/watt | Numeric Value | [7 empty] | Must be >= 20.4 | QA Checklist | Use the submitted manufacturer spec sheet (or make and model) to determine the fan efficiency (cfm/watt) | The fan efficiency should be >= 20.4 cfm/watt. This calculation can be completed by taking the flow rate (cfm) and dividing by the total input power (Watts) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 12
0 | SWPR001 | 1 | Ventilation Fan, Agriculture | C | Any | Any | EECP | 6 | A fan must have been tested by the Bioenvironmental and Structural Systems Laboratory (BESS Lab) ventilation fan testing facility at the University of Illinois to the specifications provided in the Base Case Description, and it must meet the minimum allowable cfm/W. (This value is a tradeoff between trying to encourage the highest practical efficiencies and still allowing most manufacturers to have at least one offering within the accepted range.) | Pending |  | Fan cfm/watt | Numeric Value | [7 empty] | Must be >= 21.9 | QA Checklist | Use the submitted manufacturer spec sheet (or make and model) to determine the fan efficiency (cfm/watt) | The fan efficiency should be >= 21.9 cfm/watt. This calculation can be completed by taking the flow rate (cfm) and dividing by the total input power (Watts) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 12
1 | SWPR002 | 1 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any | EECP | 1 | - | Pending | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the VFD Controls equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the VFD manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-17 | Kenny Liljestrom |  |  | 12
1 | SWPR002 | 1 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any | EECP | 2 | - | Pending | Model | Model | Text Box | [8 empty] | Inspections | Photograph the VFD Controls equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the VFD model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-17 | Kenny Liljestrom |  |  | 5
1 | SWPR002 | 1 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any | EECP | 3 | This measure is only applicable to the winery industry for process end-use applications. | Pending |  | Measure is installed for wine processing? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | Observe the building type | The building type must be a winery; or the pump must be serving a chilled wine loop | QA Checklist | Use the EEECP building type validation or installation report to determine the building type | The building type must be a winery; or the pump must be serving a chilled wine loop | This property can be configured at the enrollment level if Winery is a building type selection; if not, please configure at the measure level | 2021-09-17 | Kenny Liljestrom |  |  | 41
1 | SWPR002 | 1 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any | EECP | 4 | This measure involves the installation of a variable frequency drive (VFD) on an existing glycol pump motor. Chilled fluid, other than glycol, can be considered only if the unit energy savings (UES) is equal to or exceeds the UES of this measure. | Pending |  | Does the pump serve a glycol loop? | Drop Down List | Yes;No; | [7 empty] | QA Checklist | The installation report should indicate the type of loop the pump is serving | The pump can serve a glycol or non-glycol loop; if it is a non-glycol loop, the following property must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-17 | Kenny Liljestrom |  |  | 34
1 | SWPR002 | 1 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any | EECP | 5 | This measure involves the installation of a variable frequency drive (VFD) on an existing glycol pump motor. Chilled fluid, other than glycol, can be considered only if the unit energy savings (UES) is equal to or exceeds the UES of this measure. | Pending |  | If not a glycol loop, do the unit energy savings exceed the measure case savings? | Drop Down List | Yes;No;N/A; | [6 empty] | Must be 'Yes' or 'N/A' | QA Checklist | If the pump does not serve a glycol loop, the implementer/customer must provide proof the energy savings exceeds the savings from the workpaper; this may be present in the installation report or via a calculation file | The implementer/customer must provide proof the energy savings exceeds the savings from the workpaper | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-17 | Kenny Liljestrom |  |  | 81
1 | SWPR002 | 1 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any | EECP | 6 | Application of this measure is for the addition of a VFD on an existing glycol pump motor. The existing glycol pump(s) must operate at constant speed. | Pending |  | VFD installed on an existing constant speed pump motor? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | The implementer or customer should provide proof the existing pump motors are fixed/constant speed | Use the installation report or photographs to prove the motor is existing and operates at a constant speed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-17 | Kenny Liljestrom |  |  | 55
1 | SWPR002 | 1 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any | EECP | 7 | The VFD must have automated controls based on pressure feedback, fluid temperature feedback, and/or flow rate feedback. | Pending |  | VFD is automated by pressure, fluid temperature, or flow rate feedback? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the installation report to determine how the VFD will communicate with the pump motor | The VFD must operate based on feedback from the fluid pressure, temperature, or flow rate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-17 | Kenny Liljestrom |  |  | 71
1 | SWPR002 | 1 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any | EECP | 8 | The customer must provide documentation that the VFD is not installed on a back-up pump or redundant pump. | Pending |  | Documentation submitted showing VFD is not for backup pump? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the installation report to validate the VFD is not configured as a backup pump; the pump must be a primary | Implementer or customer should provide documentation showing the VFD is not acting as a backup pump | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-17 | Kenny Liljestrom |  |  | 59
0 | SWPR002 | 2 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the VFD Controls equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the VFD manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-23 | Kenny Liljestrom |  |  | 12
0 | SWPR002 | 2 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the VFD Controls equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the VFD model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-23 | Kenny Liljestrom |  |  | 5
0 | SWPR002 | 2 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any | EECP | 3 | This measure is only applicable to the winery industry for process end-use applications. | Yes |  | Measure is installed for wine processing? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | Observe the building type | The building type must be a winery; or the pump must be serving a chilled wine loop | QA Checklist | Use the EEECP building type validation or installation report to determine the building type | The building type must be a winery; or the pump must be serving a chilled wine loop | This property can be configured at the enrollment level if Winery is a building type selection; if not, please configure at the measure level | 2021-11-23 | Kenny Liljestrom |  |  | 41
0 | SWPR002 | 2 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any | EECP | 4 | This measure involves the installation of a variable frequency drive (VFD) on an existing glycol pump motor. Chilled fluid, other than glycol, can be considered only if the unit energy savings (UES) is equal to or exceeds the UES of this measure. | Yes |  | Does the pump serve a glycol loop? | Drop Down List | Yes;No; | [7 empty] | QA Checklist | The installation report should indicate the type of loop the pump is serving | The pump can serve a glycol or non-glycol loop; if it is a non-glycol loop, the following property must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 34
0 | SWPR002 | 2 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any | EECP | 5 | This measure involves the installation of a variable frequency drive (VFD) on an existing glycol pump motor. Chilled fluid, other than glycol, can be considered only if the unit energy savings (UES) is equal to or exceeds the UES of this measure. | Yes |  | If not a glycol loop, do the unit energy savings exceed the measure case savings? | Drop Down List | Yes;No;N/A; | [6 empty] | Must be 'Yes' or 'N/A' | QA Checklist | If the pump does not serve a glycol loop, the implementer/customer must provide proof the energy savings exceeds the savings from the workpaper; this may be present in the installation report or via a calculation file | The implementer/customer must provide proof the energy savings exceeds the savings from the workpaper | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 81
0 | SWPR002 | 2 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any | EECP | 6 | Application of this measure is for the addition of a VFD on an existing glycol pump motor. The existing glycol pump(s) must operate at constant speed. | Yes |  | VFD installed on an existing constant speed pump motor? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | The implementer or customer should provide proof the existing pump motors are fixed/constant speed | Use the installation report or photographs to prove the motor is existing and operates at a constant speed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 55
0 | SWPR002 | 2 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any | EECP | 7 | The VFD must have automated controls based on pressure feedback, fluid temperature feedback, and/or flow rate feedback. | Yes |  | VFD is automated by pressure, fluid temperature, or flow rate feedback? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the installation report to determine how the VFD will communicate with the pump motor | The VFD must operate based on feedback from the fluid pressure, temperature, or flow rate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 71
0 | SWPR002 | 2 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any | EECP | 8 | The customer must provide documentation that the VFD is not installed on a back-up pump or redundant pump. | Yes |  | Documentation submitted showing VFD is not for backup pump? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use the installation report to validate the VFD is not configured as a backup pump; the pump must be a primary | Implementer or customer should provide documentation showing the VFD is not acting as a backup pump | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 59
1 | SWPR004 | 1 | Circulating Block Heater | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-08 | Kenny Liljestrom |  | Add | 12
1 | SWPR004 | 1 | Circulating Block Heater | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-08 | Kenny Liljestrom |  | Add | 5
1 | SWPR004 | 1 | Circulating Block Heater | Any | NR | Any | EECP | 3 | For a normal replacement (NR) installation, the existing backup generator is eligible if it is not currently fitted with a circulating block heater or device utilizing similar electro-mechanical system to heat and circulate generator block pre-warming fluid. | Yes | Electro-Mechanical system | Before installation of the measure was the existing backup generator fitted with a circulating block heater or device utilizing similar electro-mechanical system to heat and circulate generator block pre-warming fluid? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Review the installation report to determine if the existing conditions are documented and whether or not the existing generator is fitted with a circulating block heater or electro-mechanical system to pre-warm the fluid | For a normal replacement (NR) installation, the existing backup generator is eligible if it is not currently fitted with a circulating block heater or device utilizing similar electro-mechanical system to heat and circulate generator block pre-warming fluid. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-08 | Kenny Liljestrom |  | Add | 218
1 | SWPR004 | 1 | Circulating Block Heater | Any | NC | Any | EECP | 4 | A new generator installation (i.e., new construction, NC), for which the base design prescribes a pre-heating device (e.g., thermosiphon heater) other than a circulating block heater or similar device is eligible to upgrade from base design to efficient design including a circulating block heater. | Yes |  | Does the base design prescribe a pre-heating device other than a circulating block heater? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Review the installation report to determine if the base design or code conditions are documented and whether or not the base design generator is fitted with a circulating block heater | A new generator installation (i.e., new construction, NC), for which the base design prescribes a pre-heating device (e.g., thermosiphon heater) other than a circulating block heater or similar device is eligible to upgrade from base design to efficient design including a circulating block heater. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-25 | Kenny Liljestrom |  | Add | 90
1 | SWPR004 | 1 | Circulating Block Heater | Any | Any | Any | EECP | 5 | Additional eligibility requirements regarding the installation include: • Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician). • Installer should follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. • Installation shall meet all applicable regulations including but not limited to latest NFPA Code 110 for Emergency Power Systems and NEC. | Yes | Qualified Tech | Was the installation of the circulating block heater performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician)? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-07-08 | Kenny Liljestrom |  | Add | 162
1 | SWPR004 | 1 | Circulating Block Heater | Any | Any | Any | EECP | 6 | Additional eligibility requirements regarding the installation include: • Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician). • Installer should follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. • Installation shall meet all applicable regulations including but not limited to latest NFPA Code 110 for Emergency Power Systems and NEC. | Yes | Installation Requirements | Did the Installer follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the circulating block heater to function at optimal energy efficiency? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-07-08 | Kenny Liljestrom |  | Add | 248
1 | SWPR004 | 1 | Circulating Block Heater | Any | Any | Any | EECP | 7 | Additional eligibility requirements regarding the installation include: • Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician). • Installer should follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. • Installation shall meet all applicable regulations including but not limited to latest NFPA Code 110 for Emergency Power Systems and NEC. | Yes |  | Installation meets latest NFPA Code 110 for Emergency Power Systems and NEC installation guidelines? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-25 | Kenny Liljestrom |  | Add | 100
1 | SWPR004 | 1 | Circulating Block Heater | Any | Any | Any | EECP | 8 | This measure is applicable to the following non-residential building types, of any vintage: Assembly; Manufacturing - Bio/Tech; Education - Community College; Manufacturing - Light Industrial; Education - Primary School; Office - Large; Education - Relocatable Classroom; Office - Small; Education - Secondary School; Restaurant - Fast-Food; Education - University; Restaurant - Sit-Down; Grocery; Retail - Multistory Large; Health/Medical - Hospital; Retail - Single-Story Large; Health/Medical - Nursing Home; Retail - Small; Lodging - Guest Rooms; Storage - Conditioned; Lodging - Hotel; Storage - Unconditioned; Lodging - Motel; Warehouse - Refrigerated | Yes |  | Building type | Drop Down List | Assembly;Manufacturing - Bio/ - Community College;Manufacturing - Light Industrial;Education - Primary School;Office - Large;Education - Relocatable Classroom;Office - Small;Education - Secondary School;Restaurant - Fast-Food;Education - University;Restaurant - Sit-Down;Grocery;Retail - Multistory Large;Health/Medical - Hospital;Retail - Single-Story Large;Health/Medical - Nursing Home;Retail - Small;Lodging - Guest Rooms;Storage - Conditioned;Lodging - Hotel;Storage - Unconditioned;Lodging - Motel;Warehouse - Refrigerated | [7 empty] | Inspections | While on site, observe and make note of the building type | The building type needs to be one of the following: Assembly, Manufacturing - Bio/Tech, Education - Community College, Manufacturing - Light Industrial, Education - Primary School, Office - Large, Education - Relocatable Classroom, Office - Small, Education - Secondary School, Restaurant - Fast-Food, Education - University, Restaurant - Sit-Down, Grocery, Retail - Multistory Large, Health/Medical - Hospital, Retail - Single-Story Large, Health/Medical - Nursing Home, Retail - Small, Lodging - Guest Rooms, Storage - Conditioned, Lodging - Hotel, Storage - Unconditioned, Lodging - Motel, Warehouse - Refrigerated | QA Checklist | Use the installation report or EECP to determine the building type | The building type needs to be one of the following: Assembly, Manufacturing - Bio/Tech, Education - Community College, Manufacturing - Light Industrial, Education - Primary School, Office - Large, Education - Relocatable Classroom, Office - Small, Education - Secondary School, Restaurant - Fast-Food, Education - University, Restaurant - Sit-Down, Grocery, Retail - Multistory Large, Health/Medical - Hospital, Retail - Single-Story Large, Health/Medical - Nursing Home, Retail - Small, Lodging - Guest Rooms, Storage - Conditioned, Lodging - Hotel, Storage - Unconditioned, Lodging - Motel, Warehouse - Refrigerated | Not configured in original upload | 2021-08-25 | Kenny Liljestrom |  | Add | 13
0 | SWPR004 | 2 | Circulating Block Heater | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-11 | Kenny Liljestrom |  |  | 12
0 | SWPR004 | 2 | Circulating Block Heater | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-11 | Kenny Liljestrom |  |  | 5
0 | SWPR004 | 2 | Circulating Block Heater | Any | Any | Any | EECP | 3 |  | Yes | Size | Back-up generator size (kW) | Numeric Value | [8 empty] | Inspections | Photograph the nameplate showing the capacity (kW) of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Review the make and model and locate the size (kW) of the backup generator | The generator size/power (kW) must algin with the measure case description |  | 2021-11-11 | Kenny Liljestrom |  |  | 27
0 | SWPR004 | 2 | Circulating Block Heater | Any | NR | Any | EECP | 4 | For a normal replacement (NR) installation, the existing backup generator is eligible if it is not currently fitted with a circulating block heater or device utilizing similar electro-mechanical system to heat and circulate generator block pre-warming fluid. | Yes | Electro-Mechanical system | Before installation of the measure was the existing backup generator fitted with a circulating block heater or device utilizing similar electro-mechanical system to heat and circulate generator block pre-warming fluid? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Review the installation report to determine if the existing conditions are documented and whether or not the existing generator is fitted with a circulating block heater or electro-mechanical system to pre-warm the fluid | For a normal replacement (NR) installation, the existing backup generator is eligible if it is not currently fitted with a circulating block heater or device utilizing similar electro-mechanical system to heat and circulate generator block pre-warming fluid. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-11 | Kenny Liljestrom |  |  | 218
0 | SWPR004 | 2 | Circulating Block Heater | Any | NC | Any | EECP | 5 | A new generator installation (i.e., new construction, NC), for which the base design prescribes a pre-heating device (e.g., thermosiphon heater) other than a circulating block heater or similar device is eligible to upgrade from base design to efficient design including a circulating block heater. | Yes |  | Does the base design prescribe a pre-heating device other than a circulating block heater? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Review the installation report to determine if the base design or code conditions are documented and whether or not the base design generator is fitted with a circulating block heater | A new generator installation (i.e., new construction, NC), for which the base design prescribes a pre-heating device (e.g., thermosiphon heater) other than a circulating block heater or similar device is eligible to upgrade from base design to efficient design including a circulating block heater. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-11 | Kenny Liljestrom |  |  | 90
0 | SWPR004 | 2 | Circulating Block Heater | Any | Any | Any | EECP | 6 | Additional eligibility requirements regarding the installation include: • Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician). • Installer should follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. • Installation shall meet all applicable regulations including but not limited to latest NFPA Code 110 for Emergency Power Systems and NEC. | Yes | Qualified Tech | Was the installation of the circulating block heater performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician)? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-11 | Kenny Liljestrom |  |  | 162
0 | SWPR004 | 2 | Circulating Block Heater | Any | Any | Any | EECP | 7 | Additional eligibility requirements regarding the installation include: • Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician). • Installer should follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. • Installation shall meet all applicable regulations including but not limited to latest NFPA Code 110 for Emergency Power Systems and NEC. | Yes | Installation Requirements | Did the Installer follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the circulating block heater to function at optimal energy efficiency? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-11 | Kenny Liljestrom |  |  | 248
0 | SWPR004 | 2 | Circulating Block Heater | Any | Any | Any | - | 7 | Additional eligibility requirements regarding the installation include: • Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician). • Installer should follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. • Installation shall meet all applicable regulations including but not limited to latest NFPA Code 110 for Emergency Power Systems and NEC. | No | NFPA Code | Installation meets latest NFPA Code 110 for Emergency Power Systems and NEC installation guidelines? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-01-05 | Kenny Liljestrom | Program ops request to remove property since contractors are held liable in their contracts to install equipment in accordance with all safety and energy codes |  | 100
0 | SWPR004 | 2 | Circulating Block Heater | Any | Any | Any | EECP | 8 | This measure is applicable to the following non-residential building types, of any vintage: Assembly; Manufacturing - Bio/ - Community College; Manufacturing - Light Industrial; Education - Primary School; Office - Large; Education - Relocatable Classroom; Office - Small; Education - Secondary School; Restaurant - Fast-Food; Education - University; Restaurant - Sit-Down; Grocery; Retail - Multistory Large; Health/Medical - Hospital; Retail - Single-Story Large; Health/Medical - Nursing Home; Retail - Small; Lodging - Guest Rooms; Storage - Conditioned; Lodging - Hotel; Storage - Unconditioned; Lodging - Motel; Warehouse - Refrigerated | Yes |  | Building type | Drop Down List | Assembly;Manufacturing - Bio/ - Community College;Manufacturing - Light Industrial;Education - Primary School;Office - Large;Education - Relocatable Classroom;Office - Small;Education - Secondary School;Restaurant - Fast-Food;Education - University;Restaurant - Sit-Down;Grocery;Retail - Multistory Large;Health/Medical - Hospital;Retail - Single-Story Large;Health/Medical - Nursing Home;Retail - Small;Lodging - Guest Rooms;Storage - Conditioned;Lodging - Hotel;Storage - Unconditioned;Lodging - Motel;Warehouse - Refrigerated | [7 empty] | Inspections | While on site, observe and make note of the building type | The building type needs to be one of the following: Assembly, Manufacturing - Bio/Tech, Education - Community College, Manufacturing - Light Industrial, Education - Primary School, Office - Large, Education - Relocatable Classroom, Office - Small, Education - Secondary School, Restaurant - Fast-Food, Education - University, Restaurant - Sit-Down, Grocery, Retail - Multistory Large, Health/Medical - Hospital, Retail - Single-Story Large, Health/Medical - Nursing Home, Retail - Small, Lodging - Guest Rooms, Storage - Conditioned, Lodging - Hotel, Storage - Unconditioned, Lodging - Motel, Warehouse - Refrigerated | QA Checklist | Use the installation report or EECP to determine the building type | The building type needs to be one of the following: Assembly, Manufacturing - Bio/Tech, Education - Community College, Manufacturing - Light Industrial, Education - Primary School, Office - Large, Education - Relocatable Classroom, Office - Small, Education - Secondary School, Restaurant - Fast-Food, Education - University, Restaurant - Sit-Down, Grocery, Retail - Multistory Large, Health/Medical - Hospital, Retail - Single-Story Large, Health/Medical - Nursing Home, Retail - Small, Lodging - Guest Rooms, Storage - Conditioned, Lodging - Hotel, Storage - Unconditioned, Lodging - Motel, Warehouse - Refrigerated | Not configured in original upload | 2021-11-11 | Kenny Liljestrom |  |  | 13
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any | EECP | 1 | - | Pending | Manufacturer | VSD Manufacturer | Text Box | [8 empty] | Inspections | Photograph the ventilation fan nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-21 | Kenny Liljestrom |  |  | 16
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any | EECP | 2 | - | Pending | Model | VSD Model | Text Box | [8 empty] | Inspections | Photograph the ventilation fan nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-21 | Kenny Liljestrom |  |  | 9
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any | EECP | 3 | - | Pending |  | Motor Manufacturer | Text Box | [8 empty] | Inspections | Photograph the ventilation fan nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-21 | Kenny Liljestrom |  |  | 18
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any | EECP | 4 | - | Pending |  | Motor Model | Text Box | [8 empty] | Inspections | Photograph the ventilation fan nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-21 | Kenny Liljestrom |  |  | 11
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any | QA Checklist | 5 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending | Fan Power Rating | The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. | None | - | [6 empty] | - | QA Checklist | Use the manufacturer spec sheet (or make and model) to find the size of the fan motor(s) | The fan power (hp) must meet the measure case description; if there is any deviation from the measure case, the motor must not be < 10 or > 150 | - | - | - |  | 2021-09-21 | Kenny Liljestrom |  |  | 89
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | A | Any | Any | EECP | 6 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [7 empty] | Inspections | Observe the building type | The building/facility must be either an industrial or an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be either an industrial or an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | B | Any | Any | EECP | 7 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [7 empty] | Inspections | Observe the building type | The building/facility must be either an industrial or an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be either an industrial or an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | C | Any | Any | EECP | 8 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [7 empty] | Inspections | Observe the building type | The building/facility must be either an industrial or an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be either an industrial or an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | D | Any | Any | EECP | 9 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [7 empty] | Inspections | Observe the building type | The building/facility must be either an industrial or an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be either an industrial or an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | E | Any | Any | EECP | 10 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [7 empty] | Inspections | Observe the building type | The building/facility must be either an industrial or an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be either an industrial or an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | F | Any | Any | EECP | 11 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [7 empty] | Inspections | Observe the building type | The building/facility must be either an industrial or an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be either an industrial or an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | G | Any | Any | EECP | 12 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [7 empty] | Inspections | Observe the building type | The building/facility must be either an industrial or an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be either an industrial or an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | H | Any | Any | EECP | 13 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [6 empty] | Must be 'Agricultural' | Inspections | Observe the building type | The building/facility must be an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | I | Any | Any | EECP | 14 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [6 empty] | Must be 'Agricultural' | Inspections | Observe the building type | The building/facility must be an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | J | Any | Any | EECP | 15 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [6 empty] | Must be 'Agricultural' | Inspections | Observe the building type | The building/facility must be an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | K | Any | Any | EECP | 16 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [6 empty] | Must be 'Agricultural' | Inspections | Observe the building type | The building/facility must be an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | L | Any | Any | EECP | 17 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [6 empty] | Must be 'Agricultural' | Inspections | Observe the building type | The building/facility must be an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any | EECP | 18 | The customer must have an existing electrically operated fixed-speed fan installed on site or plans to install a new electrically operated fixed-speed fan. The existing baghouse, fan, and motor must be in proper operating condition. The baghouse fan motor must be compatible with a variable speed drive (VSD).1 | Pending |  | Customer has (or plans to have) existing, operational, and VSD compatible fixed speed fan? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Use an installation report or photographs of the fan motor to prove the existing and proposed systems which show proof of the motor not being changed out during the project | The existing fan motor must be already installed (or planned to be installed for new construction applications), operational (working), and compatible with a VSD; the fan motor should not be changed out to be compatible with a VSD, photographs of the motor before and after the installation will prove the motor was not replaced during the project | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 90
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any | EECP | 19 | There must be no previous VSD or failed VSD installed on the baghouse existing fan motor. This measure cannot be used for the following fan applications: • HVAC fan • An individual fan motor rated less than 10 hp or higher than 150 hp • A two-speed fan motor • A fan motor with an existing VSD | Pending |  | Did existing fans (not HVAC related) previously have VSD controls? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | QA Checklist | Use an installation report or photographs of the fan motor showing there are currently no controls in place to vary the speed of the motor | The existing fan motor must not have a VSD installed; photographs of the motor before and after the installation will prove the motor did not have VSD controls already installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 66
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any | EECP | 20 | The installed VSD must be controlled based on static pressure, airflow rate (cfm), or velocity at the lowest required rate to keep particulates suspended in the air stream. The VSD is recommended to meet requirements as specified by IEEE Standard 519-2014.2. | Pending |  | VSD controlled by static pressure, airflow, or duct velocity and meets IEEE 519-2014.2 requirements? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | An installation report should indicate the method of control for the VSD feedback | The VSD must be controlled by static pressure, airflow, or duct velocity and the installation report should indicate which method of control is being used | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 100
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | H | Any | Any | EECP | 21 | The fan/blower must not be a designed high-pressure blower. High pressure blowers have designed capacities of less than 150 cfm per rated horsepower. (Applicable only to fan motors larger than 50 hp.) | Pending |  | Is the fan/blower a designed high-pressure blower (design capacity <= 150 cfm/hp)? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet (or make and model) to determine the type of fan/blower being used | The fan/blower must not be a 'high-pressure blower' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 82
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | I | Any | Any | EECP | 22 | The fan/blower must not be a designed high-pressure blower. High pressure blowers have designed capacities of less than 150 cfm per rated horsepower. (Applicable only to fan motors larger than 50 hp.) | Pending |  | Is the fan/blower a designed high-pressure blower (design capacity <= 150 cfm/hp)? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet (or make and model) to determine the type of fan/blower being used | The fan/blower must not be a 'high-pressure blower' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 82
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | J | Any | Any | EECP | 23 | The fan/blower must not be a designed high-pressure blower. High pressure blowers have designed capacities of less than 150 cfm per rated horsepower. (Applicable only to fan motors larger than 50 hp.) | Pending |  | Is the fan/blower a designed high-pressure blower (design capacity <= 150 cfm/hp)? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet (or make and model) to determine the type of fan/blower being used | The fan/blower must not be a 'high-pressure blower' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 82
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | K | Any | Any | EECP | 24 | The fan/blower must not be a designed high-pressure blower. High pressure blowers have designed capacities of less than 150 cfm per rated horsepower. (Applicable only to fan motors larger than 50 hp.) | Pending |  | Is the fan/blower a designed high-pressure blower (design capacity <= 150 cfm/hp)? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet (or make and model) to determine the type of fan/blower being used | The fan/blower must not be a 'high-pressure blower' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 82
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | L | Any | Any | EECP | 25 | The fan/blower must not be a designed high-pressure blower. High pressure blowers have designed capacities of less than 150 cfm per rated horsepower. (Applicable only to fan motors larger than 50 hp.) | Pending |  | Is the fan/blower a designed high-pressure blower (design capacity <= 150 cfm/hp)? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet (or make and model) to determine the type of fan/blower being used | The fan/blower must not be a 'high-pressure blower' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 82
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any | QA Checklist | 26 | This measure cannot be used for the following fan applications: • HVAC fan • An individual fan motor rated less than 10 hp or higher than 150 hp • A two-speed fan motor • A fan motor with an existing VSD | Pending |  | Is this measure for an HVAC fan? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | QA Checklist | Use photographs of the equipment the fan is serving | The equipment should not be HVAC related | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 32
0 | SWPR007 | 1 | Steam Boiler Economizer, Industrial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Steam boiler manufacturer | Text Box | [8 empty] | Inspections | Photograph the Steam Boiler nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the Steam Boiler manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | Update property label to 'Steam boiler manufacturer' | 2021-09-17 | Kenny Liljestrom |  |  | 25
0 | SWPR007 | 1 | Steam Boiler Economizer, Industrial | Any | Any | Any | EECP | 2 | - | Yes | Model | Steam boiler model | Text Box | [8 empty] | Inspections | Photograph the Steam Boiler nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the Steam Boiler model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | Update property label to 'Steam boiler model' | 2021-09-17 | Kenny Liljestrom |  |  | 18
0 | SWPR007 | 1 | Steam Boiler Economizer, Industrial | Any | Any | Any | EECP | 3 | This measure is applicable to steam boilers only. The steam boiler must have an input rating ≤ 20 million Btu/hr. Hot water boilers are not eligible. | Pending |  | Steam boiler input rating (MMBtu/hr) | Numeric Value | [7 empty] | Must be <= 20 | Inspections | Photograph the steam boiler nameplate to capture the make, model, and input rating (MMBtu/hr) | The input rating (MMBtu/hr) must be <= 20 and match what is listed in EECP | QA Checklist | Use the installation report or photographs which show the steam boiler input rating | The steam boiler input rating must be <= 20 MMBtu/hr If the units on the nameplate are listed in Btu/hr, divide the number by 1,000,000 to convert to MMBtu/hr |  | 2021-09-17 | Kenny Liljestrom |  |  | 36
0 | SWPR007 | 1 | Steam Boiler Economizer, Industrial | Any | Any | Any | EECP | 4 | The boiler manufacturer, model, and spec sheet should be submitted for verification. | Pending |  | Steam boiler spec sheet submitted? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Review the documentation in EECP to determine if the boiler spec sheet was submitted | A spec sheet for the boiler must be submitted with the project files in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-17 | Kenny Liljestrom |  |  | 34
0 | SWPR007 | 1 | Steam Boiler Economizer, Industrial | Any | Any | Any | EECP | 5 | For a dual-stage economizer: • The disposal of combustion condensate must meet local codes regarding sanitary drain or storm sewer. • Some applications may require a neutralizer for the acidic combustion condensate. | Pending |  | Dual stage economizer: condensate meets sanitary and acidic neutralization of combustion codes? | Drop Down List | Yes;No;N/A; | [6 empty] | Must be 'Yes' or 'N/A' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-09-17 | Kenny Liljestrom |  |  | 95
0 | SWPR007 | 1 | Steam Boiler Economizer, Industrial | Any | Any | Any | EECP | 6 | - | Pending |  | Economizer manufacturer | Text Box | [8 empty] | Inspections | If accessible, photograph the economizer nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the economizer manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-17 | Kenny Liljestrom |  |  | 23
0 | SWPR007 | 1 | Steam Boiler Economizer, Industrial | Any | Any | Any | EECP | 7 | - | Pending |  | Economizer model | Text Box | [8 empty] | Inspections | If accessible, photograph the economizer nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the economizer model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-17 | Kenny Liljestrom |  |  | 16
0 | SWPR007 | 1 | Steam Boiler Economizer, Industrial | Any | Any | Any | EECP | 8 | There are no boiler efficiency eligibility requirements for the measure, for both single stage and two stage economizers. The efficiency gains were averaged from past custom projects and meeting these efficiencies (estimated improvement at 2% and 8% for single and dual stage economizer, respectively) is not a requirement for rebate. Good to have | Pending |  | Economizer efficiency / effectiveness (%) | Numeric Value | [8 empty] | QA Checklist | Use the make and model for the economizer (or spec sheet if submitted) to validate the economizer efficiency | There are no validation criteria for this property; the value should match between EECP and the spec sheet (if not easily available, this property can be ignored) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-17 | Kenny Liljestrom |  |  | 41
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted spec sheet or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the spec sheet or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-09 | Kenny Liljestrom |  | Add | 12
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted spec sheet or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the spec sheet or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-09 | Kenny Liljestrom |  | Add | 5
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any | EECP | 3 | Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Natural Gas Heated | Is the pool heated with natural gas? | Drop Down List | Yes;No | [6 empty] | Must be Yes | Inspections | Locate the water heater for the pool; photograph the nameplate of the pool water heater to capture the make, model, and input rating (Btu/hr) | The nameplate should indicate the input rating in Btu/hr or the unit should be easily identifiable as a gas fired unit; the pool water heater must be gas fired to qualify | QA Checklist | Use photographs or the installation report for the pool water heater to determine the fuel type (electric or gas) | The pool water heater must be fueled by natural gas to qualify |  | 2021-07-09 | Kenny Liljestrom |  | Add | 36
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any | EECP | 4 | Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Pool Area SF | What is area in square footage of the pool area | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Is this property the same as the quantity field? | 2021-07-09 | Kenny Liljestrom |  | Add | 47
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any | EECP | 5 | Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | R Value | R value (ft2-hr-F/Btu) | Numeric Value | [7 empty] | Must be >= 0.5 | QA Checklist | Use the manufacturer spec sheet to validate the R value (ft2-hr-F/Btu) is listed | The R value must be >= 0.5 ft2-hr-F/Btu | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-09 | Kenny Liljestrom |  | Add | 22
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any | EECP | 6 | This measure applies to outdoor and indoor heated swimming pools that do not already have pool cover. Energy efficiency programs are to target pools without existing pool covers. | Yes | Existing Pool Cover | Is there an existing pool cover in use? | Drop Down List | Yes;No | [6 empty] | Must be No | Inspections | During the site pre-inspection, determine if an existing cover is in use or if there are signs a pool cover was in use | An existing pool cover must not be in use to qualify for this measure | QA Checklist | The implementer should provide proof that an existing pool cover is not in use via photographs of the pool area and equipment storage locations | An existing pool cover must not be in use to qualify for this measure |  | 2021-07-09 | Kenny Liljestrom |  | Add | 39
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any | EECP | 7 | Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Pool Cover Requirements | Does the installed cover have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard)? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Use the manufacturer spec sheet to validate thickness, material, and thermal conductivity is listed | The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-09 | Kenny Liljestrom |  | Add | 174
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any | EECP | 8 | Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Pool Cover Size | How much of the pool does the new pool cover encompass? (%) | Numeric Value | [7 empty] | Must be >= 95% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-07-09 | Kenny Liljestrom |  | Add | 59
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any | EECP | 9 | Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Olympic Size_Storage Reel System | If the pool is Olympic sized, is there a storage reel system? | Drop Down List | N/A;Yes;No | [6 empty] | Must be 'Yes' or 'N/A' | Inspections | If the pool is Olympic sized (50 meters in length) determine if there is a storage reel system installed | Storage reels are required for Olympic sized pools to qualify | QA Checklist | If the pool is Olympic sized (50 meters in length) determine if there is a storage reel system installed via an installation report or photographs | Storage reels are required for Olympic sized pools to qualify | Update property values ("N/A") and add validation criteria | 2021-07-09 | Kenny Liljestrom |  | Add | 61
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any | EECP | 10 | Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Pool Cover Warranty | Does the pool cover come with a minimum 5 year warranty? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Use the manufacturer spec sheet or extended warranty documentation (if applicable) to determine if there is a minimum 5-year warranty on the pool cover | Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies) is required at enrollment | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update validation criteria | 2021-07-09 | Kenny Liljestrom |  | Add | 56
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any | QA Checklist | 11 | The primary target building types for this measure are existing schools/colleges (educational institutions), city (municipal) recreational centers, home owner associations (e.g., condominiums with common pools), private/health clubs, and multifamily residences (apartment buildings). | Yes |  | Is the primary target building type for this measure an existing schools/colleges (educational institutions), city (municipal) recreational centers, home owner associations (e.g., condominiums with common pools), private/health clubs, and multifamily residences (apartment buildings)? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | Review the submitted documentation in EECP to determine the building type where the cover is being installed | The primary target building types for this measure are existing schools/colleges (educational institutions), city (municipal) recreational centers, home owner associations (e.g., condominiums with common pools), private/health clubs, and multifamily residences (apartment buildings). | - | - | - |  | 2021-07-12 | Kenny Liljestrom |  | Add | 284
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any | QA Checklist | 12 | New construction installations are not eligible. | Yes |  | New Construction | Drop Down List | Yes;No; | [6 empty] | Must be No | QA Checklist | Review the submitted documentation in EECP to determine the building vintage (Existing or New Construction) | New construction projects do not qualify for a rebate | - | - | - |  | 2021-07-12 | Kenny Liljestrom |  | Add | 16
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate of the pump to capture the manufacturer | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate of the pump to capture the model number | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any | EECP | 3 | Only main filtration pumps are eligible. | Yes | Installed on Main Pump | Was the measure installed on a main filtration pump? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Photograph the pool pumping system (all pumps visible), check to see if there are multiple VSD pumps running at one time or only one | There should only be a single VSD pump operating at a time | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 52
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any | EECP | 4 | Only one-for-one pump replacements are eligible. | Yes | Replacement | Is the measure a one-for-one pump replacement? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 46
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any | EECP | 5 | Both base case and measure case pool pumps must be between 1 hp and 3 hp, with horsepower referring to the (rated) nameplate horsepower before service factor is applied. | Yes | Size | base case and measure case pool pumps? (hp) | Numeric Value | [7 empty] | Must be >= 1 and <=3 | Inspections | Photograph the pump nameplate to capture the motor horsepower | The horsepower should match what is listed in EECP and be between 1 and 3hp | QA Checklist | Use the submitted invoice or installation report to show the existing and proposed conditions for the motor power (hp); or a manufacturer specification sheet showing the motor power (hp) | The motor power (hp) listed in EECP should match the installation report or spec sheet and must be >= 1 and <= 3 |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any | EECP | 6 | The variable speed drive (VSD) pump must replace an existing single- or two-speed pool pump and meet base case and measure case requirements, as specified in the Base Case Description and Measure Case Description, respectively. | Yes | VSD Replace | Did the installed variable speed drive (VSD) pump replace an existing single- or two-speed pool pump? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 101
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any | EECP | 7 | Nominal capacity of the new VSD pump should match the capacity of the pump being replaced (recommended). | Yes | VSD Capacity Match | Does the nominal capacity of the new VSD pump match the capacity of the pump being replaced? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 92
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any | EECP | 8 | The VSD pump must be configured to meet program pump configuration requirements. | Yes | VSD Configuration | Was the VSD pump configured to meet program pump configuration requirements? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 76
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any | EECP | 9 | For models that require an automatic control system capable of controlling both high and low speeds, a controller must be installed. | Yes | Controller Installed | For models that require an automatic control system capable of controlling both high and low speeds, was a controller installed? | Drop Down List | Yes;No;N/A | [6 empty] | Must be 'Yes' or 'N/A' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 128
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any | EECP | 10 | Measure implementation must be completed with both the customer and the installation contractor acknowledgement of energy savings settings. | Yes | Customer_Contractor | Did both the customer and the installation contractor acknowledge the energy savings setting of the installed measure? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 118
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any | EECP | 11 | The installation contractor shall follow all manufacturer installation requirements and comply with all applicable regulations. The installation shall meet all applicable standards and regulations including (but not limited to) NEC and the California Title 24 and Title 20 regulations (see Code Requirements). | Yes | Contractor Instructions | Did the installation contractor follow all manufacturer installation requirements and comply with all applicable standards and regulations including (but not limited to) NEC and the California Title 24 and Title 20 regulations (see Code Requirements).? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 252
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any | EECP | 13 | Pumps being replaced must be disposed of rather than refurbished and sold. | Yes | Disposal | Was the pump being replaced disposed of rather than refurbished and/or sold? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 76
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any | EECP | 14 | Equipment and materials must meet or exceed all applicable local, state and federal standards. | Yes | Equipment Standards | Did equipment and materials meet or exceed all applicable local, state and federal standards? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 93
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any | EECP | 15 | The installation must be completed by a utility-approved contractor or a contractor with the appropriate license and training. All direct installation with downstream delivery installations must be completed by a utility-approved contractor. Utility-approved contractors will complete both technical and program-related training to ensure proper installation. Each approved contractor will be trained such that they can properly collect and submit the correct (and corresponding) information for both accelerated replacement (AR) and normal replacement (NR) measures. | Yes | Approved Contractor | Was the installation of the measure completed by a utility-approved contractor? | Drop Down List | Yes;No | [6 empty] | If No - enable "Self-Install" | QA Checklist | Check the contractor listed as performing the work against the trade professional database | The contractor who performed the installation should be listed in the trade pro database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 79
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | B | Any | Any | EECP | 16 | Self-Installed Measures: Measure B shall be specified on applications for which the client installs their own variable speed pump, or if no certified contractor is used to install the equipment. | No |  | Only eligible for Single Family Homes, did the customer perform self-installation of the new pump? | Drop Down List | Yes;No | [6 empty] | Enable if Approved Contractor is 'No' Must be 'Yes' | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 98
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any | EECP | 17 | The variable speed pool pump or motor must be a new | Yes | New Equipment | Was the installed equipment new? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Contractor should provide evidence of proof of purchase or invoice showing the purchase date of the pump | The invoice should list the pump as being new or not used in the description | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 32
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any | EECP | 18 | Program Exclusions: New parts installed in existing units and Motor-only replacements | No |  | Was the equipment fully replaced (i.e. not a part swap or motor only replacement)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 82
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | AR | Any | EECP | 19 | For accelerated replacement application types, the customer must be approached by a direct install implementer. | No |  | Was the customer approached directly by a direct installation implementer? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 74
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | AR | Any | EECP | 20 | Preponderance of evidence (POE) will be assessed at the program-level based on the direction outlined in the “Accelerated Replacement Using Preponderance of Evidence” of the T1 Working Group Report prepared for the California Public Utilities Commission (CPUC). Additional information and documentation to ensure conformance to eligibility and implementation requirements, include (but are not limited to) the following: Customer/site information Existing equipment Replacement equipment Permits and associated documentation Pump commissioning information | No |  | Has all Preponderance of Evidence (POE) been presented including: Customer site information, Make/model of pre-existing equipment, Make/model of replacement equipment, Permits and associated documentation, and Pump commissioning information? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 242
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | AR | Any | EECP | 21 | Risk mitigation | No |  | Who was the party that filled out the POE documentation? | Drop Down List | Customer;Customer Representative;Program Advisor;Implementer; | [6 empty] | Must be 'Yes' | - | - | - | - | - | - | Not configured in original upload | 2021-10-20 | Kenny Liljestrom | Implementers responsible for POE documentation | Add | 56
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | AR | Any | EECP | 22 | All accelerated replacement measures require third-party baseline verification and data gathering in full compliance with the established POE requirements. | No |  | Was third-party baseline verification and data gathering in full compliance with the established POE requirements performed? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 124
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | A | Any | Any | EECP | 23 | Program Exclusions: Pool Pumps installed in a spa or jacuzzi at a single-family residence. | No |  | Was a pool pump installed in a spa or jacuzzi? | Drop Down List | Yes;No | [6 empty] | Must be No | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 46
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | B | Any | Any | EECP | 24 | Program Exclusions: Pool Pumps installed in a spa or jacuzzi at a single-family residence. | No |  | Was a pool pump installed in a spa or jacuzzi? | Drop Down List | Yes;No | [6 empty] | Must be No | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 46
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | C | Any | Any | EECP | 25 | Program Exclusions: Pool Pumps installed in a spa or jacuzzi at a single-family residence. | No |  | Was a pool pump installed in a spa or jacuzzi? | Drop Down List | Yes;No | [6 empty] | Must be No | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 46
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | H | Any | Any | EECP | 26 | Program Exclusions: Pool Pumps installed in a spa or jacuzzi at a single-family residence. | No |  | Was a pool pump installed in a spa or jacuzzi? | Drop Down List | Yes;No | [6 empty] | Must be No | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 46
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | I | Any | Any | EECP | 27 | Program Exclusions: Pool Pumps installed in a spa or jacuzzi at a single-family residence. | No |  | Was a pool pump installed in a spa or jacuzzi? | Drop Down List | Yes;No | [6 empty] | Must be No | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 46
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | A | Any | Any | EECP | 28 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | B | Any | Any | EECP | 29 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | C | Any | Any | EECP | 30 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any | EECP | 31 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any | EECP | 32 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any | EECP | 33 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any | EECP | 34 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any | EECP | 35 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any | EECP | 36 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | A | Any | Any | EECP | 37 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [6 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | B | Any | Any | EECP | 38 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [6 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | C | Any | Any | EECP | 39 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [6 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any | EECP | 40 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [6 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any | EECP | 41 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [6 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any | EECP | 42 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [6 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any | EECP | 43 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [6 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any | EECP | 44 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [6 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any | EECP | 45 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [6 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | A | Any | Any | EECP | 46 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | B | Any | Any | EECP | 47 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | C | Any | Any | EECP | 48 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any | EECP | 49 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any | EECP | 50 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any | EECP | 51 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any | EECP | 52 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any | EECP | 53 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any | EECP | 54 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | A | Any | Any | EECP | 55 | Only one variable-speed pool pump and motor rebate per residence. | No |  | Has only one variable-speed pool pump and motor been installed at the residence? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 80
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | B | Any | Any | EECP | 56 | Only one variable-speed pool pump and motor rebate per residence. | No |  | Has only one variable-speed pool pump and motor been installed at the residence? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 80
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | C | Any | Any | EECP | 57 | Only one variable-speed pool pump and motor rebate per residence. | No |  | Has only one variable-speed pool pump and motor been installed at the residence? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 80
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | A | Any | Any | EECP | 58 | Filtration settings must be configured to operate outside peak hours, as defined by the utility. | No |  | Have the filtration settings been configured to operate outside peak hours, as defined by the utility? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 102
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | B | Any | Any | EECP | 59 | Filtration settings must be configured to operate outside peak hours, as defined by the utility. | No |  | Have the filtration settings been configured to operate outside peak hours, as defined by the utility? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 102
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | C | Any | Any | EECP | 60 | Filtration settings must be configured to operate outside peak hours, as defined by the utility. | No |  | Have the filtration settings been configured to operate outside peak hours, as defined by the utility? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 102
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | A | Any | Any | EECP | 61 | • Customers must acknowledge and confirm operation on application form in order to be eligible for rebate. | No |  | Has the customer confirmed the operation of the replacement equipment on the application form? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 94
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | B | Any | Any | EECP | 62 | • Customers must acknowledge and confirm operation on application form in order to be eligible for rebate. | No |  | Has the customer confirmed the operation of the replacement equipment on the application form? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 94
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | C | Any | Any | EECP | 63 | • Customers must acknowledge and confirm operation on application form in order to be eligible for rebate. | No |  | Has the customer confirmed the operation of the replacement equipment on the application form? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 94
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any | EECP | 64 | Only one rebate is allowed per spa OR wading pool pump. | No |  | Has only one rebate been applied per spa or wading pool? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 56
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any | EECP | 65 | Only one rebate is allowed per spa OR wading pool pump. | No |  | Has only one rebate been applied per spa or wading pool? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 56
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any | EECP | 66 | Only one rebate is allowed per spa OR wading pool pump. | No |  | Has only one rebate been applied per spa or wading pool? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 56
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any | EECP | 67 | Only one rebate is allowed per spa OR wading pool pump. | No |  | Has only one rebate been applied per spa or wading pool? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 56
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any | EECP | 68 | A maximum of three rebates are allowed per customer property/site for main filtration pump(s). Incentive applications for more than one main filtration pump require supporting documentation verifying existing condition per Authority Having Jurisdiction. | No |  | Has the customer received less than or equal to the three maximum rebates per property/site for the main filtration pumps (includes pools, spas, and wading pools)? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 163
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any | EECP | 69 | A maximum of three rebates are allowed per customer property/site for main filtration pump(s). Incentive applications for more than one main filtration pump require supporting documentation verifying existing condition per Authority Having Jurisdiction. | No |  | Has the customer received less than or equal to the three maximum rebates per property/site for the main filtration pumps (includes pools, spas, and wading pools)? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 163
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any | EECP | 70 | A maximum of three rebates are allowed per customer property/site for main filtration pump(s). Incentive applications for more than one main filtration pump require supporting documentation verifying existing condition per Authority Having Jurisdiction. | No |  | Has the customer received less than or equal to the three maximum rebates per property/site for the main filtration pumps (includes pools, spas, and wading pools)? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 163
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any | EECP | 71 | A maximum of three rebates are allowed per customer property/site for main filtration pump(s). Incentive applications for more than one main filtration pump require supporting documentation verifying existing condition per Authority Having Jurisdiction. | No |  | Has the customer received less than or equal to the three maximum rebates per property/site for the main filtration pumps (includes pools, spas, and wading pools)? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 163
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any | EECP | 72 | A maximum of three rebates are allowed per customer property/site for main filtration pump(s). Incentive applications for more than one main filtration pump require supporting documentation verifying existing condition per Authority Having Jurisdiction. | No |  | Has the customer received less than or equal to the three maximum rebates per property/site for the main filtration pumps (includes pools, spas, and wading pools)? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 163
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any | EECP | 73 | A maximum of three rebates are allowed per customer property/site for main filtration pump(s). Incentive applications for more than one main filtration pump require supporting documentation verifying existing condition per Authority Having Jurisdiction. | No |  | Has the customer received less than or equal to the three maximum rebates per property/site for the main filtration pumps (includes pools, spas, and wading pools)? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 163
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any | EECP | 74 | During pool operating hours, the VSD setting must be “right sized” to meet turn-over requirements as specified by the 2019 Title 24 standards, Chapter 31B “Public Swimming Pools,” Section 3124B. (See Code Requirements). | Yes | VSD Setting | During pool operating hours, was the VSD setting “right sized”? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 63
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any | EECP | 75 | During pool operating hours, the VSD setting must be “right sized” to meet turn-over requirements as specified by the 2019 Title 24 standards, Chapter 31B “Public Swimming Pools,” Section 3124B. (See Code Requirements). | Yes | VSD Setting | During pool operating hours, was the VSD setting “right sized”? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 63
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any | EECP | 76 | During pool operating hours, the VSD setting must be “right sized” to meet turn-over requirements as specified by the 2019 Title 24 standards, Chapter 31B “Public Swimming Pools,” Section 3124B. (See Code Requirements). | Yes | VSD Setting | During pool operating hours, was the VSD setting “right sized”? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 63
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any | EECP | 77 | During pool operating hours, the VSD setting must be “right sized” to meet turn-over requirements as specified by the 2019 Title 24 standards, Chapter 31B “Public Swimming Pools,” Section 3124B. (See Code Requirements). | Yes | VSD Setting | During pool operating hours, was the VSD setting “right sized”? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 63
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any | EECP | 78 | During pool operating hours, the VSD setting must be “right sized” to meet turn-over requirements as specified by the 2019 Title 24 standards, Chapter 31B “Public Swimming Pools,” Section 3124B. (See Code Requirements). | Yes | VSD Setting | During pool operating hours, was the VSD setting “right sized”? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 63
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any | EECP | 79 | During pool operating hours, the VSD setting must be “right sized” to meet turn-over requirements as specified by the 2019 Title 24 standards, Chapter 31B “Public Swimming Pools,” Section 3124B. (See Code Requirements). | Yes | VSD Setting | During pool operating hours, was the VSD setting “right sized”? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 63
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | H | Any | Any | EECP | 80 | During Pool Operating Hours: Variable speed drive setting must be “right sized” to meet turnover requirements as specified by California Code of Regulations, Title 24, Building Standards Code (2016): Chapter 31B “Public Swimming Pools,” Section 3124B. | Yes | VSD Setting | During pool operating hours, was the VSD setting “right sized”? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 63
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | I | Any | Any | EECP | 81 | During Pool Operating Hours: Variable speed drive setting must be “right sized” to meet turnover requirements as specified by California Code of Regulations, Title 24, Building Standards Code (2016): Chapter 31B “Public Swimming Pools,” Section 3124B. | Yes | VSD Setting | During pool operating hours, was the VSD setting “right sized”? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 63
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any | EECP | 82 | During pool non-operating hours, the VSD setting must be configured to at least 50% of full-speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting | VSD setting percentage during non-operating hours | Numeric Value | [7 empty] | Must be <=50% | Inspections | Photograph the motor display panel showing the scheduled operating conditions for the pool pump | The setting must be less than or equal to 50% speed during nighttime hours | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any | EECP | 83 | During pool non-operating hours, the VSD setting must be configured to at least 50% of full-speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting | VSD setting percentage during non-operating hours | Numeric Value | [7 empty] | Must be <=50% | Inspections | Photograph the motor display panel showing the scheduled operating conditions for the pool pump | The setting must be less than or equal to 50% speed during nighttime hours | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any | EECP | 84 | During pool non-operating hours, the VSD setting must be configured to at least 50% of full-speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting | VSD setting percentage during non-operating hours | Numeric Value | [7 empty] | Must be <=50% | Inspections | Photograph the motor display panel showing the scheduled operating conditions for the pool pump | The setting must be less than or equal to 50% speed during nighttime hours | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any | EECP | 85 | During pool non-operating hours, the VSD setting must be configured to at least 50% of full-speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting | VSD setting percentage during non-operating hours | Numeric Value | [7 empty] | Must be <=50% | Inspections | Photograph the motor display panel showing the scheduled operating conditions for the pool pump | The setting must be less than or equal to 50% speed during nighttime hours | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any | EECP | 86 | During pool non-operating hours, the VSD setting must be configured to at least 50% of full-speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting | VSD setting percentage during non-operating hours | Numeric Value | [7 empty] | Must be <=50% | Inspections | Photograph the motor display panel showing the scheduled operating conditions for the pool pump | The setting must be less than or equal to 50% speed during nighttime hours | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any | EECP | 87 | During pool non-operating hours, the VSD setting must be configured to at least 50% of full-speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting | VSD setting percentage during non-operating hours | Numeric Value | [7 empty] | Must be <=50% | Inspections | Photograph the motor display panel showing the scheduled operating conditions for the pool pump | The setting must be less than or equal to 50% speed during nighttime hours | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | H | Any | Any | EECP | 88 | During Pool Non-Operating Hours: Variable speed drive setting must be configured to at least 50% of full speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting | VSD setting percentage during non-operating hours | Numeric Value | [7 empty] | Must be <=50% | Inspections | Photograph the motor display panel showing the scheduled operating conditions for the pool pump | The setting must be less than or equal to 50% speed during nighttime hours | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | I | Any | Any | EECP | 89 | During Pool Non-Operating Hours: Variable speed drive setting must be configured to at least 50% of full speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting | VSD setting percentage during non-operating hours | Numeric Value | [7 empty] | Must be <=50% | Inspections | Photograph the motor display panel showing the scheduled operating conditions for the pool pump | The setting must be less than or equal to 50% speed during nighttime hours | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any | EECP | 90 | Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit | Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | Drop Down List | Yes;No;N/A | [6 empty] | Must be Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 134
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any | EECP | 91 | Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit | Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | Drop Down List | Yes;No;N/A | [6 empty] | Must be Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 134
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any | EECP | 92 | Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit | Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | Drop Down List | Yes;No;N/A | [6 empty] | Must be Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 134
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any | EECP | 93 | Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit | Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | Drop Down List | Yes;No;N/A | [6 empty] | Must be Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 134
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any | EECP | 94 | Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit | Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | Drop Down List | Yes;No;N/A | [6 empty] | Must be Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 134
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any | EECP | 95 | Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit | Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | Drop Down List | Yes;No;N/A | [6 empty] | Must be Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 134
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | H | Any | Any | EECP | 96 | Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit | Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | Drop Down List | Yes;No;N/A | [6 empty] | Must be Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 134
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | I | Any | Any | EECP | 97 | Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit | Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | Drop Down List | Yes;No;N/A | [6 empty] | Must be Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 134
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any | EECP | 98 | Health code requirements and inspections must be passed successfully. | Yes | Health Inspection | Were all health code requirements and inspections passed successfully? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 70
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any | EECP | 99 | Health code requirements and inspections must be passed successfully. | Yes | Health Inspection | Were all health code requirements and inspections passed successfully? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 70
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any | EECP | 100 | Health code requirements and inspections must be passed successfully. | Yes | Health Inspection | Were all health code requirements and inspections passed successfully? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 70
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any | EECP | 101 | Health code requirements and inspections must be passed successfully. | Yes | Health Inspection | Were all health code requirements and inspections passed successfully? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 70
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any | EECP | 102 | Health code requirements and inspections must be passed successfully. | Yes | Health Inspection | Were all health code requirements and inspections passed successfully? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 70
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any | EECP | 103 | Health code requirements and inspections must be passed successfully. | Yes | Health Inspection | Were all health code requirements and inspections passed successfully? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 70
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | H | Any | Any | EECP | 104 | Health code requirements and inspections must be passed successfully. | Yes | Health Inspection | Were all health code requirements and inspections passed successfully? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 70
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | I | Any | Any | EECP | 105 | Health code requirements and inspections must be passed successfully. | Yes | Health Inspection | Were all health code requirements and inspections passed successfully? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 70
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any | EECP | 106 | EH&S Department approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved | Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any | EECP | 107 | EH&S Department approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved | Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any | EECP | 108 | EH&S Department approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved | Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any | EECP | 109 | EH&S Department approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved | Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any | EECP | 110 | EH&S Department approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved | Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any | EECP | 111 | EH&S Department approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved | Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | H | Any | Any | EECP | 112 | EH&S approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved | Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | I | Any | Any | EECP | 113 | EH&S Department approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved | Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | H | Any | Any | EECP | 114 | The customer, as part of the incentive application process shall acknowledge that the replacement pool pump VSD has been configured to achieve energy savings and agreed to have the pump filtration settings programmed for reduced flow during pool non-operating hours. | No |  | Has the customer, as part of the incentive application process, acknowledged that the replacement pool pump VSD has been configured to achieve energy savings and agreed to have the pump filtration settings programmed for reduced flow during pool non-operating hours? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-05-28 | Kenny Liljestrom | Removed, trust on part of implementer to inform customer of savings for measure. Also no way to verify | Add | 266
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | I | Any | Any | EECP | 115 | The customer, as part of the incentive application process shall acknowledge that the replacement pool pump VSD has been configured to achieve energy savings and agreed to have the pump filtration settings programmed for reduced flow during pool non-operating hours. | No |  | Has the customer, as part of the incentive application process, acknowledged that the replacement pool pump VSD has been configured to achieve energy savings and agreed to have the pump filtration settings programmed for reduced flow during pool non-operating hours? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-05-28 | Kenny Liljestrom | Removed, trust on part of implementer to inform customer of savings for measure. Also no way to verify | Add | 266
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | H | Any | Any | EECP | 116 | The customer shall agree not to modify and/or alter in any way programmed settings on the pump VSD to ensure persistence of the measure savings. | No |  | Has the customer agreed not to modify and/or alter, in any way, programmed settings on the pump VSD to ensure persistence of the measure savings? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-05-28 | Kenny Liljestrom | Removed, trust on part of implementer to inform customer of savings for measure. Also no way to verify | Add | 145
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | I | Any | Any | EECP | 117 | The customer shall agree not to modify and/or alter in any way programmed settings on the pump VSD to ensure persistence of the measure savings. | No |  | Has the customer agreed not to modify and/or alter, in any way, programmed settings on the pump VSD to ensure persistence of the measure savings? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-05-28 | Kenny Liljestrom | Removed, trust on part of implementer to inform customer of savings for measure. Also no way to verify | Add | 145
1 | SWRE003 | 1 | Heater for Pool or Spa, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-12 | Kenny Liljestrom |  | Add | 12
1 | SWRE003 | 1 | Heater for Pool or Spa, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-12 | Kenny Liljestrom |  | Add | 5
1 | SWRE003 | 1 | Heater for Pool or Spa, Commercial | Any | Any | Any | EECP | 3 | This measure is available for swimming pool heating and the unit must replace pre-existing pool heater. | Yes | Existing Heater | Did the installed heater replace an existing pool heater? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Review the submitted documentation in EECP (either photographs or an installation report) to determine if there is an existing pool heater installed | The implementer needs to provide proof there is an existing heater on site | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 57
1 | SWRE003 | 1 | Heater for Pool or Spa, Commercial | Any | Any | Any | EECP | 4 | The commercial pool heater must be certified to meet the following requirements: • The heater must have TE ≥ 84% • The heater must have an ON/OFF switch and no pilot light | Yes | EFFICIENCY | Thermal efficiency of installed heater (%) | Numeric Value | [7 empty] | Must be > 84% | Inspections | Photograph the nameplate showing the efficiency (%) of the unit | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 84% | QA Checklist | Use the manufacturer spec sheet to validate the equipment efficiency (%) | The efficiency listed in EECP should match what is listed in the spec sheet; the efficiency needs to be > 84% |  | 2021-07-12 | Kenny Liljestrom |  | Add | 42
1 | SWRE003 | 1 | Heater for Pool or Spa, Commercial | Any | Any | Any | EECP | 5 | The commercial pool heater must be certified to meet the following requirements: • The heater must have TE ≥ 84% • The heater must have an ON/OFF switch and no pilot light | Yes | ON_OFF Switch | Does the installed heater have an ON/OFF switch and no pilot light? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Use the manufacturer spec sheet to determine if the unit has an On/Off switch and no pilot light | The heater must be an On/Off type heater with no pilot light | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 67
1 | SWRE003 | 1 | Heater for Pool or Spa, Commercial | Any | Any | Any | QA Checklist | 6 | This measure is applicable to all heated pools installed in commercial facilities, such as schools, colleges, universities, YMCA/YWCA, public facilities, hotels/motels, health clubs, and spas. This measure is also applicable for multifamily properties, such as homeowner associations and other multifamily complexes. | Yes |  | Is the building type: commercial facilities, such as schools, colleges, universities, YMCA/YWCA, public facilities, hotels/motels, health clubs, and spas. This measure is also applicable for multifamily properties, such as homeowner associations and other multifamily complexes? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Review the documentation in EECP to determine the building type | The building type must be one of the following: commercial facilities, such as schools, colleges, universities, YMCA/YWCA, public facilities, hotels/motels, health clubs, and spas. This measure is also applicable for multifamily properties, such as homeowner associations and other multifamily complexes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-12 | Kenny Liljestrom |  | Add | 278
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | An installation report should indicate the work performed and show Duct Seal and testing specifications for the HVAC system including existing and proposed leakage rates | The manufacturer may be listed as the implementer or contractor who performed the work or the product used to perform the sealing | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | An installation report should indicate the work performed and show Duct Seal and testing specifications for the HVAC system including existing and proposed leakage rates | The model number may be listed as the implementer or contractor who performed the work or the product used to perform the sealing | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any | EECP | 3 | This measure is applicable for any existing single family, multifamily with two or more units, or mobile home that uses air-cooled, direct expansion (DX) cooling and gas heating, heat pump, or gas heating with no cooling. | Yes |  | What type of HVAC system does the customer have? | Drop Down List | Air-cooled direct expansion (DX) cooling and gas heating;Heat pump;Gas heating with no cooling;Other; | [6 empty] | Must not be 'Other' | QA Checklist | An installation report should indicate the type of HVAC system the customer has | HVAC system type should match EECP and be one of the following: Air-cooled direct expansion (DX) cooling and gas heating, Heat pump, or Gas heating with no cooling | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 48
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any | EECP | 4 | Up to two duct tests must be conducted: the first or “test-in” is a system check to determine whether the duct system tightness meets the California Title 24 specifications. | Yes |  | Test-in Duct Leakage Rate (%) | Numeric Value | [8 empty] | QA Checklist | An installation report should indicate the test-in leakage rate | the test-in leakage rate should be greater than or equal to the measure case leakage rate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 29
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any | EECP | 5 | If the Test-in shows that duct leakage exceeds minimum tightness specifications, and the technicians correct the situation, then a second test or “test-out” must be conducted to verify proper duct tightness was achieved. | Yes |  | Test-out Duct Leakage Rate (%) | Numeric Value | [8 empty] | QA Checklist | An installation report should indicate the test-out leakage rate | the test-out leakage rate should be less than or equal to the measure case leakage rate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 30
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any | EECP | 6 | If some or all of the existing ductwork is beyond repair and sections must be replaced, the sections that must be replaced must be less than 40 linear feet in total per Section 150.2(b) of the 2019 California Building Energy Efficiency Standards (Title 24) | Yes |  | Length of ductwork replaced (linear feet) | Numeric Value | [8 empty] | Inspections | Photograph of the ductwork showing repairs or replacements in the ducting system | Using your best judgement, determine if more than 40-linear feet of duct work was added or replaced as part of the project; the replacement ductwork must be < 40-feet to be eligible | QA Checklist | An installation report should indicate, if any, the length of the duct work replaced as part of the project | If some or all of the existing ductwork is beyond repair and sections must be replaced, the sections that must be replaced must be less than 40 linear feet in total per Section 150.2(b) of the 2019 California Building Energy Efficiency Standards (Title 24) | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 41
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any | EECP | 7 | ...or the replaced ductwork must be installed and tested in accordance with the applicable requirements in 2019 Title 24 Section 150.2(b)1D | Yes |  | Ductwork length > 40-ft been installed and tested in accordance to 2019 Title 24 Section 150.2(b)1D? | Drop Down List | Yes;No;N/A; | [6 empty] | Must be 'Yes' or 'N/A' | QA Checklist | If the length of ductwork replaced is greater than 40-linear feet, the implementer should supply the Title-24 compliance sheets as part of the documentation | Photograph of the ductwork showing repairs or replacements in the ducting system | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 100
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any | EECP | 8 | To identify these measures as part of an existing HVAC system, the program implementer must record existing duct leakage through comprehensive field testing. The testing can be performed while the system is pressurized using a duct blower fan to ensure the target leakage thresholds are achieved. Duct sealing shall be performed on the unpressurized system. After installation, testing shall be performed to ensure the target leakage thresholds are achieved. Photos and test results can serve as documentation that the work was performed on an existing HVAC system. | Yes |  | Has photographic evidence or documentation of the test-in and test-out procedures been uploaded? | Drop Down List | Yes;No; | [6 empty] | Must be ''Yes' | QA Checklist | Review the submitted documentation in EECP to look for photographic evidence or documentation of the test-in and test-out procedures | An installation report with photographs of the test-in and test-out leakage rates should be included in the submitted documentation | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 96
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any | EECP | 9 | Programs often bundle Quality Maintenance (QM) measures. The following prerequisites must be met before the QM treatments, such as airflow adjustments, can be implemented to ensure an HVAC system is running optimally. | Yes |  | Additional QM measures (i.e. airflow adjustments) being installed in conjunction with this measure? | Drop Down List | Yes;No; | [7 empty] | QA Checklist | If implementer answers 'Yes', check the measures installed as part of the enrollment and via double-dip report | If the implementer answers yes to this question, they must meet the following criteria to be eligible | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 99
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any | EECP | 10 | • The unit must be drawing power. | Yes |  | Is the unit drawing power? | Drop Down List | Yes;No; | [6 empty] | If 'QM Eligibility' is Yes then Must be ''Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, review the submitted documentation in EECP | Ensure the installation report shows the HVAC system as being functional prior to any work being performed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 26
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any | EECP | 11 | • The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted. | Yes |  | Refrigerant charge adjustments, unit has been tested to deliver supply air of at least 350 cfm/ton? | Drop Down List | Yes;No;N/A; | [6 empty] | If 'QM Eligibility' is Yes then Refrigerant Check must be 'Yes' or 'N/A' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, review the submitted documentation in EECP | Ensure the installation report shows the HVAC system having a tested airflow supply rate of greater than or equal to 350 cfm/ton 350 * tonnage of HVAC system = airflow rate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 99
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any | EECP | 12 | • The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees. | Yes |  | Does the unit have a condenser over ambient temperature (COAT) of at least 3 degrees F? | Drop Down List | Yes;No; | [6 empty] | If 'QM Eligibility' is Yes then Must be 'Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, review the submitted documentation in EECP | Ensure the installation report shows the COAT is greater than or equal to 3 degrees | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 87
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any | EECP | 13 | • An assessment and report are required in accordance with Air Conditioning Contractors of America (ACCA) Standard 48 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations. | Yes |  | Report been submitted in accordance with ACCA Standard 4 prior to any treatments being applied? | Drop Down List | Yes;No; | [6 empty] | If 'QM Eligibility' is Yes then Must be 'Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, review the submitted documentation in EECP | Ensure the installation report or other documentation clearly indicates the HVAC system is functional and not in need of any major repairs prior to the measures being installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 96
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | An installation report should indicate the work performed and show Duct Seal and testing specifications for the HVAC system including existing and proposed leakage rates | The manufacturer may be listed as the implementer or contractor who performed the work or the product used to perform the sealing | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | An installation report should indicate the work performed and show Duct Seal and testing specifications for the HVAC system including existing and proposed leakage rates | The model number may be listed as the implementer or contractor who performed the work or the product used to perform the sealing | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 3 | This measure is applicable for any existing single family, multifamily with two or more units, or mobile home that uses air-cooled, direct expansion (DX) cooling and gas heating, heat pump, or gas heating with no cooling. To confirm that the correct vintage savings are being used, the building age should be verified. See below for details on DEER 2020 vintage years for Old and Median (Existing) vintage buildings : | Yes |  | Building Vintage (construction year) | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New measure property | 2021-06-21 | Kenny Liljestrom |  | Add | 36
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 4 | This measure is applicable for any existing single family, multifamily with two or more units, or mobile home that uses air-cooled, direct expansion (DX) cooling and gas heating, heat pump, or gas heating with no cooling. | Yes |  | What type of HVAC system does the customer have? | Drop Down List | Air-cooled direct expansion (DX) cooling and gas heating;Heat pump;Gas heating with no cooling;Other; | [6 empty] | Must not be 'Other' | QA Checklist | An installation report should indicate the type of HVAC system the customer has | HVAC system type should match EECP and be one of the following: Air-cooled direct expansion (DX) cooling and gas heating, Heat pump, or Gas heating with no cooling | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 48
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 5 | In order to verify compliance with measure requirements and the correct measure selection, the following information must be collected for each installation: • Building information such as: building type, vintage (year), and climate zone • HVAC System type, capacity in tons (for systems with cooling) or kBtuh (for systems with no heating), make and model number • Duct testing information include: o Type of duct test conducted o Pre and post install duct leakage rate percentages o Duct sealing material used | Yes |  | HVAC System Cooling Capacity (tons) | Numeric Value | [8 empty] | Inspections | Photograph the condenser unit (outdoor unit) nameplate to capture the make, model, and cooling capacity (Btu/hr or tons) | The value listed in EECP should match the cooling capacity listed on the nameplate; to convert from Btu/hr to tons use the following formula: Cooling Capacity (Btu/hr) / 12,000 (Btu/ton) = Tons of cooling | QA Checklist | Use photographs or an installation report to determine the cooling capacity of the HVAC system; this can be done by using the make and model to locate the manufacturer spec sheet or the information may be present in an installation report | The value listed in EECP should match the cooling capacity (Btu/hr or tons) listed on the nameplate or in the spec sheet; to convert from Btu/hr to tons use the following formula: Cooling Capacity (Btu/hr) / 12,000 (Btu/ton) = Tons of cooling | New measure property | 2021-06-21 | Kenny Liljestrom |  | Add | 35
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 6 | In order to verify compliance with measure requirements and the correct measure selection, the following information must be collected for each installation: • Building information such as: building type, vintage (year), and climate zone • HVAC System type, capacity in tons (for systems with cooling) or kBtuh (for systems with no heating), make and model number • Duct testing information include: o Type of duct test conducted o Pre and post install duct leakage rate percentages o Duct sealing material used | Yes |  | Heating System Capacity (kBtuh) | Numeric Value | [8 empty] | QA Checklist | Photograph the heating unit nameplate to capture the make, model, and heating capacity (Btu/hr or kBtu/hr) | The value listed in EECP should match the heating capacity listed on the nameplate; to convert from Btu/hr to kBtu/hr use the following formula: Heating Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Heating Capacity (kBtu/hr) | QA Checklist | Use photographs or an installation report to determine the heating capacity of the HVAC system; this can be done by using the make and model to locate the manufacturer spec sheet or the information may be present in an installation report | The value listed in EECP should match the heating capacity (Btu/hr) listed on the nameplate or in the spec sheet; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Heating Capacity (kBtu/hr) | New measure property | 2021-06-21 | Kenny Liljestrom |  | Add | 31
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 7 | Up to two duct tests must be conducted: the first or “test-in” is a system check to determine whether the duct system tightness meets the California Title 24 specifications. | Yes |  | Test-in Duct Leakage Rate (%) | Numeric Value | [8 empty] | QA Checklist | An installation report should indicate the test-in leakage rate | The test-in leakage rate should be greater than or equal to the measure case leakage rate and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 29
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 8 | If the Test-in shows that duct leakage exceeds minimum tightness specifications, and the technicians correct the situation, then a second test or “test-out” must be conducted to verify proper duct tightness was achieved. | Yes |  | Test-out Duct Leakage Rate (%) | Numeric Value | [8 empty] | QA Checklist | An installation report should indicate the test-out leakage rate | The test-out leakage rate should be less than or equal to the measure case leakage rate and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 30
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 9 | If some or all of the existing ductwork is beyond repair and sections must be replaced, the sections that must be replaced must be less than 40 linear feet in total per Section 150.2(b) of the 2019 California Building Energy Efficiency Standards (Title 24) | Yes |  | Length of ductwork replaced (linear feet) | Numeric Value | [8 empty] | Inspections | Photograph of the ductwork showing repairs or replacements in the ducting system | Document or estimate the amount of ductwork replaced | QA Checklist | An installation report should indicate, if any, the length of the duct work replaced as part of the project | The duct work length in the installation report should match what is listed in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 41
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 10 | ...or the replaced ductwork must be installed and tested in accordance with the applicable requirements in 2019 Title 24 Section 150.2(b)1D | Yes |  | Ductwork installed and tested in accordance with requirements in 2019 Title 24 Section 150.2(b)1D? | Drop Down List | Yes;No;N/A; | [6 empty] | Must be 'Yes' or 'N/A' | QA Checklist | If the length of ductwork replaced is greater than 40-linear feet, the implementer should supply the Title-24 compliance sheets as part of the documentation | If the ductwork length is greater than 40 feet, EECP documents need to have Title-24 compliance sheets have been submitted as part of this upload | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 98
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 11 | To identify these measures as part of an existing HVAC system, the program implementer must record existing duct leakage through comprehensive field testing. The testing can be performed while the system is pressurized using a duct blower fan to ensure the target leakage thresholds are achieved. Duct sealing shall be performed on the unpressurized system. After installation, testing shall be performed to ensure the target leakage thresholds are achieved. Photos and test results can serve as documentation that the work was performed on an existing HVAC system. | Yes |  | Has photographic evidence or documentation of the test-in and test-out procedures been uploaded? | Drop Down List | Yes;No; | [6 empty] | Must be ''Yes' | QA Checklist | Check either EECP or an installation report for photographs of the test-in and test-out procedures or results | Photographs of the test-in and test-out leakage rates needs to be included in the submitted documentation | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 96
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 12 | Per Resolution E-5082 “duct connections must not be sealed with duct tape (cloth-backed rubber adhesive tapes). Mastic or aerosol sealant materials are preferred, and butyl tape can be used where mastic or aerosol are impractical.” | Yes |  | Duct sealant material | Drop Down List | Mastic;Aerosol;Butyl tape | [6 empty] | Must be Yes | QA Checklist | Use the manufacturer spec sheet to validate the type of material used for the duct sealant | The material type listed in EECP should match what is listed in the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property | 2021-06-21 | Kenny Liljestrom |  | Add | 21
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 13 | Programs often bundle Quality Maintenance (QM) measures. The following prerequisites must be met before the QM treatments, such as airflow adjustments, can be implemented to ensure an HVAC system is running optimally. | Yes | QM Eligibility | Are other Quality Maintenance (QM) measures (i.e. airflow adjustments) being installed with this measure? | Drop Down List | Yes;No; | [7 empty] | QA Checklist | If implementer answers 'Yes', check the measures installed as part of the enrollment and via double-dip report | EECP should not indicate the customer has installed QM measures previously | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-05 | Kenny Liljestrom |  | Add | 105
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 14 | • The unit must be drawing power. | Yes |  | QM1: Is the HVAC system drawing power? | Drop Down List | Yes;No;N/A | [6 empty] | If 'QM Eligibility' is Yes then Must be ''Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, ensure the installation report shows the HVAC system as being functional prior to any work being performed | The installation report must show the HVAC system as being functioning prior to any adjustments/measures being installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 38
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 15 | • The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted. | Yes |  | QM2: For refrigerant charge adjustments, does the unit deliver supply air of at least 350 cfm/ton? | Drop Down List | Yes;No;N/A; | [6 empty] | If 'QM Eligibility' is Yes then must be 'Yes' or 'N/A' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, ensure the installation report shows the HVAC system having a tested airflow supply rate of greater than or equal to 350 cfm/ton | Using the equation below, determine if the supply airflow is >= 350 cfm/ton: supply air flow, cfm / tonnage of HVAC system = airflow rate per ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 98
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 16 | • The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees. | Yes |  | QM3: Does the unit have a condenser over ambient temperature (COAT) of at least 3 degrees F? | Drop Down List | Yes;No;N/A | [6 empty] | If 'QM Eligibility' is Yes then Must be 'Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, ensure the installation report shows the condenser over ambient temperature (COAT) | Ensure the COAT is greater than or equal to 3 degrees | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 92
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any | EECP | 17 | • An assessment and report are required in accordance with Air Conditioning Contractors of America (ACCA) Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations. | Yes |  | QM4: Has a report been submitted meeting ACCA Standard 4 prior to any treatments being applied? | Drop Down List | Yes;No;N/A | [6 empty] | If 'QM Eligibility' is Yes then Must be 'Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, ensure the installation report or other documentation shows reference to the steps in the ACCA 4 Standard | ACCA Standard 4 items that need to be Include are: a. Inspect for particulate accumulation on filters b. Inspect air filter housing integrity and air seal c. Inspect grilles, registers, diffusers, and trunk/branch balancing dampers for dirt accumulation d. Inspect all accessible ductwork for areas of moisture accumulation or biological growth e. Inspect integrity of all accessible ductwork insulation f. Inspect integrity of all accessible ductwork including: duct strapping, hangers, sections, joints, and seams | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 95
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | An installation report should indicate the sealant manufacturer, implementer, or contractor who performed the work | So long as the field is not blank, it is valid | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 12
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | An installation report should indicate the sealant manufacturer, implementer, or contractor who performed the work | So long as the field is not blank, it is valid | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 5
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any | EECP | 3 | This measure is applicable for any existing single family, multifamily with two or more units, or mobile home that uses air-cooled, direct expansion (DX) cooling and gas heating, heat pump, or gas heating with no cooling. | Yes |  | Building type | Drop Down List | Single Family;Multifamily;Mobile home; | [7 empty] | Inspections | Document the type of residence the unit was installed in (Single Family Home, Multifamily, or Mobile Home) | The building type listed in EECP should match the building type during the inspection | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 13
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any | EECP | 4 | To confirm that the correct vintage savings are being used, the building age should be verified. See below for details on DEER 2020 vintage years for Old and Median (Existing) vintage buildings: • Old: Before 2002 for non-mobile homes, before 1995 for mobile homes • Median (Existing): 2002 to 2016 for non-mobile homes, 1995 to 2005 for mobile homes | Yes |  | Building vintage | Drop Down List | Old: Before 2002 for non-mobile homes, before 1995 for mobile homes;Median: 2002 to 2016 for non-mobile homes, 1995 to 2005 for mobile homes; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | This has only two drop-down options but they are defined differently (very dumb) so we cannot separate the drop-down options | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 16
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any | EECP | 5 | This measure is applicable for any existing single family, multifamily with two or more units, or mobile home that uses air-cooled, direct expansion (DX) cooling and gas heating, heat pump, or gas heating with no cooling. | Yes |  | What type of HVAC system does the customer have? | Drop Down List | Air-cooled direct expansion (DX) cooling and gas heating;Heat pump;Gas heating with no cooling; | [7 empty] | Inspections | Photograph the outdoor HVAC system nameplate to capture the manufacturer and model number | The make and model can be compared to the equipment specification sheet to identify the HVAC system type; this can be done by processing | QA Checklist | An installation report should indicate the type of HVAC system the customer has; if data is collected by the inspections team, use the HVAC make and model number to locate a manufacturer specification sheet to determine the HVAC equipment type | The HVAC system type should match what is listed in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 48
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any | EECP | 6 | Up to two duct tests must be conducted: the first or “test-in” is a system check to determine whether the duct system tightness meets the California Title 24 specifications. | Yes | Test-In | Test-in Duct Leakage Rate (%) | Numeric Value | [8 empty] | QA Checklist | An installation report should indicate the test-in leakage rate | The test-in leakage rate should be greater than or equal to the measure case leakage rate and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 29
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any | EECP | 7 | If the Test-in shows that duct leakage exceeds minimum tightness specifications, and the technicians correct the situation, then a second test or “test-out” must be conducted to verify proper duct tightness was achieved. | Yes | Test-Out | Test-out Duct Leakage Rate (%) | Numeric Value | [8 empty] | QA Checklist | An installation report should indicate the test-out leakage rate | the test-out leakage rate should be less than or equal to the measure case leakage rate and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 30
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any | EECP | 8 | If some or all of the existing ductwork is beyond repair and sections must be replaced, the sections that must be replaced must be less than 40 linear feet in total per Section 150.2(b) of the 2019 California Building Energy Efficiency Standards (Title 24) | Yes | Ductwork Length | Length of ductwork replaced (linear feet) | Numeric Value | [8 empty] | Inspections | Photograph of the ductwork showing repairs or replacements in the ducting system | Document or estimate the amount of ductwork replaced | QA Checklist | An installation report should indicate, if any, the length of the duct work replaced as part of the project | The duct work length in the installation report should match what is listed in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 41
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any | - | 9 | ...or the replaced ductwork must be installed and tested in accordance with the applicable requirements in 2019 Title 24 Section 150.2(b)1D | No | Ductwork Code Requirement | Ductwork installed and tested in accordance with requirements in 2019 Title 24 Section 150.2(b)1D? | Drop Down List | Yes;No;N/A; | [6 empty] | Must be 'Yes' or 'N/A' | QA Checklist | If the length of ductwork replaced is greater than 40-linear feet, the implementer should supply the Title-24 compliance sheets as part of the documentation | If the ductwork length is greater than 40 feet, EECP documents need to have Title-24 compliance sheets have been submitted as part of this upload | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Property removed since contractors and implementors are required to install within local and state codes | Add | 98
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any | EECP | 10 | To identify these measures as part of an existing HVAC system, the program implementer must record existing duct leakage through comprehensive field testing. The testing can be performed while the system is pressurized using a duct blower fan to ensure the target leakage thresholds are achieved. Duct sealing shall be performed on the unpressurized system. After installation, testing shall be performed to ensure the target leakage thresholds are achieved. Photos and test results can serve as documentation that the work was performed on an existing HVAC system. | Yes | Duct Leakage | Has photographic evidence or documentation of the test-in and test-out procedures been uploaded? | Drop Down List | Yes;No; | [6 empty] | Must be ''Yes' | QA Checklist | Check either EECP or an installation report for photographs of the test-in and test-out procedures or results | Photographs of the test-in and test-out leakage rates needs to be included in the submitted documentation | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 96
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any | EECP | 11 | Programs often bundle Quality Maintenance (QM) measures. The following prerequisites must be met before the QM treatments, such as airflow adjustments, can be implemented to ensure an HVAC system is running optimally. | Yes | QM Eligibility | Are other Quality Maintenance (QM) measures (i.e. airflow adjustments) being installed with this measure? | Drop Down List | Yes;No; | [7 empty] | QA Checklist | If implementer answers 'Yes', check the measures installed as part of the enrollment and via double-dip report | EECP should not indicate the customer has installed QM measures previously | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 105
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any | EECP | 12 | • The unit must be drawing power. | Yes | Power Check | QM1: Is the HVAC system drawing power? | Drop Down List | Yes;No;N/A | [6 empty] | If 'QM Eligibility' is Yes then Must be ''Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, ensure the installation report shows the HVAC system as being functional prior to any work being performed | The installation report must show the HVAC system as being functioning prior to any adjustments/measures being installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 38
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any | EECP | 13 | • The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted. | Yes |  | QM2: For refrigerant charge adjustments, does the unit deliver supply air of at least 350 cfm/ton? | Drop Down List | Yes;No;N/A; | [6 empty] | If 'QM Eligibility' is Yes then must be 'Yes' or 'N/A' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, ensure the installation report shows the HVAC system having a tested airflow supply rate of greater than or equal to 350 cfm/ton | Using the equation below, determine if the supply airflow is >= 350 cfm/ton: supply air flow, cfm / tonnage of HVAC system = airflow rate per ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 98
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any | EECP | 14 | • The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees. | Yes |  | QM3: Does the unit have a condenser over ambient temperature (COAT) of at least 3 degrees F? | Drop Down List | Yes;No;N/A | [6 empty] | If 'QM Eligibility' is Yes then Must be 'Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, ensure the installation report shows the condenser over ambient temperature (COAT) | Ensure the COAT is greater than or equal to 3 degrees | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 92
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any | EECP | 15 | • An assessment and report are required in accordance with Air Conditioning Contractors of America (ACCA) Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations. | Yes |  | QM4: Has a report been submitted meeting ACCA Standard 4 prior to any treatments being applied? | Drop Down List | Yes;No;N/A | [6 empty] | If 'QM Eligibility' is Yes then Must be 'Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, ensure the installation report or other documentation shows reference to the steps in the ACCA 4 Standard | ACCA Standard 4 items that need to be Include are: a. Inspect for particulate accumulation on filters b. Inspect air filter housing integrity and air seal c. Inspect grilles, registers, diffusers, and trunk/branch balancing dampers for dirt accumulation d. Inspect all accessible ductwork for areas of moisture accumulation or biological growth e. Inspect integrity of all accessible ductwork insulation f. Inspect integrity of all accessible ductwork including: duct strapping, hangers, sections, joints, and seams | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 95
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Make | Make | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 4
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 5
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any | EECP | 3 | Legacy property, set to expire 12/31/21 | Yes | Actual QTY | Cap-Tons | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any | EECP | 4 | Legacy property, set to expire 12/31/21 | Yes | Base Case Measure Code | Base Case Measure Code | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 22
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any | EECP | 5 | Legacy property, set to expire 12/31/21 | Yes | Base Case Measure Description | Base Case Measure Description | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 29
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any | EECP | 6 | Legacy property, set to expire 12/31/21 | Yes | Cap-Tons | Cap-Tons | Numeric Value | [8 empty] | Inspections | Photograph the outdoor HVAC system nameplate to capture the manufacturer, model number, and capacity (Btu/hr or tons) | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit | QA Checklist | Use an installation report to determine the capacity of the HVAC system; this can be found using the HVAC make and model and locating the specification sheet | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any | EECP | 7 | Legacy property, set to expire 12/31/21 | Yes | End Use | End Use | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 7
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any | EECP | 8 | Legacy property, set to expire 12/31/21 | Yes | Location | Location | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any | EECP | 12 | Legacy property, set to expire 12/31/21 | Yes | Refrigerant applied | Refrigerant successfully applied and meets manufacturer recommended levels | Drop Down List | Yes¦1;No¦0 | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 74
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any | EECP | 13 | Legacy property, set to expire 12/31/21 | Yes | Serial Number | Serial Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 13
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any | EECP | 14 | Legacy property, set to expire 12/31/21 | Yes | Size | Cap-Tons | Numeric Value | [8 empty] | Inspections | Photograph the outdoor HVAC system nameplate to capture the manufacturer, model number, and capacity (Btu/hr or tons) | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit | QA Checklist | Use an installation report to determine the capacity of the HVAC system; this can be found using the HVAC make and model and locating the specification sheet | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Make | Make | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 4
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 5
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any | EECP | 3 | Legacy property, set to expire 12/31/21 | Yes | Actual QTY | Cap-Tons | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any | EECP | 4 | Legacy property, set to expire 12/31/21 | Yes | Base Case Measure Code | Base Case Measure Code | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 22
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any | EECP | 5 | Legacy property, set to expire 12/31/21 | Yes | Base Case Measure Description | Base Case Measure Description | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 29
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any | EECP | 6 | Legacy property, set to expire 12/31/21 | Yes | Cap-Tons | Cap-Tons | Numeric Value | [8 empty] | Inspections | Photograph the outdoor HVAC system nameplate to capture the manufacturer, model number, and capacity (Btu/hr or tons) | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit | QA Checklist | Use an installation report to determine the capacity of the HVAC system; this can be found using the HVAC make and model and locating the specification sheet | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any | EECP | 7 | Legacy property, set to expire 12/31/21 | Yes | End Use | End Use | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 7
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any | EECP | 8 | Legacy property, set to expire 12/31/21 | Yes | Location | Location | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any | EECP | 12 | Legacy property, set to expire 12/31/21 | Yes | Refrigerant applied | Refrigerant successfully applied and meets manufacturer recommended levels | Drop Down List | Yes¦1;No¦0 | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 74
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any | EECP | 13 | Legacy property, set to expire 12/31/21 | Yes | Serial Number | Serial Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 13
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any | EECP | 14 | Legacy property, set to expire 12/31/21 | Yes | Size | Cap-Tons | Numeric Value | [8 empty] | Inspections | Photograph the outdoor HVAC system nameplate to capture the manufacturer, model number, and capacity (Btu/hr or tons) | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit | QA Checklist | Use an installation report to determine the capacity of the HVAC system; this can be found using the HVAC make and model and locating the specification sheet | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Make | Make | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 4
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 5
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any | EECP | 3 | Legacy property, set to expire 12/31/21 | Yes | Actual QTY | Cap-Tons | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any | EECP | 4 | Legacy property, set to expire 12/31/21 | Yes | Base Case Measure Code | Base Case Measure Code | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 22
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any | EECP | 5 | Legacy property, set to expire 12/31/21 | Yes | Base Case Measure Description | Base Case Measure Description | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 29
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any | EECP | 6 | Legacy property, set to expire 12/31/21 | Yes | Cap-Tons | Cap-Tons | Numeric Value | [8 empty] | Inspections | Photograph the outdoor HVAC system nameplate to capture the manufacturer, model number, and capacity (Btu/hr or tons) | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit | QA Checklist | Use an installation report to determine the capacity of the HVAC system; this can be found using the HVAC make and model and locating the specification sheet | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any | EECP | 7 | Legacy property, set to expire 12/31/21 | Yes | End Use | End Use | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 7
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any | EECP | 8 | Legacy property, set to expire 12/31/21 | Yes | Location | Location | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any | EECP | 12 | Legacy property, set to expire 12/31/21 | Yes | Refrigerant applied | Refrigerant successfully applied and meets manufacturer recommended levels | Drop Down List | Yes¦1;No¦0 | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 74
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any | EECP | 13 | Legacy property, set to expire 12/31/21 | Yes | Serial Number | Serial Number | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 13
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any | EECP | 14 | Legacy property, set to expire 12/31/21 | Yes | Size | Cap-Tons | Numeric Value | [8 empty] | Inspections | Photograph the outdoor HVAC system nameplate to capture the manufacturer, model number, and capacity (Btu/hr or tons) | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit | QA Checklist | Use an installation report to determine the capacity of the HVAC system; this can be found using the HVAC make and model and locating the specification sheet | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | An invoice or installation report should indicate the Refrigerant type, the manufacturer of the refrigerant, or the implementer who performed the work | The manufacturer may be listed as the implementer or contractor who performed the work, the refrigerant type used, or the refrigerant manufacturer | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | An invoice or installation report should indicate the Refrigerant type, the manufacturer of the refrigerant, or the implementer who performed the work | The model number may be listed as the implementer or contractor who performed the work, the refrigerant type used, or the refrigerant manufacturer | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any | EECP | 3 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Air Flow Rate | After implementation air flow rate? (cfm/ton) | Numeric Value | [7 empty] | Must be >= 350 | QA Checklist | An installation report should indicate the airflow rate after the refrigerant charge adjustment | The value should be above 350 cfm/ton 350 * tonnage of HVAC system = airflow rate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any | EECP | 4 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Operational | Is the unit operational? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Inspect both the outdoor and indoor HVAC systems | Ensure both units are energized and functional | QA Checklist | The installation report should indicate the HVAC system was operational in the existing conditions performance data; i.e. airflows, power draw, etc. should not be zero | An installation report should indicate the airflow rate after the refrigerant charge adjustment |  | 2021-06-21 | Kenny Liljestrom |  | Add | 24
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any | EECP | 5 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | COAT | Before implementation condenser over ambient temperature (COAT) ? (degrees) | Numeric Value | [7 empty] | Must be >= 3 | QA Checklist | Review the submitted installation report or documentation in EECP for the condenser over ambient temperature (COAT) | Ensure the installation report shows the COAT is greater than or equal to 3 degrees | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 75
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any | EECP | 6 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Assessment_Report | Before implementation of the measure was an assessment and report created in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Review the submitted installation report or documentation in EECP for ACCA Standard 4 requirements being met | The installation report or other documentation should clearly indicates the HVAC system is functional and not in need of any major repairs prior to the measures being installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label to change 'ACCA Standard 43' to 'ACCA Standard 4' | 2021-06-21 | Kenny Liljestrom |  | Add | 228
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any | EECP | 7 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | QM Service Agreement | Has Customer agreed to the QM Service Agreement? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | A service agreement or signed contract with the customer should be included in the submitted documentation | The document should indicate the customer has agreed to future quality maintenance performed at their residence (no requirement for the length or number of services performed) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 48
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any | EECP | 8 | This measure is applicable for residential single family, multifamily, and double-wide mobile homes that use central air-cooled direct expansion (DX) cooling and gas heating. | Yes | DX Cooling_Gas Heat | Does premise have central air-cooled direct expansion (DX) cooling and gas heating? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the make and model of the HVAC system and furnace to determine the HVAC system type | The system type is limited to Direct Expansion (DX) cooling and gas heating | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 83
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any | EECP | 9 | The contractor must provide the amount and percent refrigerant charge added to or removed from the system to verify the applicable measure. | Yes |  | Amount of refrigerant added or removed | Numeric Value | [8 empty] | QA Checklist | Review the installation report to validate the amount of refrigerant added or removed | The installation report should indicate the amount (in lbs) of the refrigerant added or removed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-25 | Kenny Liljestrom |  | Add | 38
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any | EECP | 10 | The contractor must provide the amount and percent refrigerant charge added to or removed from the system to verify the applicable measure. | Yes |  | Percent of refrigerant added or removed | Numeric Value | [8 empty] | QA Checklist | Review the installation report to validate the percent of refrigerant added or removed | The installation report should indicate the percent of the refrigerant added or removed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-25 | Kenny Liljestrom |  | Add | 39
1 | SWSV007 | 1 | Condenser Coil Cleaning, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | An installation report should indicate the implementer or contractor who performed the work | The manufacturer may be listed as the implementer or contractor who performed the work | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
1 | SWSV007 | 1 | Condenser Coil Cleaning, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | An installation report should indicate the implementer or contractor who performed the work | The model number may be listed as the implementer or contractor who performed the work | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
1 | SWSV007 | 1 | Condenser Coil Cleaning, Residential | Any | Any | Any | EECP | 3 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Air Flow Rate | After implementation air flow rate? (cfm/ton) | Numeric Value | [7 empty] | Must be >= 350 | QA Checklist | An installation report should indicate the airflow rate after the refrigerant charge adjustment | The value should be above 350 cfm/ton 350 * tonnage of HVAC system = airflow rate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
1 | SWSV007 | 1 | Condenser Coil Cleaning, Residential | Any | Any | Any | EECP | 4 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Operational | Is the unit operational? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Inspect both the outdoor and indoor HVAC systems | Ensure both units are energized and functional | QA Checklist | The installation report should indicate the HVAC system was operational in the existing conditions performance data; i.e. airflows, power draw, etc. should not be zero | An installation report should indicate the airflow rate after the refrigerant charge adjustment |  | 2021-06-21 | Kenny Liljestrom |  | Add | 24
1 | SWSV007 | 1 | Condenser Coil Cleaning, Residential | Any | Any | Any | EECP | 5 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | COAT | Before implementation condenser over ambient temperature (COAT) ? (degrees) | Numeric Value | [7 empty] | Must be >= 3 | QA Checklist | Review the submitted installation report or documentation in EECP for the condenser over ambient temperature (COAT) | Ensure the installation report shows the COAT is greater than or equal to 3 degrees | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 75
1 | SWSV007 | 1 | Condenser Coil Cleaning, Residential | Any | Any | Any | EECP | 6 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Assessment_Report | Before implementation of the measure was an assessment and report created in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Review the submitted installation report or documentation in EECP for ACCA Standard 4 requirements being met | The installation report or other documentation should clearly indicates the HVAC system is functional and not in need of any major repairs prior to the measures being installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label to change 'ACCA Standard 43' to 'ACCA Standard 4' | 2021-06-21 | Kenny Liljestrom |  | Add | 228
1 | SWSV007 | 1 | Condenser Coil Cleaning, Residential | Any | Any | Any | EECP | 7 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | QM Service Agreement | Has Customer agreed to the QM Service Agreement? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | A service agreement or signed contract with the customer should be included in the submitted documentation | The document should indicate the customer has agreed to future quality maintenance performed at their residence (no requirement for the length or number of services performed) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 48
1 | SWSV007 | 1 | Condenser Coil Cleaning, Residential | Any | Any | Any | EECP | 8 | This measure is applicable for residential single family, multifamily, and double-wide mobile homes that use central air-cooled direct expansion (DX) cooling and gas heating. | Yes | DX Cooling_Gas Heat | Does premise have central air-cooled direct expansion (DX) cooling and gas heating? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the make and model of the HVAC system and furnace to determine the HVAC system type | The system type is limited to Direct Expansion (DX) cooling and gas heating | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 83
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | An installation report should indicate the implementer or contractor who performed the work | The manufacturer may be listed as the implementer or contractor who performed the work | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | An installation report should indicate the implementer or contractor who performed the work | The model number may be listed as the implementer or contractor who performed the work | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any | EECP | 3 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Air Flow Rate | After implementation air flow rate? (cfm/ton) | Numeric Value | [7 empty] | Must be >= 350 | QA Checklist | An installation report should indicate the airflow rate after the refrigerant charge adjustment | The value should be above 350 cfm/ton 350 * tonnage of HVAC system = airflow rate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any | EECP | 4 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Operational | Is the unit operational? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Inspect both the outdoor and indoor HVAC systems | Ensure both units are energized and functional | QA Checklist | The installation report should indicate the HVAC system was operational in the existing conditions performance data; i.e. airflows, power draw, etc. should not be zero | An installation report should indicate the airflow rate after the refrigerant charge adjustment |  | 2021-06-21 | Kenny Liljestrom |  | Add | 24
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any | EECP | 5 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | COAT | Before implementation condenser over ambient temperature (COAT) ? (degrees) | Numeric Value | [7 empty] | Must be >= 3 | QA Checklist | Review the submitted installation report or documentation in EECP for the condenser over ambient temperature (COAT) | Ensure the installation report shows the COAT is greater than or equal to 3 degrees | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 75
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any | EECP | 6 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Assessment_Report | Before implementation of the measure was an assessment and report created in accordance with ACCA Standard 43 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Review the submitted installation report or documentation in EECP for ACCA Standard 4 requirements being met | The installation report or other documentation should clearly indicates the HVAC system is functional and not in need of any major repairs prior to the measures being installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 229
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any | EECP | 7 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | QM Service Agreement | Has Customer agreed to the QM Service Agreement? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | A service agreement or signed contract with the customer should be included in the submitted documentation | The document should indicate the customer has agreed to future quality maintenance performed at their residence (no requirement for the length or number of services performed) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 48
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any | EECP | 8 | This measure is applicable for residential single family, multifamily, and double-wide mobile homes that use central air-cooled direct expansion (DX) cooling and gas heating. | Yes | DX Cooling_Gas Heat | Does premise have central air-cooled direct expansion (DX) cooling and gas heating? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Use the make and model of the HVAC system and furnace to determine the HVAC system type | The system type is limited to Direct Expansion (DX) cooling and gas heating | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 83
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any | EECP | 9 | Legacy property | Yes | End Use | End Use | Text Box | [8 empty] | - | - | - | - | - | - | Possibly Legacy, if not active, remove | 2021-06-21 | Kenny Liljestrom |  | Add | 7
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any | EECP | 10 | Legacy property | Yes | Location | Location | Text Box | [8 empty] | - | - | - | - | - | - | Possibly Legacy, if not active, remove | 2021-06-21 | Kenny Liljestrom |  | Add | 8
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any | EECP | 11 | Legacy property | Yes | Serial Number | Serial Number | Text Box | [8 empty] | - | - | - | - | - | - | Possibly Legacy, if not active, remove | 2021-06-21 | Kenny Liljestrom |  | Add | 13
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any | EECP | 12 | Legacy property | Yes | Sticker Number | Sticker Number | Text Box | [8 empty] | - | - | - | - | - | - | Possibly Legacy, if not active, remove | 2021-06-21 | Kenny Liljestrom |  | Add | 14
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | Any | Any | Any | EECP | 1 | The Return Duct Retrofit measure shall be installed by a residential HVAC contractor in a mobile home where there is an existing open belly return with a supply system in the ceiling. The Crossover Duct Replacement measure shall be installed by a residential HVAC contractor in an extended mobile home where two or more sections of the home has been joined. The crossover duct connects the supply ducting of two or more sections. | Yes |  | Installation contractor | Text Box | [8 empty] | QA Checklist | Review the submitted installation report to verify the contractor used for the project | The contractor used on the project should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 23
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | A | Any | Any | EECP | 2 | The Return Duct Retrofit measure shall be installed by a residential HVAC contractor in a mobile home where there is an existing open belly return with a supply system in the ceiling. | Yes |  | Photograph of open belly return duct submitted? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Review the submitted files in EECP or the installation report for a photograph of the existing conditions at the site | The photograph should contain an open duct (a duct that does not return back to the HVAC unit) | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 47
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | B | Any | Any | EECP | 3 | The ducting must be deteriorated, damaged, or not installed correctly to be eligible for this measure. | Yes |  | Photograph showing deterioration, damage, or poor installation of crossover duct submitted? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Review the submitted files in EECP or the installation report for a photograph of the existing conditions at the site | The photograph must show the duct as being damaged, deteriorated, or having gaps indicating poor installation | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 91
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | C | Any | Any | EECP | 4 | The Return Duct Retrofit measure shall be installed by a residential HVAC contractor in a mobile home where there is an existing open belly return with a supply system in the ceiling. | Yes |  | Photograph of open belly return duct submitted? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Review the submitted files in EECP or the installation report for a photograph of the existing conditions at the site | The photograph should contain an open duct (a duct that does not return back to the HVAC unit) | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 47
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | D | Any | Any | EECP | 5 | The ducting must be deteriorated, damaged, or not installed correctly to be eligible for this measure. | Yes |  | Photograph showing deterioration, damage, or poor installation of crossover duct submitted? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Review the submitted files in EECP or the installation report for a photograph of the existing conditions at the site | The photograph must show the duct as being damaged, deteriorated, or having gaps indicating poor installation | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 91
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | A | Any | Any | EECP | 6 | Installed return ducts shall be made from either galvanized steel, tinplated steel, or aluminum, or shall be listed as Class 0 or Class 1 air ducts under Underwriters' Laboratories, Inc. Standard for Air Ducts, UL181-1972. | Yes |  | Replacement duct material | Drop Down List | Galvanized steel;Tinplated steel;Aluminium;Class 0 air duct;Class 1 air duct; | [7 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-01-20 | Kenny Liljestrom |  |  | 25
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | B | Any | Any | EECP | 7 | Installed return ducts shall be made from either galvanized steel, tinplated steel, or aluminum, or shall be listed as Class 0 or Class 1 air ducts under Underwriters' Laboratories, Inc. Standard for Air Ducts, UL181-1972. | Yes |  | Replacement duct material | Drop Down List | Galvanized steel;Tinplated steel;Aluminium; | [7 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-01-20 | Kenny Liljestrom |  |  | 25
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | C | Any | Any | EECP | 8 | Installed return ducts shall be made from either galvanized steel, tinplated steel, or aluminum, or shall be listed as Class 0 or Class 1 air ducts under Underwriters' Laboratories, Inc. Standard for Air Ducts, UL181-1972. | Yes |  | Replacement duct material | Drop Down List | Galvanized steel;Tinplated steel;Aluminium;Class 0 air duct;Class 1 air duct; | [7 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-01-20 | Kenny Liljestrom |  |  | 25
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | D | Any | Any | EECP | 9 | Installed return ducts shall be made from either galvanized steel, tinplated steel, or aluminum, or shall be listed as Class 0 or Class 1 air ducts under Underwriters' Laboratories, Inc. Standard for Air Ducts, UL181-1972. | Yes |  | Replacement duct material | Drop Down List | Galvanized steel;Tinplated steel;Aluminium; | [7 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-01-20 | Kenny Liljestrom |  |  | 25
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | A | Any | Any | EECP | 10 | Return ducts in unconditioned spaces shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. | Yes | Return Duct | Is the return duct in a conditioned space? | Drop Down List | Yes;No; | [7 empty] | Inspections | Locate the ducting for the HVAC unit | Make note of the ducting location because it determines the eligibility of the thermal insulation measure property | QA Checklist | Use the submitted invoice or installation report to determine where the ducting is located | Make note of the ducting location because it determines the eligibility of the thermal insulation measure property |  | 2022-01-20 | Kenny Liljestrom |  |  | 42
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | B | Any | Any | EECP | 11 | The crossover duct shall be supported and or prevented from ground contact. If located in interior areas, not exposed to outdoor air, crossover ducts shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. If the crossover duct is installed in an area that is exposed to outdoor air, such as outside the building’s envelope, the ducts shall be insulated with material having effective thermal resistance (R) of not less than 8.0. | Yes | Duct Location | Crossover duct location | Drop Down List | Interior;Exterior; | [7 empty] | Inspections | Locate the ducting for the HVAC unit | Make note of the ducting location because it determines the eligibility of the thermal insulation measure property | QA Checklist | Use the submitted invoice or installation report to determine where the ducting is located | Make note of the ducting location because it determines the eligibility of the thermal insulation measure property |  | 2022-01-20 | Kenny Liljestrom |  |  | 23
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | C | Any | Any | EECP | 12 | Return ducts in unconditioned spaces shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. | Yes | Return Duct | Is the return duct in a conditioned space? | Drop Down List | Yes;No; | [7 empty] | Inspections | Locate the ducting for the HVAC unit | Make note of the ducting location because it determines the eligibility of the thermal insulation measure property | QA Checklist | Use the submitted invoice or installation report to determine where the ducting is located | Make note of the ducting location because it determines the eligibility of the thermal insulation measure property |  | 2022-01-20 | Kenny Liljestrom |  |  | 42
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | D | Any | Any | EECP | 13 | The crossover duct shall be supported and or prevented from ground contact. If located in interior areas, not exposed to outdoor air, crossover ducts shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. If the crossover duct is installed in an area that is exposed to outdoor air, such as outside the building’s envelope, the ducts shall be insulated with material having effective thermal resistance (R) of not less than 8.0. | Yes | Duct Location | Crossover duct location | Drop Down List | Interior;Exterior; | [7 empty] | Inspections | Locate the ducting for the HVAC unit | Make note of the ducting location because it determines the eligibility of the thermal insulation measure property | QA Checklist | Use the submitted invoice or installation report to determine where the ducting is located | Make note of the ducting location because it determines the eligibility of the thermal insulation measure property |  | 2022-01-20 | Kenny Liljestrom |  |  | 23
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | A | Any | Any | EECP | 14 | Return ducts in unconditioned spaces shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. | Yes |  | Return duct insulation thermal resistance (R) | Numeric Value | [7 empty] | If Return Duct is 'No' then Must be >= 4 | Inspections | Locate the ducting for the HVAC unit | If the return ducting is in a conditioned space, the ducting does not require insulation; If the return ducting is in an unconditioned space, the ducting must have insulation covering it | QA Checklist | Use the submitted invoice or installation report to determine where the ducting is located | If the return ducting is in a conditioned space, the ducting does not require insulation; If the return ducting is in an unconditioned space, the ducting must have insulation covering it and the thermal resistance rating (R) must be >= 4; the insulation rating can be determined with a submittal of the insulation specification sheet or statement in the installation report |  | 2022-01-20 | Kenny Liljestrom |  |  | 45
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | B | Any | Any | EECP | 15 | The crossover duct shall be supported and or prevented from ground contact. If located in interior areas, not exposed to outdoor air, crossover ducts shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. If the crossover duct is installed in an area that is exposed to outdoor air, such as outside the building’s envelope, the ducts shall be insulated with material having effective thermal resistance (R) of not less than 8.0. | Yes |  | Crossover duct insulation thermal resistance (R) | Numeric Value | [7 empty] | If Duct Location is Interior then must be >= 4 If Duct Location is Exterior then must be >= 8 | Inspections | Locate the ducting for the HVAC unit | If the return ducting is in a conditioned space, the ducting does not require insulation; If the return ducting is in an unconditioned space, the ducting must have insulation covering it | QA Checklist | Use the submitted invoice or installation report to determine where the ducting is located | If the return ducting is located in the interior of the mobile home, the ducting must have insulation covering it and the thermal resistance rating (R) must be >= 4; If the return ducting is located on the exterior of the mobile home, the ducting must have insulation covering it and the thermal resistance rating (R) must be >= 8; the insulation rating can be determined with a submittal of the insulation specification sheet or statement in the installation report |  | 2022-01-20 | Kenny Liljestrom |  |  | 48
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | C | Any | Any | EECP | 16 | Return ducts in unconditioned spaces shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. | Yes |  | Return duct insulation thermal resistance (R) | Numeric Value | [7 empty] | If Return Duct is 'No' then Must be >= 4 | Inspections | Locate the ducting for the HVAC unit | If the return ducting is in a conditioned space, the ducting does not require insulation; If the return ducting is in an unconditioned space, the ducting must have insulation covering it | QA Checklist | Use the submitted invoice or installation report to determine where the ducting is located | If the return ducting is in a conditioned space, the ducting does not require insulation; If the return ducting is in an unconditioned space, the ducting must have insulation covering it and the thermal resistance rating (R) must be >= 4; the insulation rating can be determined with a submittal of the insulation specification sheet or statement in the installation report |  | 2022-01-20 | Kenny Liljestrom |  |  | 45
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | D | Any | Any | EECP | 17 | The crossover duct shall be supported and or prevented from ground contact. If located in interior areas, not exposed to outdoor air, crossover ducts shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. If the crossover duct is installed in an area that is exposed to outdoor air, such as outside the building’s envelope, the ducts shall be insulated with material having effective thermal resistance (R) of not less than 8.0. | Yes |  | Crossover duct insulation thermal resistance (R) | Numeric Value | [7 empty] | If Duct Location is Interior then must be >= 4 If Duct Location is Exterior then must be >= 8 | Inspections | Locate the ducting for the HVAC unit |  | QA Checklist | Use the submitted invoice or installation report to determine where the ducting is located | If the return ducting is located in the interior of the mobile home, the ducting must have insulation covering it and the thermal resistance rating (R) must be >= 4; If the return ducting is located on the exterior of the mobile home, the ducting must have insulation covering it and the thermal resistance rating (R) must be >= 8; the insulation rating can be determined with a submittal of the insulation specification sheet or statement in the installation report |  | 2022-01-20 | Kenny Liljestrom |  |  | 48
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | A | Any | Any | EECP | 18 | Belly return systems shall be verified by a pre and post total leakage duct test at 25 pascals on the return side of the duct system only. This shall be achieved by separating the supply from return side of the duct system by sealing at the air handler/furnace, typically at the filter slot to eliminate supply side leakage from the test. | Yes |  | Pre leakage rate (%) | Numeric Value | [7 empty] | Must be >= 50% | QA Checklist | Use the installation report to verify the pre-installation leakage rate of the system | The leakage rate should be listed as a percentage; if the percentage is not listed in the installation report, it can be determined by one of the following formulas: Leakage Rate (cfm) / Total Airflow Rate (cfm) = % Leakage Leakage Pressure / Total Pressure = % leakage The leakage rate must be >= 50% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 20
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | B | Any | Any | EECP | 19 | Belly return systems shall be verified by a pre and post total leakage duct test at 25 pascals on the return side of the duct system only. This shall be achieved by separating the supply from return side of the duct system by sealing at the air handler/furnace, typically at the filter slot to eliminate supply side leakage from the test. | Yes |  | Pre leakage rate (%) | Numeric Value | [7 empty] | Must be >= 35% | QA Checklist | Use the installation report to verify the pre-installation leakage rate of the system | The leakage rate should be listed as a percentage; if the percentage is not listed in the installation report, it can be determined by one of the following formulas: Leakage Rate (cfm) / Total Airflow Rate (cfm) = % Leakage Leakage Pressure / Total Pressure = % leakage The leakage rate must be >= 35% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 20
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | C | Any | Any | EECP | 20 | Belly return systems shall be verified by a pre and post total leakage duct test at 25 pascals on the return side of the duct system only. This shall be achieved by separating the supply from return side of the duct system by sealing at the air handler/furnace, typically at the filter slot to eliminate supply side leakage from the test. | Yes |  | Pre leakage rate (%) | Numeric Value | [7 empty] | Must be >= 50% | QA Checklist | Use the installation report to verify the pre-installation leakage rate of the system | The leakage rate should be listed as a percentage; if the percentage is not listed in the installation report, it can be determined by one of the following formulas: Leakage Rate (cfm) / Total Airflow Rate (cfm) = % Leakage Leakage Pressure / Total Pressure = % leakage The leakage rate must be >= 50% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 20
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | D | Any | Any | EECP | 21 | Belly return systems shall be verified by a pre and post total leakage duct test at 25 pascals on the return side of the duct system only. This shall be achieved by separating the supply from return side of the duct system by sealing at the air handler/furnace, typically at the filter slot to eliminate supply side leakage from the test. | Yes |  | Pre leakage rate (%) | Numeric Value | [7 empty] | Must be >= 35% | QA Checklist | Use the installation report to verify the pre-installation leakage rate of the system | The leakage rate should be listed as a percentage; if the percentage is not listed in the installation report, it can be determined by one of the following formulas: Leakage Rate (cfm) / Total Airflow Rate (cfm) = % Leakage Leakage Pressure / Total Pressure = % leakage The leakage rate must be >= 35% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 20
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | Any | Any | Any | EECP | 22 | Belly return systems shall be verified by a pre and post total leakage duct test at 25 pascals on the return side of the duct system only. This shall be achieved by separating the supply from return side of the duct system by sealing at the air handler/furnace, typically at the filter slot to eliminate supply side leakage from the test. | Yes |  | Post leakage rate (%) | Numeric Value | [7 empty] | Must be <= 15% | QA Checklist | Use the installation report to verify the post-installation leakage rate of the system | The leakage rate should be listed as a percentage; if the percentage is not listed in the installation report, it can be determined by one of the following formulas: Leakage Rate (cfm) / Total Airflow Rate (cfm) = % Leakage Leakage Pressure / Total Pressure = % leakage The leakage rate must be <= 15% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 21
0 | SWWH001 | 2 | Faucet Aerator, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWWH001 | 2 | Faucet Aerator, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWWH001 | 2 | Faucet Aerator, Residential | Any | Any | Any | EECP | 3 | The existing faucet must have a flow rate of at least 2.2 gpm. | Yes | Existing Flow Rate | Existing Flow Rate (gpm) | Numeric Value | [7 empty] | Must be >= 2.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 24
0 | SWWH001 | 2 | Faucet Aerator, Residential | Any | Any | Any | EECP | 4 | Revisit | Yes | Flow Rate | Flow Rate of Installed Unit (gpm) | Numeric Value | [8 empty] | QA Checklist | Cross check manufacturer and model number with flow rate | The flow rate of the installed unit must match the flow entered in EECP and be less than or equal to the flowrate required by the measure. | Inspections | Using a measuring cup or flow rate measuring device, fill the device for 6 seconds, record the amount of Oz of water in the device; gallons per minute can be calculated as: Measured Oz * 0.078125 = GPM | The flow rate of the installed unit must match the flow entered in EECP and be less than or equal to the flowrate required by the measure. |  | 2021-06-21 | Kenny Liljestrom |  | Add | 33
0 | SWWH001 | 2 | Faucet Aerator, Residential | Any | Any | Any | EECP | 5 | Revisit | Yes | Natural Gas WH | Does the facility utilize natural gas water heating equipment? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Locate the water heater for the building and determine if the unit is fueled by natural gas (yellow pipe) | The water heater must be fueled by natural gas | QA Checklist | A photograph of the water heater showing the yellow gas pipe; or the make and model of the water heater which can be cross referenced with the manufacturer specification sheet to identify of the unit is gas fired | The water heater must be fueled by natural gas |  | 2021-06-21 | Kenny Liljestrom |  | Add | 62
0 | SWWH001 | 2 | Faucet Aerator, Residential | Any | AR | Any | EECP | 6 | For accelerated replacement application types, the retrofit faucet must have an existing faucet aerator. For all other application types, the faucet must not have an aerator installed. | Yes | Existing Aerator | Does the faucet have an existing aerator installed? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | A photograph of the existing faucet aerator is sufficient documentation if available | Must be 'Yes' for AR measures and show an existing aerator | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-03-11 | Kenny Liljestrom | Updated to make the validation rules more clear | Add | 51
0 | SWWH001 | 2 | Faucet Aerator, Residential | Any | AOE | Any | EECP | 6 | For accelerated replacement application types, the retrofit faucet must have an existing faucet aerator. For all other application types, the faucet must not have an aerator installed. | Yes | Existing Aerator | Does the faucet have an existing aerator installed? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | QA Checklist | A photograph of the existing faucet aerator is sufficient documentation if available | An aerator must not be installed on the faucet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-03-11 | Kenny Liljestrom | Updated to make the validation rules more clear |  | 51
0 | SWWH001 | 2 | Faucet Aerator, Residential | Any | Any | Any | QA Checklist | 7 | The measure is not applicable to new faucets that meet or exceed the 2016 California Appliance Efficiency Regulations (Title 20) code requirement of 1.2 gpm flow rate for lavatory faucet and 1.8 gpm flow rate for kitchen faucet. | No | Title 20 | Was this measure installed on a new faucet that met or exceeded the 2016 California Appliance Efficiency Regulations (Title 20) code requirement of 1.2 gpm flow rate for lavatory faucet and 1.8 gpm flow rate for kitchen faucet? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Property label needs to be updated | 2022-03-11 | Kenny Liljestrom | Property removed since contractors and implementors are required to install within local and state codes | Add | 227
1 | SWWH002 | 2 | Low-Flow Showerhead - Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph of installed showerhead, if nameplate is visible on the threaded connector or showerhead, document or photograph the model number | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
1 | SWWH002 | 2 | Low-Flow Showerhead - Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph of installed showerhead, if nameplate is visible on the threaded connector or showerhead, document or photograph the model number | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
1 | SWWH002 | 2 | Low-Flow Showerhead - Residential | Any | Any | Any | EECP | 3 | Good to have | Yes | Existing Flow Rate | Existing Flow Rate (gpm) | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 24
1 | SWWH002 | 2 | Low-Flow Showerhead - Residential | Any | Any | Any | EECP | 4 | Good to have | Yes | Flow Rate | Flow Rate of Installed Unit (gpm) | Numeric Value | [8 empty] | Inspections | Using a measuring cup or flow rate measuring device, fill the device for 6 seconds, record the amount of Oz of water in the device; gallons per minute can be calculated as: Measured Oz * 0.078125 = GPM | The flow rate of the installed unit must match the flow entered in EECP and be less than or equal to the flowrate required by the measure. | QA Checklist | Cross check manufacturer and model number with flow rate | The flow rate of the installed unit must match the flow entered in EECP and be less than or equal to the flowrate required by the measure. | Request to remove | 2021-06-21 | Kenny Liljestrom |  | Add | 33
1 | SWWH002 | 2 | Low-Flow Showerhead - Residential | Any | Any | Any | EECP | 5 | Measure Description | Yes | Natural Gas WH | Does the facility utilize natural gas water heating equipment? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Locate the water heater for the building and determine if the unit is fueled by natural gas (yellow pipe) | The water heater must be fueled by natural gas | QA Checklist | Use the installation report to verify the type of water heater used to heat the domestic hot water | The water heater must be fueled by natural gas | Request to remove | 2021-06-21 | Kenny Liljestrom |  | Add | 62
1 | SWWH002 | 2 | Low-Flow Showerhead - Residential | Any | AR | Any | EECP | 6 | To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers • Customer/site information • Make/model of pre-existing equipment and/or • Performance/flowrate measurements of pre-existing equipment, and/or • Photograph of pre-existing equipment in place and operating | Yes | Preponderance of Evidence | Has required Preponderance of Evidence (POE) been submitted in accordance with the workpaper? | Drop Down List | Yes;No; | [6 empty] | Must be ''Yes' | QA Checklist | Review the POE documentation and determine if it is adequate based on required criteria. | Has required Preponderance of Evidence (POE) been submitted to include but not limited to: Targeted segment of the market or customers, customer/site information, make/model of pre-existing equipment and/or performance/flowrate measurements of pre-existing equipment and/or photograph of pre-existing equipment in place and operating, or one of the three alternatives listed in Section 7.3 of POEV 2.0? | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-25 | Kenny Liljestrom |  | Add | 93
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any | EECP | 3 | Thermostatic shower valve (TSV): Any TSV certified by applicable standards (e.g., ANSI, ASPE, etc.) is eligible. | Yes | Certified | Is the TSV certified by applicable standards (e.g., ANSI, ASPE, etc.) ? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Using the make and model, cross reference the ANSI or ASPE databases to ensure the model is listed | The make and model must be listed in one of the approved databases | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 71
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any | EECP | 4 | The make and model number and a copy of the customer receipt must be submitted with the application. | Yes | Receipt | Was a copy of the purchase receipt submitted? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Review the submitted documents in EECP | Ensure a copy of the receipt or invoice is included in the submitted documentation | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any | EECP | 5 | Good to have | Yes | Flow Rate | Flow Rate of Installed Unit (gpm) | Numeric Value | [8 empty] | QA Checklist | Use the manufacturer spec sheet to validate the flow rate of the newly installed unit | The flow rate listed in EECP should match what is on the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 33
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any | EECP | 6 | This measure is not applicable where recirculation pumps are used or where potential crossover between hot water and cold water may occur. | Yes | Recirculation Pump | Was the measure installed where recirculation pumps are used or where potential crossover between hot water and cold water may occur? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | Inspections | In the hot water piping system, near the water heater, document if there is a small pump that runs when the demand for water is off or zero | There should be only a small pump that is off unless there is a demand for hot water; a photograph of the hot water pump make and model number can also suffice | QA Checklist | Use the make and model of the hot water pump to determine if it is a recirculation pump or an on demand pump | The pump type should not be circulation or recirculation |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any | EECP | 7 | The measure is not applicable where tankless water heaters are used; instantaneous tankless water heaters may have different effect on savings with temperature-initiated flow-restriction valves. | Yes | Tankless | Does the facility utilize tankless water heaters? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | Inspections | Locate and photograph the water heater serving the domestic hot water systems (showers, faucets, etc.) | Ensure the water heater is not a tankless water heater (typically installed on a wall inside/outside of the garage) | QA Checklist | The make and model of the water heater may be provided in an installation report; the water heater type should not be instantaneous or tankless | The water heater type should not be instantaneous or tankless |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any | EECP | 8 | Measure Description | Yes | Natural Gas WH | Does the facility utilize natural gas water heating equipment? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Photograph the water heater showing the gas pipe (yellow pipe) going into the water heater | Determine if the water heater is fueled by natural gas (yellow pipe); the nameplate showing the make and model will also suffice | QA Checklist | The make and model of the water heater may be provided in an installation report | the water heater type should not be instantaneous or tankless |  | 2021-06-21 | Kenny Liljestrom |  | Add | 62
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any | EECP | 9 | The measure is not applicable where the showerhead is installed in tub/shower combination systems. (However, note that the gross savings installation adjustment (GSIA) factor accounts for expected leakage. See Gross Savings Installation Adjustment.) | Yes |  | Is the showerhead is installed in tub/shower combination system? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | Inspections | Photograph the shower the thermostatic valve is installed in | The shower should not be a shower/tub combo | QA Checklist | Photographs from the implementer showing the configuration of the shower will show what type of shower the equipment is installed in | The shower should not be a shower/tub combo | Revisit | 2021-08-25 | Kenny Liljestrom |  | Add | 64
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any | EECP | 1 | - | No | Manufacturer | Manufacturer | Text Box | [8 empty] | - | - | - | - | - | - |  | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 12
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any | EECP | 2 | - | No | Model | Model | Text Box | [8 empty] | - | - | - | - | - | - |  | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 5
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any | EECP | 3 | - | No | LFR Served By Gas | Is the installed LFR served by natural gas water heating equipment? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - |  | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 67
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any | EECP | 4 | - | No | Existing Flow Rate | Existing flow rate (gpm) | Numeric Value | [8 empty] | - | - | - | - | - | - |  | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 24
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any | EECP | 5 | - | No | Flow Rate | Flow rate of installed unit (gpm) | Numeric Value | [8 empty] | - | - | - | - | - | - |  | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 33
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any | EECP | 6 | Eligibility requirements for the laminar flow restrictor measure include: • The device must be installed only in health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation/inspection requirements. • The device must meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation. • The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | No | LFR Labeled Vandal | Is the LFR labeled as “Vandal Proof” or can not be removed without a proprietary tool, except for dialysis and scrub sink locations? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - |  | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 132
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any | EECP | 7 | Eligibility requirements for the laminar flow restrictor measure include: • The device must be installed only in health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation/inspection requirements. • The device must meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation. • The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | No | Meets Code | Does the installed device meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - |  | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 115
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any | QA Checklist | 8 | Eligibility requirements for the laminar flow restrictor measure include: • The device must be installed only in health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation/inspection requirements. • The device must meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation. • The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | No |  | Is the device installed in a health care facility subject to the OSHPD code and regulation/inspection requirements? | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 115
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any | QA Checklist | 9 | Eligible building types for this measure are health care facilities and/or medical buildings of any vintage that adhere to the Office of Statewide Health Planning and Development (OSHPD) regulations in the State of California that also utilize natural gas-powered water heating equipment. These facilities include (but are not limited to): • Hospitals (large regional or local) • Emergency rooms • In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals • Doctor offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.) • Clinics and nursing homes | No |  | Is the facility: • Hospitals (large regional or local) • Emergency rooms • In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals • Doctor offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.) • Clinics and nursing homes | Drop Down List | Yes;No | [6 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 315
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any | QA Checklist | 10 | New construction health care facilities are not eligible. | No |  | New Construction | Drop Down List | Yes;No | [6 empty] | Must be No | - | - | - | - | - | - | Not configured in original upload | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 16
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 12
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 5
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any | EECP | 3 | Savings limited to gas fired water heaters only | Yes | LFR Served By Gas | Is the installed LFR served by natural gas water heating equipment? | Drop Down List | Yes;No | [6 empty] | Must be Yes | Inspections | Photograph the water heater showing the gas pipe (yellow pipe) going into the water heater | Determine if the water heater is fueled by natural gas (yellow pipe); the nameplate showing the make and model will also suffice | QA Checklist | The make and model of the water heater may be provided in an installation report | the water heater type should not be instantaneous or tankless |  | 2021-07-12 | Kenny Liljestrom |  | Add | 67
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any | EECP | 4 | good to have | Yes | Existing Flow Rate | Existing flow rate (gpm) | Numeric Value | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Can probably remove with measure case descriptions and QA checks | 2021-07-12 | Kenny Liljestrom |  | Add | 24
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any | EECP | 5 | Measure Description | Yes | Flow Rate | Flow rate of installed unit (gpm) | Numeric Value | [8 empty] | QA Checklist | Use the manufacturer spec sheet to validate the flow rate of the newly installed unit | The flow rate listed in EECP should match what is on the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Can probably remove with measure case descriptions and QA checks | 2021-07-12 | Kenny Liljestrom |  | Add | 33
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any | EECP | 6 | Eligibility requirements for the laminar flow restrictor measure include: • The device must be installed only in health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation/inspection requirements. • The device must meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation. • The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | Yes | LFR Labeled Vandal | Is the LFR labeled as “Vandal Proof” or can not be removed without a proprietary tool, except for dialysis and scrub sink locations? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Use the manufacturer spec sheet to determine if the unit is identified as a Vandal Proof model or requires a specialty tool to remove | The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 132
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any | EECP | 7 | Eligibility requirements for the laminar flow restrictor measure include: • The device must be installed only in health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation/inspection requirements. • The device must meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation. • The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | Yes | Meets Code | Does the installed device meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-07-12 | Kenny Liljestrom |  | Add | 115
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any | QA Checklist | 9 | Eligible building types for this measure are health care facilities and/or medical buildings of any vintage that adhere to the Office of Statewide Health Planning and Development (OSHPD) regulations in the State of California that also utilize natural gas-powered water heating equipment. These facilities include (but are not limited to): • Hospitals (large regional or local) • Emergency rooms • In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals • Doctor offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.) • Clinics and nursing homes | Yes |  | Is the facility: • Hospitals (large regional or local) • Emergency rooms • In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals • Doctor offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.) • Clinics and nursing homes | Drop Down List | Yes;No | [6 empty] | Must be Yes | Inspections | Make note of the building type at the inspection site | The facility must be one of the following: • Hospitals (large regional or local) • Emergency rooms • In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals • Doctor offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.) • Clinics and nursing homes | QA Checklist | Use the installation report or EECP to determine the building type | Is the facility: • Hospitals (large regional or local) • Emergency rooms • In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals • Doctor offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.) • Clinics and nursing homes | Not configured in original upload | 2021-07-12 | Kenny Liljestrom |  | Add | 315
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any | QA Checklist | 10 | New construction health care facilities are not eligible. | Yes |  | New Construction | Drop Down List | Yes;No | [6 empty] | Must be No | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-12 | Kenny Liljestrom |  | Add | 16
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-12 | Kenny Liljestrom |  | Add | 12
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-12 | Kenny Liljestrom |  | Add | 5
1 | SWWH005 | 3 | Boiler, Commercial | Any | AR | Any | EECP | 3 | For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers, Customer/site information, Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating | Yes |  | Has all Preponderance of Evidence (POE) been included as defined in the workpaper? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Review the submitted documentation for Preponderance of Evidence (POE) | For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers, Customer/site information, Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-12 | Kenny Liljestrom |  | Add | 82
1 | SWWH005 | 3 | Boiler, Commercial | Any | AR | Any | EECP | 5 | Good to have | No |  | Who was the party that filled out the POE documentation? | Drop Down List | Tenant;Owner;Owner Representative;Implementer; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-10-20 | Kenny Liljestrom | Implementers responsible for POE documentation | Add | 56
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any | EECP | 6 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description and must comply with emission limits per air district, if applicable. Note that Tier 2 & 3 hot water heaters are condensing and often require flue modifications to handle the condensate. • Only gas-for-gas replacement installations are eligible. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use. • Have an input rating of at least 4,000 Btu/hr/gal of stored water. | Yes | Emission Limits Boiler | Does the boiler installation comply with emission limits per air district, if applicable? (Note that Tier 2 hot water heaters are condensing and often require flue modifications to handle the condensate.) | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-05-28 | Kenny Liljestrom |  | Add | 204
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any | EECP | 7 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description and must comply with emission limits per air district, if applicable. Note that Tier 2 & 3 hot water heaters are condensing and often require flue modifications to handle the condensate. • Only gas-for-gas replacement installations are eligible. Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use. • Have an input rating of at least 4,000 Btu/hr/gal of stored water. | Yes | Replacing Gas_Gas | Replacing gas unit with gas unit? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | The installation report should indicate the existing conditions including the fuel type of the existing boiler | The existing and proposed boilers must be fueled by natural gas | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-05-28 | Kenny Liljestrom |  | Add | 33
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any | EECP | 8 | This measure does not include water heaters or hot water boilers used for space conditioning, industrial (process) end-use applications, pools, or spas. | Yes | Boiler Use | Is the hot water boiler used for space conditioning, industrial (process) end-use applications, pools, or spas? | Drop Down List | Yes;No | [6 empty] | Must be No | Inspections | While on site, ask the customer if this boiler is used for domestic hot water or for service (HVAC) hot water | The boiler must be used for domestic hot water (showerheads, faucets, etc.), not HVAC equipment or other processes | QA Checklist | The installation report should indicate what equipment the hot water boiler serves | The hot water boiler must serve the domestic hot water load at the facility (showers, faucets, etc.); the boiler can NOT serve HVAC systems or manufacturing processes |  | 2021-05-28 | Kenny Liljestrom | Moved to FAI to check by inspections team | Add | 111
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any | EECP | 10 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description and must comply with emission limits per air district, if applicable. Note that Tier 2 & 3 hot water heaters are condensing and often require flue modifications to handle the condensate. • Only gas-for-gas replacement installations are eligible. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use. • Have an input rating of at least 4,000 Btu/hr/gal of stored water. | Yes |  | Does the installed unit only provide hot water when there is a hot water draw from the end use? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-05-28 | Kenny Liljestrom | Moved to FAI to check by inspections team | Add | 95
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any | EECP | 11 | This measure cannot be used to supply hot water to a circulation loop without an intermediary hot water storage tank. | Yes | Circulation Loop | Does the boiler supply hot water to a circulation loop without an intermediary hot water storage tank? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-05-28 | Kenny Liljestrom |  | Add | 102
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any | EECP | 12 | Good to have | Yes | Size | Size (kBtu/hr) | Numeric Value | [8 empty] | Inspections | Photograph the nameplate showing the Input Rating (Btu/hr) of the unit | The Input Rating (Btu/hr) listed in EECP should match what is listed on the nameplate; to convert from Btu/hr to kBtu/hr use the following formula: Input Rating (Btu/hr) / 1,000 (Btu/kBtu) = Input Rating (kBtu/hr) | QA Checklist | Use the manufacturer spec sheet to validate the Input Rating (Btu/hr) | The Input Rating (Btu/hr) listed in EECP should match what is listed on the spec sheet; to convert from Btu/hr to kBtu/hr use the following formula: Input Rating (Btu/hr) / 1,000 (Btu/kBtu) = Input Rating (kBtu/hr) | Remove validation criteria | 2021-07-12 | Kenny Liljestrom |  | Add | 14
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any | EECP | 13 | Good to have | Yes | Energy Factor | Uniform Energy Factor | Numeric Value | [8 empty] | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor (UEF) | The UEF listed in EECP should match what is listed on the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Remove validation criteria | 2021-07-12 | Kenny Liljestrom |  | Add | 21
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any | EECP | 14 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description and must comply with emission limits per air district, if applicable. Note that Tier 2 & 3 hot water heaters are condensing and often require flue modifications to handle the condensate. • Only gas-for-gas replacement installations are eligible. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use. • Have an input rating of at least 4,000 Btu/hr/gal of stored water. | Yes | Input Rating | Input Rating (btu/hr/gallon of stored water) | Numeric Value | [7 empty] | Must be >=4000 | QA Checklist | Use the manufacturer spec sheet to validate the Input Rating (Btu/hr-gallon) | The Input Rating (Btu/hr-gallon) listed in EECP should match what is listed on the spec sheet; if not listed, the value can be calculated as: Input Rating (Btu/hr) / Storage Capacity (gallons) = Input Rating (Btu/hr-gallon) This value needs to be >= 4,000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Validation criteria needs to be updated to reflect the >= 4000 requirement | 2021-07-12 | Kenny Liljestrom |  | Add | 44
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-12 | Kenny Liljestrom |  | Add | 12
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-12 | Kenny Liljestrom |  | Add | 5
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | AR | Any | EECP | 3 | To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. | Yes |  | Was the customer approached directly by a direct installation implementer? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-12 | Kenny Liljestrom |  | Add | 74
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | AR | Any | EECP | 4 | For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. | Yes |  | Has all Preponderance of Evidence (POE) been submitted as defined by the workpaper? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Review the submitted documentation in EECP for POE | For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-12 | Kenny Liljestrom |  | Add | 83
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | AR | Any | EECP | 5 | Good to have | No |  | Who was the party that filled out the POE documentation? | Drop Down List | Tenant;Owner;Owner Representative;Implementer; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-10-20 | Kenny Liljestrom | Implementers responsible for POE documentation | Add | 56
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | A | Any | Any | EECP | 6 | Measure Description | Yes | Energy Factor | Uniform Energy Factor | Numeric Value | [7 empty] | Must be >= 0.81 | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor | The Uniform Energy Factor Must be >= 0.81 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 21
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | B | Any | Any | EECP | 7 | Measure Description | Yes | Energy Factor | Uniform Energy Factor | Numeric Value | [7 empty] | Must be >= 0.87 | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor | The Uniform Energy Factor Must be >= 0.87 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 21
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | C | Any | Any | EECP | 8 | Measure Description | Yes | EFFICIENCY | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 0.80% | QA Checklist | Use the manufacturer spec sheet to validate the Thermal Efficiency (%) | The Thermal Efficiency (%) Must be >= 0.80% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 22
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | D | Any | Any | EECP | 9 | Measure Description | Yes | EFFICIENCY | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 0.90% | QA Checklist | Use the manufacturer spec sheet to validate the Thermal Efficiency (%) | The Thermal Efficiency (%) Must be >= 0.90% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 22
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | E | Any | Any | EECP | 10 | Measure Description | Yes | EFFICIENCY | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 0.90% | QA Checklist | Use the manufacturer spec sheet to validate the Thermal Efficiency (%) | The Thermal Efficiency (%) Must be >= 0.90% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 22
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | F | Any | Any | EECP | 11 | Measure Description | Yes | EFFICIENCY | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 0.96% | QA Checklist | Use the manufacturer spec sheet to validate the Thermal Efficiency (%) | The Thermal Efficiency (%) Must be >= 0.96% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 22
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | Any | Any | EECP | 12 | Measure Description | Yes | Size | Size (kBtu/hr) | Numeric Value | [8 empty] | Inspections | Photograph the nameplate showing the Input Rating (Btu/hr) of the unit | The Input Rating (Btu/hr) listed in EECP should match what is listed on the nameplate; to convert from Btu/hr to kBtu/hr use the following formula: Input Rating (Btu/hr) / 1,000 (Btu/kBtu) = Input Rating (kBtu/hr) | QA Checklist | Use the manufacturer spec sheet to validate the Input Rating (Btu/hr) | The Input Rating (Btu/hr) listed in EECP should match what is listed on the spec sheet; to convert from Btu/hr to kBtu/hr use the following formula: Input Rating (Btu/hr) / 1,000 (Btu/kBtu) = Input Rating (kBtu/hr) |  | 2021-07-12 | Kenny Liljestrom |  | Add | 14
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | NR | Any | EECP | 13 | For normal replacement (NR) measure application type, only gas-for-gas replacements are eligible | Yes | Replacing Gas_Gas | Replacing gas unit with gas unit? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | The installation report should indicate the existing conditions including the fuel type of the existing boiler | The existing and proposed boilers must be fueled by natural gas | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 33
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | Any | Any | EECP | 14 | Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use • Have an input rating of at least 4,000 Btu/hr per gallon of stored water | Yes | Input Rating | Input Rating (btu/hr/gallon of stored water) | Numeric Value | [7 empty] | Must be >= 4000 | QA Checklist | Use the manufacturer spec sheet to validate the Input Rating (Btu/hr-gallon) | The Input Rating (Btu/hr-gallon) listed in EECP should match what is listed on the spec sheet; if not listed, the value can be calculated as: Input Rating (Btu/hr) / Storage Capacity (gallons) = Input Rating (Btu/hr-gallon) This value needs to be >= 4,000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 44
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | Any | Any | EECP | 15 | Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use • Have an input rating of at least 4,000 Btu/hr per gallon of stored water | Yes |  | Does the installed unit only provide hot water when there is a hot water draw from the end use? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-12 | Kenny Liljestrom |  | Add | 95
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | Any | Any | EECP | 16 | Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use • Have an input rating of at least 4,000 Btu/hr per gallon of stored water This measure does not include water heaters or hot water boilers used for space conditioning, industrial (process) end-use applications, pools, or spas. | Yes | Primary Use Domestic Water | Primarily used for domestic water? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | While on site, ask the customer if this boiler is used for domestic hot water or for service (HVAC) hot water | The boiler must be used for domestic hot water (showerheads, faucets, etc.), not HVAC equipment or other processes | QA Checklist | The installation report should indicate what equipment the hot water boiler serves | The hot water boiler must serve the domestic hot water load at the facility (showers, faucets, etc.); the boiler can NOT serve HVAC systems or manufacturing processes | Not configured in original upload | 2021-05-28 | Kenny Liljestrom |  | Add | 34
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | AR | Any | EECP | 17 | This measure cannot be used to supply hot water to a circulation loop without an intermediary hot water storage tank. | Yes |  | For hot water circulation loops, is there an intermediary hot water storage tank? | Drop Down List | Yes;No;N/A; | [6 empty] | Must be: Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-05-28 | Kenny Liljestrom |  | Add | 81
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | Any | Any | EECP | 18 | - | Yes | Market Cost | Market Cost | Formula | [8 empty] | - | - | - | - | - | - | Remove if legacy (not used in programs) | 2021-08-25 | Kenny Liljestrom |  | Add | 11
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-19 | Kenny Liljestrom |  | Add | 12
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-19 | Kenny Liljestrom |  | Add | 5
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | AR | Any | EECP | 3 | For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers, Customer/site information, Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating | Yes |  | Has all Preponderance of Evidence (POE) been submitted as defined by the workpaper? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Review the submitted documentation in EECP for POE | For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers, Customer/site information, Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 83
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | AR | Any | EECP | 5 | Good to have | No |  | Who was the party that filled out the POE documentation? | Drop Down List | Tenant;Owner;Owner Representative;Implementer; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-10-20 | Kenny Liljestrom | Implementers responsible for POE documentation | Add | 56
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | NR | Any | EECP | 6 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes | Replacing Gas_Gas | Replacing gas unit with gas unit? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | The installation report should indicate the existing conditions including the fuel type of the existing boiler | The existing and proposed boilers must be fueled by natural gas | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 33
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | Any | Any | EECP | 7 | Water heaters or hot water boilers used for space conditioning, industrial (process) end-use applications, pools, or spas are not eligible. | Yes |  | Installed in a commercial domestic (or “service”) hot water application in a NonRes facility? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 93
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | Any | Any | EECP | 8 | Good to have | Yes |  | Cap-kBtuh | Numeric Value | [8 empty] | Inspections | Photograph the nameplate showing the Input Rating (Btu/hr) of the unit | The Input Rating (Btu/hr) listed in EECP should match what is listed on the nameplate; to convert from Btu/hr to kBtu/hr use the following formula: Input Rating (Btu/hr) / 1,000 (Btu/kBtu) = Input Rating (kBtu/hr) | QA Checklist | Use the manufacturer spec sheet to validate the Input Rating (Btu/hr) | The Input Rating (Btu/hr) listed in EECP should match what is listed on the spec sheet; to convert from Btu/hr to kBtu/hr use the following formula: Input Rating (Btu/hr) / 1,000 (Btu/kBtu) = Input Rating (kBtu/hr) | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 9
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | Any | Any | EECP | 9 | Good to have | Yes |  | Size (gallons) | Numeric Value | [8 empty] | Inspections | Photograph the nameplate showing the Storage Capacity or Volume (gallons) of the unit | The Storage Capacity or Volume (gallons) listed in EECP should match what is listed on the nameplate | QA Checklist | Use the manufacturer spec sheet to validate the Storage Capacity or Volume (gallons) | The Storage Capacity or Volume (gallons) listed in EECP should match what is listed on the spec sheet | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 14
1 | SWWH007 | 4 | Storage Water Heater, Commercial | A | Any | Any | EECP | 10 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Uniform Energy Factor (UEF) | Numeric Value | [7 empty] | Must be >= 0.68 | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor (UEF) | The Uniform Energy Factor (UEF) Must be >= 0.68 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 27
1 | SWWH007 | 4 | Storage Water Heater, Commercial | B | Any | Any | EECP | 11 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Uniform Energy Factor (UEF) | Numeric Value | [7 empty] | Must be >= 0.64 | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor (UEF) | The Uniform Energy Factor (UEF) Must be >= 0.64 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 27
1 | SWWH007 | 4 | Storage Water Heater, Commercial | C | Any | Any | EECP | 12 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Uniform Energy Factor (UEF) | Numeric Value | [7 empty] | Must be >= 0.68 | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor (UEF) | The Uniform Energy Factor (UEF) Must be >= 0.68 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 27
1 | SWWH007 | 4 | Storage Water Heater, Commercial | D | Any | Any | EECP | 13 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Uniform Energy Factor (UEF) | Numeric Value | [7 empty] | Must be >= 0.64 | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor (UEF) | The Uniform Energy Factor (UEF) Must be >= 0.64 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 27
1 | SWWH007 | 4 | Storage Water Heater, Commercial | E | Any | Any | EECP | 14 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Uniform Energy Factor (UEF) | Numeric Value | [7 empty] | Must be >= 0.68 | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor (UEF) | The Uniform Energy Factor (UEF) Must be >= 0.68 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 27
1 | SWWH007 | 4 | Storage Water Heater, Commercial | F | Any | Any | EECP | 15 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Uniform Energy Factor (UEF) | Numeric Value | [7 empty] | Must be >= 0.64 | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor (UEF) | The Uniform Energy Factor (UEF) Must be >= 0.64 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 27
1 | SWWH007 | 4 | Storage Water Heater, Commercial | G | Any | Any | EECP | 16 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 83% | QA Checklist | Use the manufacturer spec sheet to validate the Thermal Efficiency (%) | The Thermal Efficiency (%) Must be >= 83% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 22
1 | SWWH007 | 4 | Storage Water Heater, Commercial | H | Any | Any | EECP | 17 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 90% | QA Checklist | Use the manufacturer spec sheet to validate the Thermal Efficiency (%) | The Thermal Efficiency (%) Must be >= 90% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 22
1 | SWWH007 | 4 | Storage Water Heater, Commercial | I | Any | Any | EECP | 18 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Thermal Efficiency (%) | Numeric Value | [7 empty] | Must be >= 96% | QA Checklist | Use the manufacturer spec sheet to validate the Thermal Efficiency (%) | The Thermal Efficiency (%) Must be >= 96% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 22
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | Any | Any | EECP | 19 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes | Input Rating | Input Rating (btu/hr/gallon) | Numeric Value | [7 empty] | Must be <=4000 | QA Checklist | Use the manufacturer spec sheet to validate the Input Rating (Btu/hr-gallon) | The Input Rating (Btu/hr-gallon) listed in EECP should match what is listed on the spec sheet; if not listed, the value can be calculated as: Input Rating (Btu/hr) / Storage Capacity (gallons) = Input Rating (Btu/hr-gallon) This value needs to be <= 4,000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-19 | Kenny Liljestrom |  | Add | 28
0 | SWWH008 | 1 | Boiler, Process | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-19 | Kenny Liljestrom |  | Add | 12
0 | SWWH008 | 1 | Boiler, Process | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-19 | Kenny Liljestrom |  | Add | 5
0 | SWWH008 | 1 | Boiler, Process | A | Any | Any | EECP | 3 | Water boilers must have an input rating ≤ 200,000 kBtu/hr. The combustion efficiency must have a documented combustion efficiency of 85% or greater under full load conditions. Steam boilers must have an input rating ≤ 200,000 kBtu/hr. The combustion efficiency must have a documented combustion efficiency of 83% or greater under full load conditions. | Yes | EFFICIENCY | Combustion Efficiency (%) | Numeric Value | [7 empty] | Must be >= 85% | QA Checklist | Use the manufacturer spec sheet to validate the Combustion Efficiency (%) | The Combustion Efficiency (%) Must be >= 85% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Only configured for a single implementation, needs to be expanded across all SWWH008 implementations | 2021-07-19 | Kenny Liljestrom |  | Add | 25
0 | SWWH008 | 1 | Boiler, Process | B | Any | Any | EECP | 4 | Water boilers must have an input rating ≤ 200,000 kBtu/hr. The combustion efficiency must have a documented combustion efficiency of 85% or greater under full load conditions. Steam boilers must have an input rating ≤ 200,000 kBtu/hr. The combustion efficiency must have a documented combustion efficiency of 83% or greater under full load conditions. | Yes | EFFICIENCY | Combustion Efficiency (%) | Numeric Value | [7 empty] | Must be >= 90% | QA Checklist | Use the manufacturer spec sheet to validate the Combustion Efficiency (%) | The Combustion Efficiency (%) Must be >= 90% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Only configured for a single implementation, needs to be expanded across all SWWH008 implementations (A, B, C), Update property label and validation to account for % | 2021-07-19 | Kenny Liljestrom |  | Add | 25
0 | SWWH008 | 1 | Boiler, Process | C | Any | Any | EECP | 5 | Water boilers must have an input rating ≤ 200,000 kBtu/hr. The combustion efficiency must have a documented combustion efficiency of 85% or greater under full load conditions. Steam boilers must have an input rating ≤ 200,000 kBtu/hr. The combustion efficiency must have a documented combustion efficiency of 83% or greater under full load conditions. | Yes | EFFICIENCY | Combustion Efficiency (%) | Numeric Value | [7 empty] | Must be >= 83% | QA Checklist | Use the manufacturer spec sheet to validate the Combustion Efficiency (%) | The Combustion Efficiency (%) Must be >= 83% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Only configured for a single implementation, needs to be expanded across all SWWH008 implementations (A, B, C) | 2021-07-19 | Kenny Liljestrom |  | Add | 25
0 | SWWH008 | 1 | Boiler, Process | Any | Any | Any | EECP | 6 | Good to have | Yes |  | Size ( kBtu/hr) | Numeric Value | [7 empty] | Must be <=20000 | Inspections | Photograph the nameplate showing the Input Rating (Btu/hr) of the unit | The Input Rating (Btu/hr) listed in EECP should match what is listed on the nameplate; to convert from Btu/hr to kBtu/hr use the following formula: Input Rating (Btu/hr) / 1,000 (Btu/kBtu) = Input Rating (kBtu/hr) The value must be <= 20,000 kBtu/hr | QA Checklist | Use the manufacturer spec sheet to validate the Input Rating (Btu/hr) | The Input Rating (Btu/hr) listed in EECP should match what is listed on the spec sheet; to convert from Btu/hr to kBtu/hr use the following formula: Input Rating (Btu/hr) / 1,000 (Btu/kBtu) = Input Rating (kBtu/hr) The value must be <= 20,000 kBtu/hr | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 15
0 | SWWH008 | 1 | Boiler, Process | Any | Any | Any | EECP | 7 | This measure is not applicable to boilers used for space heating, domestic hot water, pools, or spas, and is not eligible for domestic hot water or space heating. | Yes | Boiler Use | Is the boiler used for space heating, domestic hot water, pools, or spas? | Drop Down List | Yes;No; | [6 empty] | Must be No | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-07-19 | Kenny Liljestrom |  | Add | 74
0 | SWWH008 | 1 | Boiler, Process | Any | Any | Any | EECP | 8 | This measure is not eligible for new construction installations. | Yes |  | Is this measure being installed on a new construction project? | Drop Down List | Yes;No; | [6 empty] | Must be No | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 62
0 | SWWH008 | 1 | Boiler, Process | Any | Any | Any | EECP | 9 | Eligible building types include all existing commercial, agriculture, and industrial (nonresidential) buildings of any vintage. This measure is available to industrial end-use customers that manufacture a saleable product, typically (but not limited to) NAICS codes 31, 32, and 33. | Yes |  | Installed in a NAICS code 31, 31, or 33? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | Use the NAICS database to determine if the building type is considered to be in building types beginning with 31, 32, or 33 | This measure is available to industrial end-use customers that manufacture a saleable product, typically (but not limited to) NAICS codes 31, 32, and 33. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 40
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | UpDeemed | EECP | 0 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 7
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | UpDeemed | EECP | 5 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 12
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | Any | EECP | 10 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 12
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | Any | EECP | 15 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 5
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | UpDeemed | EECP | 20 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 13
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | Any | EECP | 25 | Only gas-for-gas normal replacements or for new construction installations are eligible. Normal replacements must replace a storage water heater with another storage water heater. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | AR | Any | EECP | 30 | Only storage water heaters as defined by the California Energy Commission qualify, and they must: Be used primarily for domestic hot water. Water heaters used for space conditioning, process end use applications, pools or spas are not eligible. | Yes | Primary Use Domestic Water | Water heater is primarily used for domestic hot water, not for space conditioning, pools or spas? | Drop Down List | Yes;No | Equal | Yes |  |  |  |  | Must be Yes | Inspections | Ask the customer if the water heater is used primarily for domestic hot water (i.e. not connected to the HVAC system) | The domestic water heater should be used primarily for hot water loads such as showers and faucets | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  | Add | 97
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | Any | EECP | 35 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). “Storage water heater” means a water heater that heats and stores water within the appliance at a thermostatically-controlled temperature for delivery on demand, and that has an input less than 4,000 Btu/hr/gal of stored water. | Yes | Input Rating | Input rating (kBtu/hr) | Numeric Value |  |  |  | General | 0 | 75 | 1 | Must be < = 75 | Inspections | Photograph the equipment nameplate to capture the input capacity (Btu/hr) | The listed input capacity in EECP should match the nameplate by using the following conversion: kBtu/hr = Btu/hr / 1,000 | QA Checklist | Review the manufacturer specficiation sheet to check for the input capacity (Btu/hr) of the installed equipment | The listed input capacity in EECP should match the nameplate by using the following conversion: kBtu/hr = Btu/hr / 1,000 |  | 2022-06-13 | Kenny Liljestrom |  |  | 22
1 | SWWH012 | 2 | Storage Water Heater, Residential | E | Any | Any | EECP | 40 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  | General | 30 | 39.9 | 1 | Must be between 30 - 39.9 | Inspections | Photograph the equipment nameplate to capture the storage capacity (gallons) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the manufacturer specficiation sheet to check for the storage capacity (gallons) of the installed equipment | The equipment in EECP should have a storage capacity (gallons) that matches EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | F | Any | Any | EECP | 40 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  | General | 40 | 49.9 | 1 | Must be between 40 - 49.9 | Inspections | Photograph the equipment nameplate to capture the storage capacity (gallons) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the manufacturer specficiation sheet to check for the storage capacity (gallons) of the installed equipment | The equipment in EECP should have a storage capacity (gallons) that matches EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | G | Any | Any | EECP | 40 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  | General | 40 | 49.9 | 1 | Must be between 40 - 49.9 | Inspections | Photograph the equipment nameplate to capture the storage capacity (gallons) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the manufacturer specficiation sheet to check for the storage capacity (gallons) of the installed equipment | The equipment in EECP should have a storage capacity (gallons) that matches EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | H | Any | Any | EECP | 40 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  | General | 50 | 59.9 | 1 | Must be between 50 - 59.9 | Inspections | Photograph the equipment nameplate to capture the storage capacity (gallons) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the manufacturer specficiation sheet to check for the storage capacity (gallons) of the installed equipment | The equipment in EECP should have a storage capacity (gallons) that matches EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | I | Any | Any | EECP | 40 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  | General | 50 | 59.9 | 1 | Must be between 50 - 59.9 | Inspections | Photograph the equipment nameplate to capture the storage capacity (gallons) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the manufacturer specficiation sheet to check for the storage capacity (gallons) of the installed equipment | The equipment in EECP should have a storage capacity (gallons) that matches EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | J | Any | Any | EECP | 40 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  | General | 30 | 39.9 | 1 | Must be between 30 - 39.9 | Inspections | Photograph the equipment nameplate to capture the storage capacity (gallons) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the manufacturer specficiation sheet to check for the storage capacity (gallons) of the installed equipment | The equipment in EECP should have a storage capacity (gallons) that matches EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | K | Any | Any | EECP | 40 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  | General | 40 | 49.9 | 1 | Must be between 40 - 49.9 | Inspections | Photograph the equipment nameplate to capture the storage capacity (gallons) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the manufacturer specficiation sheet to check for the storage capacity (gallons) of the installed equipment | The equipment in EECP should have a storage capacity (gallons) that matches EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | L | Any | Any | EECP | 40 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  | General | 50 | 59.9 | 1 | Must be between 50 - 59.9 | Inspections | Photograph the equipment nameplate to capture the storage capacity (gallons) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the manufacturer specficiation sheet to check for the storage capacity (gallons) of the installed equipment | The equipment in EECP should have a storage capacity (gallons) that matches EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | E | Any | Any | EECP | 45 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 0.64 | 5 | 2 | Must be <= 0.64 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH012 | 2 | Storage Water Heater, Residential | F | Any | Any | EECP | 45 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 0.64 | 5 | 2 | Must be <= 0.64 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH012 | 2 | Storage Water Heater, Residential | G | Any | Any | EECP | 45 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 0.68 | 5 | 2 | Must be <= 0.68 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH012 | 2 | Storage Water Heater, Residential | H | Any | Any | EECP | 45 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 0.64 | 5 | 2 | Must be <= 0.64 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH012 | 2 | Storage Water Heater, Residential | I | Any | Any | EECP | 45 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 0.68 | 5 | 2 | Must be <= 0.68 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH012 | 2 | Storage Water Heater, Residential | J | Any | Any | EECP | 45 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 0.68 | 5 | 2 | Must be <= 0.68 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH012 | 2 | Storage Water Heater, Residential | K | Any | Any | EECP | 45 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 0.83 | 5 | 2 | Must be <= 0.83 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH012 | 2 | Storage Water Heater, Residential | L | Any | Any | EECP | 45 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 0.88 | 5 | 2 | Must be <= 0.88 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | UpDeemed | EECP | 190 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value |  |  |  | General |  |  | 0 |  | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 8
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | UpDeemed | EECP | 195 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 15
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | AR | Any | QA Checklist | 205 | For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: targeted segment of the market or customers, Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating | Yes | POE Docs | Have POE requirements in the measure package been included in uploaded documentation? | None | [8 empty] | QA Checklist | Review the POE documentation and determine if it is adequate based on required criteria. | The POE documentation needs to list the targeted segment of the market or customers, Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating or one of the three alternatives listed in Section 7.3 of POEV 2.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-06-13 | Kenny Liljestrom |  | Add | 85
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | Any | QA Checklist | 210 | If necessary, customer must provide proof of unit efficiency (e.g., manufacturer’s equipment specification sheet). | Yes | - | Has the manufacturer specification sheet been submitted to prove the equipment efficiency? | Drop Down List | Yes;No | Equal | Yes |  |  |  |  | Must be Yes | QA Checklist | Review the EECP submitted documentation for the manufacturer specification sheet | The submitted specification sheet should list the manufacturer and model number listed in EECP and verified by inspections | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  | Add | 90
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | Any | QA Checklist | 215 | Equipment must comply with the test methods referenced in the California Building Energy Efficiency Standards (Title 24) and the California Appliance Efficiency Regulations (Title 20). | No | - | Does the water heater meet all Title 24 and Title 20 testing methods? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom | There is no way to check for this if the product is not on a qualified products list. | Add | 69
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | Any | EECP | 220 | Additionally, the equipment must meet minimum emissions requirements as defined by local air quality management districts. See Code Requirements. | No | - | Water heater meet all emissions requirements as outlined by local air quality management districts? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom | This is difficult to prove, all water heaters on the market should qualify for this | Add | 99
0 | SWWH014 | 2 | Heat Pump Water Heater, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-20 | Kenny Liljestrom |  | Add | 12
0 | SWWH014 | 2 | Heat Pump Water Heater, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-20 | Kenny Liljestrom |  | Add | 5
0 | SWWH014 | 2 | Heat Pump Water Heater, Residential | Any | NC | Any | EECP | 3 | For new construction (NC), the baseline can be a gas-fired water heater. But, energy savings and measure cost are estimated and reported as the difference between the corresponding heat pump water heater and the baseline electric resistance water heater. (See also Base Case Description.) | Yes |  | What is the assumed baseline fuel type? | Drop Down List | Electric;Gas; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 39
0 | SWWH014 | 2 | Heat Pump Water Heater, Residential | Any | Any | Any | EECP | 4 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes |  | Is the installed equipment a residential-style electric storage water heater? | Drop Down List | Yes;No | [6 empty] | Must be Yes | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than or equal to 45-gallons | QA Checklist | Using the make and model, locate the equipment specifications and determine the equipment type, you may be able to do this with the EnergyStar database | The unit should not be listed as an “instantaneous” or “tankless” water heater | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 77
0 | SWWH014 | 2 | Heat Pump Water Heater, Residential | Any | Any | Any | EECP | 5 | A new heat pump water heater with storage capacity less than 45 gallons does not qualify. | Yes |  | Storage Capacity (gallons) | Numeric Value | [7 empty] | Must be >= 45 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than or equal to 45-gallons | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than or equal to 45-gallons and match what is listed in EECP | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | Any | Any | UpDeemed | EECP | 0 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 7
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | Any | Any | UpDeemed | EECP | 5 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 12
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | Any | Any | Any | EECP | 10 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 12
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | Any | Any | Any | EECP | 15 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 5
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | Any | Any | UpDeemed | EECP | 20 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 13
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | A | Any | Any | EECP | 25 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Instantaneous;Heat Pump;Electric Storage;Tankless; | Equal | Electric Storage |  |  |  |  | Must be 'Electric Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | B | Any | Any | EECP | 25 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Instantaneous;Heat Pump;Electric Storage;Tankless; | Equal | Electric Storage |  |  |  |  | Must be 'Electric Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | C | Any | Any | EECP | 25 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Instantaneous;Heat Pump;Electric Storage;Tankless; | Equal | Electric Storage |  |  |  |  | Must be 'Electric Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | D | Any | Any | EECP | 25 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Instantaneous;Heat Pump;Electric Storage;Tankless; | Equal | Electric Storage |  |  |  |  | Must be 'Electric Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | E | Any | Any | EECP | 25 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Instantaneous;Heat Pump;Electric Storage;Tankless; | Equal | Electric Storage |  |  |  |  | Must be 'Electric Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | F | Any | Any | EECP | 25 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Instantaneous;Heat Pump;Electric Storage;Tankless; | Equal | Electric Storage |  |  |  |  | Must be 'Electric Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | G | Any | Any | EECP | 25 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Instantaneous;Heat Pump;Electric Storage;Tankless; | Equal | Heat Pump |  |  |  |  | Must be 'Heat Pump' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | H | Any | Any | EECP | 25 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Instantaneous;Heat Pump;Electric Storage;Tankless; | Equal | Heat Pump |  |  |  |  | Must be 'Heat Pump' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | A | Any | Any | EECP | 30 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  | General | 45 | 55 | 0 | Must be >= 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | B | Any | Any | EECP | 30 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  | General | 45 | 55 | 0 | Must be >= 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | C | Any | Any | EECP | 30 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  | General | 45 | 55 | 0 | Must be >= 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | D | Any | Any | EECP | 30 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  | General | 45 | 55 | 0 | Must be >= 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | E | Any | Any | EECP | 30 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  | General | 45 | 55 | 0 | Must be >= 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | F | Any | Any | EECP | 30 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  | General | 45 | 55 | 0 | Must be >= 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | G | Any | Any | EECP | 30 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  | General | 56 | 75 | 0 | Must be > 55 and <= 75 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 55-gallons and less than or equal to 75-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 55-gallons and less than or equal to 75-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | H | Any | Any | EECP | 30 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  | General | 75 |  | 0 | Must be > 75 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 75-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 75-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | A | Any | Any | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | B | Any | Any | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | C | Any | Any | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | D | Any | Any | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | E | Any | Any | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | F | Any | Any | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | G | Any | Any | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.33 |  | 2 | Must be >= 3.33 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | H | Any | Any | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.42 |  | 2 | Must be >= 3.42 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | Any | Any | Any | EECP | 40 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | FHR | First Hour Rating (FHR) | Numeric Value |  |  |  | General | 0 |  | 0 | Must be > 0 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The First Hour Rating (FHR) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 23
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | Any | Any | UpDeemed | EECP | 190 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value |  |  |  | General |  |  | 0 |  | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 8
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | Any | Any | UpDeemed | EECP | 195 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 15
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | Any | Any | Any | EECP | 1 | - | Pending | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the controller nameplate to capture the manufacturer; the controller will most likely be mounted on or near the hot water boiler or tank | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-10-13 | Kenny Liljestrom |  |  | 12
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | Any | Any | Any | EECP | 2 | - | Pending | Model | Model | Text Box | [8 empty] | Inspections | Photograph the controller nameplate to capture the model number; the controller will most likely be mounted on or near the hot water boiler or tank | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-10-13 | Kenny Liljestrom |  |  | 5
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | A | Any | Any | EECP | 3 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | B | Any | Any | EECP | 4 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | C | Any | Any | EECP | 5 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | D | Any | Any | EECP | 6 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | E | Any | Any | EECP | 7 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | F | Any | Any | EECP | 8 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | G | Any | Any | EECP | 9 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | H | Any | Any | EECP | 10 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | I | Any | Any | EECP | 11 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | J | Any | Any | EECP | 12 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | K | Any | Any | EECP | 13 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | L | Any | Any | EECP | 14 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | M | Any | Any | EECP | 15 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | N | Any | Any | EECP | 16 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | O | Any | Any | EECP | 17 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | P | Any | Any | EECP | 18 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | Q | Any | Any | EECP | 19 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | R | Any | Any | EECP | 20 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | S | Any | Any | EECP | 21 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | T | Any | Any | EECP | 22 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [8 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | Any | Any | Any | EECP | 23 | This measure qualifies only for central hot-water systems used primarily for domestic hot-water heating. | Pending |  | Domestic hot water served by central system? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | Locate and photograph the domestic hot water heater system | The domestic hot water heater must be a centralized system; these can be identified typically by their locations which can be in mechanical equipment rooms, on the roof, or on the exterior of a building; central hot water systems are defined as units that serve an entire building, not individual or several units | QA Checklist | Use the installation report to determine the type of domestic hot water system at the facility | The domestic hot water heater must be a centralized system; these can be identified typically by their locations which can be in mechanical equipment rooms, on the roof, or on the exterior of a building; central hot water systems are defined as units that serve an entire building, not individual or several units |  | 2021-10-13 | Kenny Liljestrom |  |  | 44
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | Any | Any | Any | EECP | 24 | Central hot water systems with demand-controlled recirculation pump are not eligible. | Pending |  | Existing domestic hot water system had demand-controlled recirculation pump? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | QA Checklist | Use the installation report or photos of existing equipment to determine the recirculation pump controls | Existing systems must not already have demand-control recirculation pumps | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-10-13 | Kenny Liljestrom |  |  | 76
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | Any | Any | Any | EECP | 25 | Facilities that must maintain hot water temperature of 140°F to control Legionella bacteria are not eligible. Local, state, and federal regulations must be followed to avoid the risk of Legionella growth and scalding. | Pending |  | Domestic hot water loop temperature (F) | Numeric Value | [7 empty] | Must be >= 140 | Inspections | Photograph and record the loop temperature of the domestic hot water system | The hot water temperature must be greater than 140F | QA Checklist | Use the installation report to determine the hot water loop temperature (F) | The hot water temperature must be greater than 140F |  | 2021-10-13 | Kenny Liljestrom |  |  | 39
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | Any | Any | Any | QA Checklist | 26 | Data to be collected will include manufacturer and model numbers of controllers installed. Controller invoice amount and installation cost will be required to be collected to calibrate cost data. | Pending | Data Collection | Data to be collected will include manufacturer and model numbers of controllers installed. Controller invoice amount and installation cost will be required to be collected to calibrate cost data. | Text Box | [8 empty] | QA Checklist | Ensure all documentation has been uploaded by the implementer | Data to be collected will include manufacturer and model numbers of controllers installed. Invoice amount and installation cost will be required to be collected to calibrate cost data. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-10-13 | Kenny Liljestrom |  |  | 195
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 0 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 5 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | A | Any | Any | EECP | 10 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | B | Any | Any | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | C | Any | Any | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | J | Any | Any | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | K | Any | Any | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | L | Any | Any | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | S | Any | Any | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | T | Any | Any | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | U | Any | Any | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AB | Any | Any | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AC | Any | Any | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AD | Any | Any | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | D | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | E | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | F | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | G | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | H | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | I | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | M | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | N | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | O | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | P | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Q | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | R | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | V | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | W | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | X | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Y | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Z | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AA | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AE | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AF | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AG | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AH | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AI | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AJ | Any | Any | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [7 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 20 | The manufacturer specification sheet must be submitted with the application. | Yes | Manufacturer Cut Sheet Submitted | Insulation manufacturer specification sheet submitted with the application? | Drop Down List | Yes;No | Equal | Yes |  |  |  |  | Must be Yes | QA Checklist | Review the EECP submitted documentation for the manufacturer specification sheet | An insulation specification sheet should be included in the submitted documentation | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 75
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 25 | A minimum of one inch of pipe insulation must be added to existing bare commercial or industrial steel or copper pipe. | Yes | Pipe Insulation Added | At least 1-in of insulation added to existing bare commercial or industrial steel or copper pipe? | Drop Down List | Yes;No | Equal | Yes |  |  |  |  | Must be Yes | Inspections | Locate the insulated piping and look at the diameter of the bare pipe | The insulation thickness should be greater than or equal to 1-inch and the piping should be either copper or steel (i.e. not PVC or other materials) | QA Checklist | The make and model of the insulation should indicate on the manufacturer specification sheet the insulation thickness; a photograph of the piping system in an installation report may show the type of piping installed | The insulation thickness should be greater than or equal to 1-inch and the eligible types are piping include copper and steel |  | 2021-06-21 | Kenny Liljestrom |  | Add | 97
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 30 | The hours of operation must be indicated on the top of the application. | Yes | Hours of operation | Hours of operation of the hot water system | Numeric Value |  |  |  | General | 0 | 8760 | 0 | Must be <= 8760 | QA Checklist | The application form should indicate the hours of operation for the hot water system | No validation criteria | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 42
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 35 | The minimum qualifying pipe diameter is ½-inch. | Yes | Size | Pipe Diameter (in) | Numeric Value |  |  |  | General | 0.5 | 10 | 2 | Must be >= 0.5 in (1/2-in) | Inspections | Using a ruler or best judgement, estimate the diameter of the hot water piping and record the value | The value should match what is listed in EECP | QA Checklist | An installation report may show the piping diameter | Piping must be greater than 1/2-inch |  | 2022-03-15 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | D | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  | Add | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | E | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | F | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | G | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | H | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | I | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | M | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | N | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | O | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | P | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Q | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | R | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | V | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | W | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | X | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Y | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Z | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AA | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AE | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AF | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AG | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AH | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AI | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AJ | Any | Any | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 45 | The length of insulation to be installed with each pipe size must be indicated. | No | Length | Length of piping in linear feet | Numeric Value |  |  |  | General |  |  | 1 |  | Inspections | Using a measuring wheel or best estimate; measure the length (in feet) of the piping insulation | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report should indicate the length of the insulation installed | No validation criteria |  | 2021-06-21 | Kenny Liljestrom | This is captured with the measure quantity | Add | 31
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 45 | Insulation required by California Building Energy Efficiency Standards (Title 24) or employee safety laws (Occupational Safety and Health Administration, OSHA) is not eligible. | Yes | Title 24 | In the installed insulation required by California Building Energy Efficiency Standards (Title 24) or employee safety laws (Occupational Safety and Health Administration, OSHA)? | Drop Down List | Yes;No | Equal | Yes |  |  |  |  | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Property label should be updated to correct the front end: "Is the installed…" | 2021-06-21 | Kenny Liljestrom |  | Add | 177
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 50 | Replacement of damaged (existing) insulation is not eligible. | Yes | Existing Insulation | Does the piping have existing insulation that is damaged or being replaced? | Drop Down List | Yes;No | Equal | No |  |  |  |  | Must be No | Inspections | Photograph the piping system, indicate if there are any old glue marks, aged insulation, or mothballed insulation near or around the piping | There should be no signs of any previously installed insulation on the piping | QA Checklist | Photographs of the existing and installed measure conditions of the hot water piping | The existing piping should not have any insulation installed |  | 2021-06-21 | Kenny Liljestrom |  | Add | 75
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 1 | The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 2 | The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 3 | The tank must be coupled to gas-fired commercial, industrial, agriculture, or multifamily central equipment that transfers heat to the contained liquid or solution. | Yes | Coupled Tank | Is the tank that was insulated coupled to gas-fired commercial, industrial, or agriculture equipment that transfers heat to the contained liquid or solution? | Drop Down List | Yes;No | [6 empty] | Must be Yes | Inspections | Photograph the water heater and piping; ask the customer if the water heater is used for any purpose other than serving showerheads or faucets | Ensure the water heater is not serving any industrial process loads (heated water tanks, heat exchangers, etc.) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 157
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 4 | The following conditions and applications are not eligible: • Tanks with pre-existing insulation • Replacement of old or damaged insulation • Tanks insulated to prevent burns. • Insulation for exposed hot-water tanks within seven feet of the floor that are not otherwise guarded in such manner as to prevent contact. The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Existing Insulation | Does the tank have existing insulation (in any condition) or evidence of prior insulation being installed ? | Drop Down List | Yes;No | [6 empty] | Must be No | Inspections | Inspect the area around the water heater to look for any clues of previous insulation being installed | Ensure the tank doesn't show any evidence of prior insulation being installed such as: scattered insulation on the floor around the tank, old glue marks on the outside of the tank, pieces of old insulation still on the tank, etc.) | QA Checklist | Photographs of the existing and installed measure conditions of the hot water tank | No insulation should be installed on the existing water tank |  | 2021-06-21 | Kenny Liljestrom |  | Add | 107
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 5 | The following conditions and applications are not eligible: • Tanks with pre-existing insulation • Replacement of old or damaged insulation • Tanks insulated to prevent burns. • Insulation for exposed hot-water tanks within seven feet of the floor that are not otherwise guarded in such manner as to prevent contact. | Yes | Insulation Required to Prevent Burns | Is the insulation required to prevent burns or is the tank located where burns can be sustained? | Drop Down List | Yes;No | [6 empty] | Must be No | Inspections | Check if the tank is in an area with high traffic or located within arms reach of an uncovered walkway | Indicate whether or not the tank is in a location where it would be easy to sustain a burn by walking by, the tank should not be located in an easily accessible location where burns could be sustained from walking by | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 96
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 6 | The following conditions and applications are not eligible: • Tanks with pre-existing insulation • Replacement of old or damaged insulation • Tanks insulated to prevent burns. • Insulation for exposed hot-water tanks within seven feet of the floor that are not otherwise guarded in such manner as to prevent contact. The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Exposed Hot Water Tanks | Is the insulation for exposed hot-water tanks within seven feet of the floor that are not otherwise guarded in such manner as to prevent contact? | Drop Down List | Yes;No | [6 empty] | Must be No | Inspections | Check if the tank is in an area with high traffic or located within arms reach of an uncovered walkway | Indicate whether or not the tank is in a location where it would be easy to sustain a burn by walking by, the tank should not be located in an easily accessible location where burns could be sustained from walking by | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 145
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 7 | The insulation thickness and process temperature (tank solution temperature) will determine the energy savings. The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Tank Temp | Temperature inside the tank (F) | Numeric Value | [8 empty] | Inspections | Photograph the thermometer installed at the top of the tank or along the piping indicating the temperature of the fluid inside the tank or piping | The value listed in EECP should be within 10% of the measured value in the field | QA Checklist | An installation report should indicate the water temperature inside the hot water tank | The value listed in EECP should be within 10% of the measured value in the field |  | 2021-06-21 | Kenny Liljestrom |  | Add | 31
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 8 | The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Insulation material type | Insulation material type | Text Box | [8 empty] | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the insulation material type | The insulation material listed in EECP should match the data in the installation report or spec sheet | EECP | Trust Implementer response in EECP | Not configured in original upload |  | 2021-06-21 | Kenny Liljestrom |  | Add | 24
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 9 | The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Insulation Material k-value rating | Insulation material k-value rating | Text Box | [8 empty] | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the insulation k-value rating | The insulation material k-value listed in EECP should match the data in the installation report or spec sheet | EECP | Trust Implementer response in EECP | Not configured in original upload |  | 2021-06-21 | Kenny Liljestrom |  | Add | 34
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 10 | The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Type of tank material | Type of tank material (steel, fiberglass, etc.) | Text Box | [8 empty] | Inspections | Photograph the tank and make your best guess as to the material the tank is made of (i.e. steel, fiberglass, concrete, etc.) | There are not requirements for this just a best guess or judgement | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the tank material type | The tank material type listed in EECP should match the data in the installation report or spec sheet (fiberglass, steel, etc.) |  | 2021-06-21 | Kenny Liljestrom |  | Add | 47
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 11 | - | Yes | Usage | Usage | Drop Down List | High;Medium; | [6 empty] | Measure case description dictates allowable use type | - | - | - | - | - | - | Request to remove property, in measure description | 2021-08-06 | Kenny Liljestrom |  | Add | 5
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any | EECP | 12 | - | Yes | Tank Location | Where is the tank located? | Drop Down List | Indoor;Outdoor; | [6 empty] | Measure case description dictates allowable use type | - | - | - | - | - | - | Request to remove property, in measure description | 2021-08-06 | Kenny Liljestrom |  | Add | 26
1 | SWWH019 | 3 | Faucet Aerator, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice, installation report, or manufacturer spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom |  | Add | 12
1 | SWWH019 | 3 | Faucet Aerator, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice, installation report, or manufacturer spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom |  | Add | 5
1 | SWWH019 | 3 | Faucet Aerator, Commercial | Any | Any | Any | EECP | 3 | This energy efficiency measure is applicable to an existing faucet in a commercial building that has a flow rate of 1.67 gpm or greater. | Yes |  | Existing Faucet Flow Rate (gpm) | Numeric Value | [7 empty] | Must be >= 1.67 | QA Checklist | Use the submitted installation report to verify existing flow rate of the faucet is listed | The existing flow rate needs to be greater than 1.67 gallons per minute (gpm) and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 31
1 | SWWH019 | 3 | Faucet Aerator, Commercial | Any | Any | Any | EECP | 4 | Good to have | Yes |  | New Faucet Flow Rate (gpm) | Numeric Value | [8 empty] | QA Checklist | Use the submitted invoice, installation report, or manufacturer spec sheet to validate the new faucet aerator flow rate is listed | The flow rate of the installed unit must match the flow entered in EECP and be less than or equal to the flowrate required by the measure. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Remove validation criteria from property, measure description captures the min flow rate | 2021-08-19 | Kenny Liljestrom |  | Add | 26
1 | SWWH019 | 3 | Faucet Aerator, Commercial | Any | Any | Any | EECP | 5 | Only facilities that utilize natural gas water heating equipment are eligible to receive incentives for this measure. | Yes |  | Is the existing faucet served by a natural gas fired water heater in an existing building? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | Inspections | Ask the customer to show you where the hot water heater is located that serves the domestic hot water loads (faucets, showerheads, etc.); Photograph the water heater and nameplate to determine if the water heater is natural gas fired (yellow corrugated pipe into the burner) | The water heater serving the faucet aerators must be served by a natural gas fired water heater; the water heater nameplate should list the 'Input Rating' in Btu/hr, kBtu/hr, or MMBtu/hr | QA Checklist | Have the implementer provide photos of the water heater serving the faucets; the photos can include a photo of the nameplate (showing make, model, and input rating) | The make and model can be used to locate the equipment specification sheet to identify the fuel type of the water heater, or the Input Rating can be used to identify the fuel type by having units of Btu/hr, kBtu/hr, or MMBtu/hr; The water heater must be served by natural gas | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 90
1 | SWWH019 | 3 | Faucet Aerator, Commercial | Any | Any | Any | EECP | 6 | Faucets at health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation (e.g. hospitals, clinics, skilled nursing facilities) are not applicable for this measure. The use of aerators is banned in the health care industry due to aerator flow control methods and components. The mixing of air and water within the aerator allows airborne bacteria to become waterborne and, in warm stagnant conditions, promote bacterial growth. Non-aerating laminar flow restrictors (LFRs) must be installed on faucets in these facilities | Yes |  | Is the existing building considered a Health Care facility as defined by OSHPD? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | Inspections | Document the type of building the aerator was installed in | The building type listed in EECP should match the building type during the inspection; the building can not be a healthcare type of facility (nursing home, hospital, clinic, etc.) | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP and not be a healthcare type facility (hospital, nursing home, clinic, etc.) | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 79
0 | SWWH020 | 3 | Low-Flow Showerhead, Commercial | Any | Any | Any | EECP | 1 | Make and model number must be included with a copy of the invoice. | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice, installation report, or manufacturer spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom |  | Add | 12
0 | SWWH020 | 3 | Low-Flow Showerhead, Commercial | Any | Any | Any | EECP | 2 | Make and model number must be included with a copy of the invoice. | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice, installation report, or manufacturer spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom |  | Add | 5
0 | SWWH020 | 3 | Low-Flow Showerhead, Commercial | Any | Any | Any | EECP | 3 | The measure for the installation of low flow showerheads is applicable for the accelerated replacement of the existing showerhead of 2.5 gpm flow rate or greater with a low-flow showerhead of 1.8 gpm or lower flow rate. The installed low-flow showerhead shall meet the requirements of test procedure ANSI/ASME A112.18.1-2000, Section 5.5 The measure for the installation of flow control valves is applicable for the add-on equipment onto an existing showerhead with the flow rate of 2.5 gpm or greater, reducing the flow rate to 1.5 gpm or lower. | Yes | Existing Flow Rate | Existing Flow Rate (gpm) | Numeric Value | [7 empty] | Must be >= 2.5 | QA Checklist | Use the submitted installation report to verify existing flow rate of the showerhead is listed | The existing flow rate needs to be greater than 2.5 gallons per minute (gpm) and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom |  | Add | 24
0 | SWWH020 | 3 | Low-Flow Showerhead, Commercial | Any | Any | Any | EECP | 4 | good to have | Yes | Flow Rate | Flow Rate of Installed Unit (gpm) | Numeric Value | [8 empty] | QA Checklist | Use the submitted invoice, installation report, or manufacturer spec sheet to validate the new showerhead flow rate is listed | The flow rate of the installed unit must match the flow entered in EECP and be less than or equal to the flowrate required by the measure. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Remove validation criteria, measure description captures the measure case flow rate | 2021-08-19 | Kenny Liljestrom |  | Add | 33
0 | SWWH020 | 3 | Low-Flow Showerhead, Commercial | Any | Any | Any | EECP | 5 | This measure is excluded from newly constructed buildings, additions to existing buildings, and alterations to existing buildings. | Yes | Unit Installed Building Type | Is the unit being installed in a newly constructed buildings, additions to existing buildings, and alterations to existing buildings? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | QA Checklist | Use the submitted invoice, installation report, or manufacturer spec sheet to validate the new showerhead flow rate is listed | The flow rate of the installed unit must match the flow entered in EECP and be less than or equal to the flowrate required by the measure. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom |  | Add | 133
0 | SWWH020 | 3 | Low-Flow Showerhead, Commercial | Any | Any | Any | EECP | 6 | The facility must have natural gas as the water heating source fuel. | Yes | Natural Gas WH | Does the facility utilize natural gas water heating equipment? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Ask the customer to show you where the hot water heater is located that serves the domestic hot water loads (faucets, showerheads, etc.); Photograph the water heater and nameplate to determine if the water heater is natural gas fired (yellow corrugated pipe into the burner) | The water heater serving the showerheads must be served by a natural gas fired water heater; the water heater nameplate should list the 'Input Rating' in Btu/hr, kBtu/hr, or MMBtu/hr | QA Checklist | Have the implementer provide photos of the water heater serving the showerheads; the photos can include a photo of the nameplate (showing make, model, and input rating) | The make and model can be used to locate the equipment specification sheet to identify the fuel type of the water heater, or the Input Rating can be used to identify the fuel type by having units of Btu/hr, kBtu/hr, or MMBtu/hr; The water heater must be served by natural gas |  | 2021-08-19 | Kenny Liljestrom |  | Add | 62
0 | SWWH020 | 3 | Low-Flow Showerhead, Commercial | Any | Any | Any | EECP | 7 | For accelerated replacement measure application type (MAT), this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers Customer/site information Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating Specific documentation requirements will be determined by the program administrator and will be specified in the program implementation plan. Program influence evidence can be demonstrated through one of the three alternatives listed in Section 7.3 of POEV 2.0. This measure establishes the program-level evidence of program influence by adopting the net-to-gross (NTG) ratio from prior program evaluation results. | Yes |  | Have all POE requirements spelled out in the workpaper been included in the program documentation? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | For accelerated replacement measure application type (MAT), this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers Customer/site information Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating Specific documentation requirements will be determined by the program administrator and will be specified in the program implementation plan. Program influence evidence can be demonstrated through one of the three alternatives listed in Section 7.3 of POEV 2.0. This measure establishes the program-level evidence of program influence by adopting the net-to-gross (NTG) ratio from prior program evaluation results. | Verify all POE requirements are included in the submitted influence documentation | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 98
1 | SWWH021 | 1 | Recirculation Pump Timer, Commercial | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-20 | Kenny Liljestrom |  | Add | 12
1 | SWWH021 | 1 | Recirculation Pump Timer, Commercial | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-20 | Kenny Liljestrom |  | Add | 5
1 | SWWH021 | 1 | Recirculation Pump Timer, Commercial | Any | Any | Any | EECP | 3 | Good to have | Yes |  | Size of Recirculation Pump Motor | Numeric Value | [8 empty] | Inspections | Photograph the equipment nameplate to capture the power rating (hp) | The listed power rating (hp) in EECP should match the nameplate | QA Checklist | Use the submitted installation report to validate the motor power rating (hp) is listed | The power rating (hp) listed in EECP should match what is listed in the installation report | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 32
1 | SWWH021 | 1 | Recirculation Pump Timer, Commercial | Any | Any | Any | EECP | 4 | Eligibility requirements for this measure include the following: • The building must have a hot water recirculation system that can be turned OFF entirely for a set period of the day and/or week. • The building must have a centralized, gas-fired, hot-water system with a constant-flow, fractional-horsepower, uncontrolled recirculation pump. • The timer device must have seven-day (or better) scheduling capabilities. • There is no restriction on manufacturer or brand-naming. | Yes |  | Building has hot water recirculation system that can be turned OFF for a set period time? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | QA Checklist | Use the manufacturer spec sheet to validate if the controls include allowing the system to be turned OFF entirely for a set period of the day and/or week. | The building must have a hot water recirculation system that can be turned OFF entirely for a set period of the day and/or week. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 89
1 | SWWH021 | 1 | Recirculation Pump Timer, Commercial | Any | Any | Any | EECP | 5 | Eligibility requirements for this measure include the following: • The building must have a hot water recirculation system that can be turned OFF entirely for a set period of the day and/or week. • The building must have a centralized, gas-fired, hot-water system with a constant-flow, fractional-horsepower, uncontrolled recirculation pump. • The timer device must have seven-day (or better) scheduling capabilities. • There is no restriction on manufacturer or brand-naming. | Yes |  | Hot water is central, gas-fired, constant-flow, fractional horsepower, uncontrolled recirc pump? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 96
1 | SWWH021 | 1 | Recirculation Pump Timer, Commercial | Any | Any | Any | EECP | 6 | Eligibility requirements for this measure include the following: • The building must have a hot water recirculation system that can be turned OFF entirely for a set period of the day and/or week. • The building must have a centralized, gas-fired, hot-water system with a constant-flow, fractional-horsepower, uncontrolled recirculation pump. • The timer device must have seven-day (or better) scheduling capabilities. • There is no restriction on manufacturer or brand-naming. | Yes |  | Does the installed timer device have seven-day (or better) scheduling capabilities? | Drop Down List | Yes;No; | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 83
1 | SWWH021 | 1 | Recirculation Pump Timer, Commercial | Any | Any | Any | EECP | 7 | This measure is applicable to existing buildings and is limited to the commercial building types specified below. • Healthcare – outpatient • Service – fitness • Office – large • Office – small • Education – primary • Education - secondary | Yes |  | Building Type | Drop Down List | Healthcare – outpatient ;Service – fitness;Office – large ;Office – small ;Education – primary;Education - secondary;Other; | [6 empty] | Must not be 'Other' | Inspections | While on site, observe the building type | The building type must be one of the following: Healthcare – outpatient , Service – fitness, Office – large , Office – small , Education – primary, Education - secondary | QA Checklist | Use the installation report or EECP to determine the building type | The building type must be one of the following: Healthcare – outpatient , Service – fitness, Office – large , Office – small , Education – primary, Education - secondary | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 13
1 | SWWH021 | 1 | Recirculation Pump Timer, Commercial | Any | Any | Any | EECP | 8 | This measure is excluded from newly constructed buildings, additions to existing buildings, and alterations to existing buildings. | Yes |  | Measure installed on a newly constructed, additions or alterations to an existing building? | Drop Down List | Yes;No; | [6 empty] | Must be No | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 91
0 | SWWH023 | 1 | Diverting Tub Spout with TSV, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWWH023 | 1 | Diverting Tub Spout with TSV, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWWH023 | 1 | Diverting Tub Spout with TSV, Residential | Any | Any | Any | EECP | 3 | Revisit | Yes | Receipt | Was a copy of the purchase receipt submitted? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Review the submitted documentation in EECP | A copy of the invoice should be included in the submitted documentation | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
0 | SWWH023 | 1 | Diverting Tub Spout with TSV, Residential | Any | Any | Any | EECP | 4 | Revisit | Yes | Natural Gas WH | Does the facility utilize natural gas water heating equipment? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | Inspections | Photograph the water heater showing the gas pipe (yellow pipe) going into the water heater; the nameplate showing the make and model will also suffice | The water heater must be fueled by natural gas | QA Checklist | An installation report may indicate the water heater type or make and model which can be used to check the type | The water heater must be fueled by natural gas |  | 2021-06-21 | Kenny Liljestrom |  | Add | 62
0 | SWWH023 | 1 | Diverting Tub Spout with TSV, Residential | Any | Any | Any | EECP | 5 | Revisit | Yes | IAPMO | Is the installed product certified by International Association of Plumbing and Mechanical Officials (IAPMO)? | Drop Down List | Yes;No | [6 empty] | Must be 'Yes' | QA Checklist | Cross reference the make and model with the IAPMO database | The product needs to be listed in the database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 109
0 | SWWH023 | 1 | Diverting Tub Spout with TSV, Residential | Any | Any | Any | EECP | 6 | Revisit | Yes | Tankless | Does the facility utilize tankless water heaters? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | Inspections | Photograph the water heater and make note of the water heater type | Ensure it is not a tankless type water heater (typically installed on a wall inside/outside of the garage) | QA Checklist | The make and model of the water heater may be provided in an installation report | The water heater type should not be instantaneous or tankless |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWWH023 | 1 | Diverting Tub Spout with TSV, Residential | Any | Any | Any | EECP | 7 | Revisit | Yes | Wall Mounted Diverter | Does the shower have a wall-mounted diverter? | Drop Down List | Yes;No | [6 empty] | Must be 'No' | Inspections | Photograph the shower layout | There should be no diverter between the showerhead and the tub spout | QA Checklist | A photograph of the shower layout showing the tub spout and showerhead | There should be no diverter between the tub spout and showerhead |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
0 | SWWH023 | 1 | Diverting Tub Spout with TSV, Residential | Any | Any | Any | EECP | 9 | Revisit | Yes | Flow Rate | Flow Rate of Installed Unit (gpm) | Numeric Value | [8 empty] | QA Checklist | Use the manufacturer spec sheet to validate the flow rate of the newly installed unit | The flow rate listed in EECP should match what is on the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 33
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | UpDeemed | EECP | 0 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  | Add | 7
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | UpDeemed | EECP | 5 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  | Add | 12
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | Any | EECP | 10 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 12
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | Any | EECP | 15 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 5
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | UpDeemed | EECP | 20 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 13
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | DnDeemed | EECP | 25 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Electrification Infrastructure | If site required electric infrastructure upgrades, have itemized invoices with costs been submitted? | Drop Down List | Yes;No;N/A; | Not Equal | No |  |  |  |  | Must be 'Yes' or 'N/A' | QA Checklist | If implementer answered 'Yes', review EECP documentation for additional invoice data | In addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer. These are defined in Decision 19‐08‐009: What is the existing fuel type for the existing equipment? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  | Add | 100
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | DnDeemDI | EECP | 25 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Electrification Infrastructure | If site required electric infrastructure upgrades, have itemized invoices with costs been submitted? | Drop Down List | Yes;No;N/A; | Not Equal | No |  |  |  |  | Must be 'Yes' or 'N/A' | QA Checklist | If implementer answered 'Yes', review EECP documentation for additional invoice data | In addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer. These are defined in Decision 19‐08‐009: What is the existing fuel type for the existing equipment? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 100
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | DnDeemed | EECP | 30 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Electrification Measures | List other electrification measures installed with the heat pump water heater | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 77
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | DnDeemDI | EECP | 30 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Electrification Measures | List other electrification measures installed with the heat pump water heater | Text Box | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 77
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | DnDeemed | EECP | 35 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Electrification Measures Costs | If site had electrification measures, have itemized infrastructure costs invoices been submitted? | Drop Down List | Yes;No;N/A; | Not Equal | No |  |  |  |  | Must be 'Yes' or 'N/A' | QA Checklist | If implementer answered 'Yes', review EECP documentation for additional invoice data | In addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer. These are defined in Decision 19‐08‐009: What is the existing fuel type for the existing equipment? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 98
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | DnDeemDI | EECP | 35 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Electrification Measures Costs | If site had electrification measures, have itemized infrastructure costs invoices been submitted? | Drop Down List | Yes;No;N/A; | Not Equal | No |  |  |  |  | Must be 'Yes' or 'N/A' | QA Checklist | If implementer answered 'Yes', review EECP documentation for additional invoice data | In addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer. These are defined in Decision 19‐08‐009: What is the existing fuel type for the existing equipment? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 98
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | DnDeemed | EECP | 40 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Heater Fuel | If installed in a conditioned space, existing space heating fuel type | Drop Down List | Electric;Gas;Unconditioned; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 69
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | DnDeemDI | EECP | 40 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Heater Fuel | If installed in a conditioned space, existing space heating fuel type | Drop Down List | Electric;Gas;Unconditioned; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 69
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | A | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | B | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | C | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | D | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | E | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | F | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | G | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | H | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | I | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | J | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | K | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | M | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | O | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | P | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Q | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | R | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | S | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | T | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | U | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | V | Any | DnDeemed | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | A | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | B | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | C | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | D | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | E | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | F | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | G | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | H | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | I | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | J | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | K | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | M | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | O | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | P | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Q | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | R | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | S | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | T | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | U | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | V | Any | DnDeemDI | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | Any | EECP | 50 | Existing base equipment must be disposed. | Yes | Disposal Method | Has the existing equipment been properly disposed of and not abandoned in place? | Drop Down List | Yes;No | [6 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-06-13 | Kenny Liljestrom |  | Add | 80
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | NC | DnDeemed | EECP | 50 | NC is only eligible for downstream delivery under the following conditions. These are defined as new services in fuel substitution technical guidance: Measures are installed in new areas of an existing building, Measures are installed in a major renovation of an existing building, or Measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. | Yes | New Area | For NC, select the 'new services' condition | Drop Down List | New area;Major renovation;Capacity expansion; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  | Add | 43
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | Any | EECP | 55 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, and proposed building type where the product will be installed. | Yes | Input Rating | Input rating (kBtu/hr) | Numeric Value |  |  |  | General | 0 |  | 2 | Must be >= 0 | [7 empty] | 2022-06-13 | Kenny Liljestrom |  |  | 22
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | A | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | B | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | C | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | D | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | E | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | F | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | G | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | H | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | I | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | J | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | K | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 56 | 75 | 0 | Must be > 55 and <= 75 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 55-gallons and less than or equal to 75-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 55-gallons and less than or equal to 75-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | M | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 75 |  | 0 | Must be > 75 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 75-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 75-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | O | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 45 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | P | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 45 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Q | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 45 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | R | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 45 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | S | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 0 | 45 | 0 | Must be <= 45 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be less than or equal to 45-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be less than or equal to 45-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | T | Any | Any | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  | General | 0 | 45 | 0 | Must be <= 45 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be less than or equal to 45-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be less than or equal to 45-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | A | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | B | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | C | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | D | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | E | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | F | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | G | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | H | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | I | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | J | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | K | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.33 |  | 2 | Must be >= 3.33 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | M | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.42 |  | 2 | Must be >= 3.42 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | O | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | P | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Q | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | R | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | S | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | T | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | U | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.5 |  | 2 | Must be >= 3.5 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | V | Any | Any | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.5 |  | 2 | Must be >= 3.5 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | Any | EECP | 70 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | FHR | First Hour Rating (FHR) | Numeric Value |  |  |  | General | 0 |  | 0 | Must be > 0 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The First Hour Rating (FHR) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 23
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | UpDeemed | EECP | 190 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value |  |  |  | General |  |  | 0 |  | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 8
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | UpDeemed | EECP | 195 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 15
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | AR | Any | QA Checklist | 205 | Preponderance of evidence (POE) must be documented for all accelerated replacement application types. Notably, programs shall document if measure was replaced as a direct result of information, recommendations, and support provided by the program administrator, and programs shall require the collection and submission of documentation to ensure proper conformance to eligibility and implementation requirements. The following are the types of information that will be required for all projects: Customer/site information Specifications of existing equipment Proof that water heater is still operating as intended Existing water heater nameplate data with manufacturer date to confirm remaining useful life Replacement water heater information To document POE, the implementer must complete the provided the survey, or similar. R1539 | Yes | POE Docs | Have POE requirements in the measure package been included in uploaded documentation? | None | [8 empty] | QA Checklist | Review the POE documentation and determine if it is adequate based on required criteria. | The POE documentation needs to list the: Customer/site information, Specifications of existing equipment, Proof that water heater is still operating as intended, Existing water heater nameplate data with manufacturer date to confirm remaining useful life, Replacement water heater information. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-06-13 | Kenny Liljestrom |  |  | 85
0 | SWWH026 | 1 | Water Heater Pipe Wrap, Residential | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWWH026 | 1 | Water Heater Pipe Wrap, Residential | Any | Any | Any | EECP | 2 | - | Yes | Model | Model | Text Box | [8 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWWH026 | 1 | Water Heater Pipe Wrap, Residential | Any | Any | Any | EECP | 3 | Program eligibility requirements for the addition of insulation to hot water and cold water pipes, within the first three feet of a storage water heater include: | Yes | Insulation Addition | Does the measure include addition of insulation to hot water and cold-water pipes within the first 3 feet of a storage water heater? | Drop Down List | Yes;No | [6 empty] | Must be Yes | Inspections | Photograph the pipe insulation, document whether or not the insulation is installed within 3-feet of the water heater. | The insulation must be located within approximately 3-feet of the storage tank water heater | QA Checklist | A photograph in the installation report may show the pipe wrap near the water heater | The pipe wrap must be located within 3-feet of the water heater or tank |  | 2021-06-21 | Kenny Liljestrom |  | Add | 132
0 | SWWH026 | 1 | Water Heater Pipe Wrap, Residential | Any | Any | Any | EECP | 4 | A minimum of 1-inch of pipe insulation must be added to existing bare pipe | Yes | Minimum Thickness | Was a minimum thickness of 1 inch of pipe insulation added to existing bare pipe? | Drop Down List | Yes;No | [6 empty] | Must be Yes | Inspections | Photograph the insulated piping showing both the insulation and any exposed piping | The insulation thickness should be greater than or equal to 1-inch and the piping should be either copper or steel (i.e. not PVC or other materials) | QA Checklist | The make and model of the insulation should indicate on the manufacturer specification sheet the insulation thickness | Insulation thickness should be greater than or equal to 1-inch; a photograph of the piping system in an installation report may show the type of piping installed, eligible types are copper and steel |  | 2021-06-21 | Kenny Liljestrom |  | Add | 81
0 | SWWH026 | 1 | Water Heater Pipe Wrap, Residential | Any | Any | Any | EECP | 5 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam | Yes | Type | Type of insulation for hot water pipes installed | Drop Down List | Elastomeric Foam;Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [7 empty] | QA Checklist | Cross-Check invoice or specification sheet with submitted data in EECP | Acceptable types of insulation should match EECP and are listed below: Elastomeric Foam; Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 48
0 | SWWH026 | 1 | Water Heater Pipe Wrap, Residential | Any | Any | Any | EECP | 6 | Must be installed by an authorized implementer | Yes | Approved Contractor | Was the installation of the measure completed by a utility-approved contractor? | Drop Down List | Yes;No | [6 empty] | Must be Yes | QA Checklist | Cross-Check invoice with submitted data in EECP, determine if contractor is on Trade-Pro list | The trade pro from the installation report should be in the approved trade pro list | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 79
0 | SWWH026 | 1 | Water Heater Pipe Wrap, Residential | Any | Any | Any | EECP | 7 | Must verify no existing pipe insulation as the existing condition | Yes | Existing Insulation | Did the pipes have existing pipe insulation ? | Drop Down List | Yes;No | [6 empty] | Must be No | Inspections | Photograph of pipe insulation, look for signs of existing insulation which may include small pieces still glued to the pipe, glue lines along the piping, pieces of old insulation on the floor around the water heater. | There should not be any signs of previously installed insulation | QA Checklist | Photographs of the existing and installed measure piping systems; the existing system should not have any insulation installed | There should not be any signs of previously installed insulation |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
0 | SWWH026 | 1 | Water Heater Pipe Wrap, Residential | Any | Any | Any | EECP | 8 | This measure is not applicable for commercial or industrial applications. This measure is not eligible for new construction applications as defined by the California Plumbing Code. | Yes | New Construction | Was the measure installed in a new construction application? | Drop Down List | Yes;No | [6 empty] | Must be No | QA Checklist | Check the billing history in EECP; the customer should have several months of billing data | The building should be existing, not new | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 61
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | Any | Any | Any | EECP | 0 | - | Yes | Manufacturer | HPWH Manufacturer | Text Box | [8 empty] | Inspections | Photograph the nameplate of the heat pump water heater to capture the manufacturer | The manufacturer listed in EECP should match the nameplate on the equipment | QA Checklist | Use an installation report or invoice to determine the manufacturer of the heat pump water heater (HPWH) | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2022-06-20 | Kenny Liljestrom |  |  | 17
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | Any | Any | Any | EECP | 5 | - | Yes | Model | HPWH Model | Text Box | [8 empty] | Inspections | Photograph the nameplate of the heat pump water heater to capture the model number | The model number listed in EECP should match the nameplate on the equipment | QA Checklist | Use an installation report or invoice to determine the model number of the heat pump water heater (HPWH) | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2022-06-20 | Kenny Liljestrom |  |  | 10
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | A | Any | Any | EECP | 10 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity | HPWH Storage Capacity (gallons) | Numeric Value |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 31
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | B | Any | Any | EECP | 10 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity | HPWH Storage Capacity (gallons) | Numeric Value |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 31
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | C | Any | Any | EECP | 10 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity | HPWH Storage Capacity (gallons) | Numeric Value |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 31
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | D | Any | Any | EECP | 10 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity | HPWH Storage Capacity (gallons) | Numeric Value |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 31
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | E | Any | Any | EECP | 10 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity | HPWH Storage Capacity (gallons) | Numeric Value |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 31
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | F | Any | Any | EECP | 10 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity | HPWH Storage Capacity (gallons) | Numeric Value |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 31
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | G | Any | Any | EECP | 10 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity | HPWH Storage Capacity (gallons) | Numeric Value |  |  |  | General | 56 | 75 | 0 | Must be > 55 and <= 75 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 55-gallons and less than or equal to 75-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 55-gallons and less than or equal to 75-gallons and match what is listed in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 31
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | H | Any | Any | EECP | 10 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity | HPWH Storage Capacity (gallons) | Numeric Value |  |  |  | General | 76 |  | 0 | Must be > 75 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 75-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 75-gallons and match what is listed in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 31
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | A | Any | Any | EECP | 15 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 27
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | B | Any | Any | EECP | 15 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 27
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | C | Any | Any | EECP | 15 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 27
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | D | Any | Any | EECP | 15 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 27
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | E | Any | Any | EECP | 15 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 27
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | F | Any | Any | EECP | 15 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 27
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | G | Any | Any | EECP | 15 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.33 |  | 2 | Must be >= 3.33 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 27
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | H | Any | Any | EECP | 15 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  | General | 3.42 |  | 2 | Must be >= 3.42 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 27
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | Any | Any | Any | EECP | 20 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | FHR | HPWH First Hour Rating (FHR) | Numeric Value |  |  |  | General |  |  | 0 |  | QA Checklist | Use the make and model number in EECP to locate the specification sheet for the heat pump water heater to find the first hour rating (FHR); the specification sheet may have been submitted by the 3PI, so check the documents section of EECP | The FHR should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 28
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | Any | Any | Any | EECP | 25 | Replacement of an "instantaneous" or "tankless" water heater does not qualify. | Yes | Disposal Method | Existing water heater was a storage tank style and disposed of (not retrofitted)? | Drop Down List | Yes;No; | Equal | Yes |  |  |  |  | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-06-20 | Kenny Liljestrom |  |  | 81
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | Any | Any | DnDeemed | EECP | 0 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | No | - | Building type | Drop Down List | Asm;Com;ECC;EPr;ERC;ESe;EUn;Gro;HGR;Hsp;Htl;MBT;MLI;Mtl;Nrs;OfL;OfS;RFF;RSD;Rt3;RtL;RtS;SCn;SUn;WRf; | [7 empty] | Inspections | Make note of the building type at the inspection site | The building type must match what is listed in EECP | QA Checklist | Use the installation report to determine the building type of the customer | The building type listed in EECP must match what is on the installation report | Property can be configured at the enrollment level | 2022-06-20 | Kenny Liljestrom | Property is configured at the enrollment level, don't need another property type |  | 13
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | Any | Any | Any | EECP | 190 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | ZC | Zip Code | Numeric Value |  |  |  | General |  |  | 0 |  | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-20 | Kenny Liljestrom |  |  | 8
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | Any | Any | Any | EECP | 195 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-20 | Kenny Liljestrom |  |  | 15
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | Any | Any | Any | QA Checklist | 205 | Deployment of the program may require rebates or financial incentives to participants that exceed the incremental measure cost (IMC). Incentives or rebates that exceed the IMC for a measure must be justified by individual program administrators (PAs) in addendum to measure submissions to document program implementation practice prior to program implementation. | Yes | - | IMC | None | [8 empty] | QA Checklist | Deployment of the program may require rebates or financial incentives to participants that exceed the incremental measure cost (IMC). Incentives or rebates that exceed the IMC for a measure must be justified by individual program administrators (PAs) in addendum to measure submissions to document program implementation practice prior to program implementation. | No processing checks to be made for this property, just notice of measure requirements | - | - | - |  | 2022-06-20 | Kenny Liljestrom |  |  | 3
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any | EECP | 1 | - | Yes | Manufacturer | VFD Manufacturer | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | Quantity of measure should be limited to 1 in order to capture all the manufacturer and model numbers of the VFDs | 2021-11-23 | Kenny Liljestrom |  |  | 16
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any | EECP | 2 | - | Yes | Model | VFD Model | Text Box | [8 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-23 | Kenny Liljestrom |  |  | 9
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any | EECP | 3 | The VFD must be installed on the pump motor with a minimum operation of 1,000 hours per year. | Yes |  | Pump annual hours of operation (hr/yr) | Numeric Value | [7 empty] | Must be >= 1000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 38
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any | EECP | 4 | To substantiate conformance with program requirements, the customer must supply an invoice or other supporting documentation that includes the following: • Quantity of VFDs • Type (well and/or booster) • Horsepower rating of motor(s) and VFD(s) • Area map showing physical location of pumps • Manufacturer make/models of each VFD installed | Yes |  | Pump type | Drop Down List | Well;Booster;Well and Booster; | [7 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 9
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any | EECP | 5 | To substantiate conformance with program requirements, the customer must supply an invoice or other supporting documentation that includes the following: • Quantity of VFDs • Type (well and/or booster) • Horsepower rating of motor(s) and VFD(s) • Area map showing physical location of pumps • Manufacturer make/models of each VFD installed | Yes |  | Pump horsepower (hp) | Numeric Value | [8 empty] | Inspections | Photograph the pump motor nameplate to capture the power (hp) rating | The pump horsepower (hp) on the motor nameplate should match what is listed in EECP | QA Checklist | Using a photograph or pump make and manufacturer, identify the motor horsepower | The pump horsepower must match what is listed in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 20
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any | EECP | 6 | To substantiate conformance with program requirements, the customer must supply an invoice or other supporting documentation that includes the following: • Quantity of VFDs • Type (well and/or booster) • Horsepower rating of motor(s) and VFD(s) • Area map showing physical location of pumps • Manufacturer make/models of each VFD installed The customer must have an existing electrically operated agricultural booster or well pump installed on site or plans to install a new agricultural booster or well pump. | Yes |  | A map of the pump service area has been submitted? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist | Review the submitted documents in the enrollment package or EECP for a map of the location the pump is/will serve | A map of the pump service location must be submitted by the customer or implementer | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 50
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any | EECP | 7 | The variable frequency drive (VFD) must be used to adjust operation of a pump to meet flow/pressure requirements and not be used simply as a soft starter or for cavitation control. | Yes |  | VFD is used for flow/pressure control, not for soft start or cavitation? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 72
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any | EECP | 8 | The pumping application must currently have the means to vary the pressure/flow (i.e. throttle valve, control valve, etc.). | Yes |  | Existing pump has means to vary the pressure or flow (i.e. throttle valve, control valve, etc.)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | QA Checklist |  |  | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 96
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any | EECP | 9 | The VFD must be installed on a pressurized irrigation system (no flood irrigation). | Yes |  | VFD is installed on a pressurized irrigation system (no flood irrigation)? | Drop Down List | Yes;No; | [6 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 74
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any | EECP | 10 | This measure cannot be used for the following pumping applications: • A well pump used to fill a reservoir, • A well pump discharging directly into a canal, and/or • A mixed flow pump (high volume, low head). | Yes |  | Is the pump is used as a well pump to fill a reservoir or discharging into a canal? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 83
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any | EECP | 11 | This measure cannot be used for the following pumping applications: • A well pump used to fill a reservoir, • A well pump discharging directly into a canal, and/or • A mixed flow pump (high volume, low head). | Yes |  | Is the pump a mixed flow pump with high volume and low head? | Drop Down List | Yes;No; | [6 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 60
Note on J257: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Example of "IF item 8 fails, THEN check this" Should it be a single line?

## Sheet4
SWAP001 | 128 | SWHC014 | 182
SWAP003 | 20 | SWHC049 | 152
SWAP004 | 36 | SWHC013 | 151
SWAP005 | 13 | SWAP001 | 128
SWAP006 | 12 | SWRE002 | 116
SWAP007 | 11 | SWHC046 | 108
SWAP012 | 12 | SWWH025 | 98
SWBE001 | 8 | SWHC005 | 88
SWBE002 | 7 | SWHC004 | 83
SWCR001 | 23 | SWWH017 | 69
SWCR003 | 14 | SWLG011 | 58
SWCR004 | 11 | SWFS003 | 51
SWCR005 | 14 | SWHC044 | 49
SWCR007 | 24 | SWSV001 | 45
SWCR010 | 13 | SWFS018 | 44
SWCR015 | 6 | SWHC045 | 43
SWCR017 | 18 | SWWH014 | 37
SWCR018 | 7 | SWAP004 | 36
SWCR019 | 6 | SWHC020 | 36
SWCR020 | 6 | SWFS006 | 35
SWCR021 | 11 | SWWH012 | 30
SWFS001 | 18 | SWHC031 | 29
SWFS002 | 18 | SWHC027 | 27
SWFS003 | 51 | SWLG009 | 27
SWFS004 | 11 | SWPR005 | 26
SWFS005 | 10 | SWWH016 | 26
SWFS006 | 35 | SWHC039 | 25
SWFS007 | 22 | SWLG018 | 25
SWFS008 | 6 | SWCR007 | 24
SWFS010 | 12 | SWHC052 | 24
SWFS011 | 20 | SWWH031 | 24
SWFS012 | 9 | SWCR001 | 23
SWFS013 | 6 | SWFS007 | 22
SWFS014 | 6 | SWHC038 | 22
SWFS017 | 12 | SWSV013 | 22
SWFS018 | 44 | SWAP003 | 20
SWFS019 | 10 | SWFS011 | 20
SWFS023 | 9 | SWHC001 | 20
SWHC001 | 20 | SWHC041 | 20
SWHC002 | 8 | SWHC043 | 19
SWHC004 | 83 | SWWH004 | 19
SWHC005 | 88 | SWCR017 | 18
SWHC009 | 15 | SWFS001 | 18
SWHC012 | 10 | SWFS002 | 18
SWHC013 | 151 | SWWH006 | 18
SWHC014 | 182 | SWWH007 | 18
SWHC018 | 8 | SWPR004 | 17
SWHC020 | 36 | SWHC029 | 16
SWHC023 | 12 | SWPR002 | 16
SWHC024 | 12 | SWHC009 | 15
SWHC027 | 27 | SWCR003 | 14
SWHC029 | 16 | SWCR005 | 14
SWHC031 | 29 | SWAP005 | 13
SWHC038 | 22 | SWCR010 | 13
SWHC039 | 25 | SWAP006 | 12
SWHC041 | 20 | SWAP012 | 12
SWHC042 | 9 | SWFS010 | 12
SWHC043 | 19 | SWFS017 | 12
SWHC044 | 49 | SWHC023 | 12
SWHC045 | 43 | SWHC024 | 12
SWHC046 | 108 | SWHC048 | 12
SWHC048 | 12 | SWRE001 | 12
SWHC049 | 152 | SWSV009 | 12
SWHC052 | 24 | SWWH005 | 12
SWLG009 | 27 | SWWH018 | 12
SWLG011 | 58 | SWAP007 | 11
SWLG018 | 25 | SWCR004 | 11
SWPR001 | 6 | SWCR021 | 11
SWPR002 | 16 | SWFS004 | 11
SWPR004 | 17 | SWSV002 | 11
SWPR005 | 26 | SWSV003 | 11
SWPR007 | 8 | SWSV004 | 11
SWRE001 | 12 | SWWP002 | 11
SWRE002 | 116 | SWFS005 | 10
SWRE003 | 6 | SWFS019 | 10
SWSV001 | 45 | SWHC012 | 10
SWSV002 | 11 | SWSV006 | 10
SWSV003 | 11 | SWFS012 | 9
SWSV004 | 11 | SWFS023 | 9
SWSV006 | 10 | SWHC042 | 9
SWSV007 | 8 | SWWH003 | 9
SWSV009 | 12 | SWWH008 | 9
SWSV013 | 22 | SWBE001 | 8
SWWH001 | 8 | SWHC002 | 8
SWWH002 | 6 | SWHC018 | 8
SWWH003 | 9 | SWPR007 | 8
SWWH004 | 19 | SWSV007 | 8
SWWH005 | 12 | SWWH001 | 8
SWWH006 | 18 | SWWH021 | 8
SWWH007 | 18 | SWWH023 | 8
SWWH008 | 9 | SWWH026 | 8
SWWH012 | 30 | SWBE002 | 7
SWWH014 | 37 | SWCR018 | 7
SWWH016 | 26 | SWWH020 | 7
SWWH017 | 69 | SWCR015 | 6
SWWH018 | 12 | SWCR019 | 6
SWWH019 | 6 | SWCR020 | 6
SWWH020 | 7 | SWFS008 | 6
SWWH021 | 8 | SWFS013 | 6
SWWH023 | 8 | SWFS014 | 6
SWWH025 | 98 | SWPR001 | 6
SWWH026 | 8 | SWRE003 | 6
SWWH031 | 24 | SWWH002 | 6
SWWP002 | 11 | SWWH019 | 6

## Sheet2
Source Record (Item from Workpaper requiring Property) | Property Enabled | Property Name
- | Yes | Manufacturer
Eligible building types include any residential single family, multifamily, and residential double-wide mobile homes. | Yes
- | Yes | Model
The product eligibility requirements for the ENERGY STAR and ENERGY STAR Most Efficient tiers are provided below. See Measure Case Description for a full list of refrigerator model specifications. Must be on the ENERGY STAR qualifying list. | Yes
Good to have | Yes
ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes
Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes
Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes
Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes
Eligible building types include any new or existing residential building, including single family, multifamily units, and double-wide mobile homes. | Yes
Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes
Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) and ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. | Yes
ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes
ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes
ENERGY STAR Commercial Clothes Washer - Owned – Must be an ENERGY STAR-qualified commercial front-loading model. – The clothes container volume must be > 1.6 and < 8.0 cubic feet. – All models must have MEF J2 ≥ 2.2 and IWF ≤ 4.0 | Yes
ENERGY STAR Commercial Clothes Washer – Leased – Must be an ENERGY STAR-qualified commercial front-loading model. – The clothes container volume must be > 1.6 and < 8.0 cubic feet. – All models must have MEF J2 ≥ 2.2 and IWF ≤ 4.0 – Lease Term must be for a minimum term of 5 years and term cannot end prior to five years after the qualified measure is installed. Annual renewal leases do not qualify. | Yes
Eligible building types include residential single-family, double-wide mobile homes, and in-unit multifamily residences as well as multifamily common area laundry. | Yes
This measure is applicable for hotels/motels, health centers, nursing homes, and correctional facilities. | Yes
Eligible ozone laundry products must meet the following requirements: • The washing capacity of each washing machine must be rated at 200 pounds or less. • The customer must have a natural gas-fired boiler or natural gas water heater that supplies hot water to the on-premise laundry (OPL) equipment. • The ozone laundry system(s) must be a new purchased product and installed with a new or existing commercial washing machine(s). • The ozone laundry system(s) must transfer ozone into the water with either the venture injection or bubble diffusion process. | Yes | Capacity
Eligible ozone laundry products must meet the following requirements: • The washing capacity of each washing machine must be rated at 200 pounds or less. • The customer must have a natural gas-fired boiler or natural gas water heater that supplies hot water to the on-premise laundry (OPL) equipment. • The ozone laundry system(s) must be a new purchased product and installed with a new or existing commercial washing machine(s). • The ozone laundry system(s) must transfer ozone into the water with either the venture injection or bubble diffusion process. | Yes
- | Yes | LBS
Eligible ozone laundry products must meet the following requirements: • The washing capacity of each washing machine must be rated at 200 pounds or less. • The customer must have a natural gas-fired boiler or natural gas water heater that supplies hot water to the on-premise laundry (OPL) equipment. • The ozone laundry system(s) must be a new purchased product and installed with a new or existing commercial washing machine(s). • The ozone laundry system(s) must transfer ozone into the water with either the venture injection or bubble diffusion process. | Yes | Market Cost
- | Yes | Number of Guest Rooms
- | Yes | Serial Number
Eligible ozone laundry products must meet the following requirements: • The washing capacity of each washing machine must be rated at 200 pounds or less. • The customer must have a natural gas-fired boiler or natural gas water heater that supplies hot water to the on-premise laundry (OPL) equipment. • The ozone laundry system(s) must be a new purchased product and installed with a new or existing commercial washing machine(s). • The ozone laundry system(s) must transfer ozone into the water with either the venture injection or bubble diffusion process. | Yes | Size
Laundry systems equipped with tunnel washers are not eligible. | Yes
This measure is eligible for all residential building types of any vintage that utilize natural gas water heating equipment. | Yes
Compact residential dishwashers and commercial dishwashers are excluded from this measure. | Yes
The dishwasher must meet ENERGY STAR Program Requirements for Residential Dishwashers (Version 6.0).3 Please note that the offering is more stringent than the ENERGY STAR Most Efficient criteria. | Yes
E-5152 Data Collection Requirements | Yes | Site ID
E-5152 Data Collection Requirements | Yes | Equipment ID
E-5152 Data Collection Requirements | Yes | Manufacturer
E-5152 Data Collection Requirements | Yes | Model
E-5152 Data Collection Requirements | Yes | Serial Number
The following products are not eligible: packaged terminal air conditioners (PTACs), portable air conditioners, room air conditioner models with electric resistance heat as the primary heat source, and dehumidifiers. | Yes | Equipment Type
The room air conditioner must meet or exceed the current ENERGY STAR efficiency levels and carry the ENERGY STAR qualification, as per specification in the Measure Case Description. | Yes | Energy Star ID
E-5152 Data Collection Requirements | Yes | Capacity
E-5152 Data Collection Requirements | Yes | CEER
E-5152 Data Collection Requirements | Yes | ZC
E-5152 Data Collection Requirements | Yes | ClimateZone
This measure is applicable for all new and existing commercial or multifamily buildings of all vintages. For the commercial sector, this measure will apply to the following building types: general commercial, hotels, motels, small retail, and nursing homes. | Yes
A professional installer will be required for all installations of this product as the inlet natural gas line will have to be removed and reattached during installation. | Yes
All applicants must have their dryers on site | Yes | Dryer OnSite
A dryer that makes use of a common or dedicated steam system is not eligible. | Yes
The natural gas dryer must not be modified by any technology that would reduce the natural gas consumption beyond the manufacturer specifications. | Yes
This measure is not eligible for dryers with a capacity greater than 200 lbs or less than 20 lbs. For capacities outside of this range, a custom measure type is recommended. | Yes
Natural gas must be supplied by a California utility. | Yes
| Yes | Natural Gas
| Yes | Size
This measure is applicable for agricultural or commercial greenhouse of any vintage for the primary purpose of the production of nursery products, horticultural specialties, or ornamental products | Yes
Eligible products must meet the following requirements: Must be a single-layer interior curtain installed for heat retention. Must be installed in a gas-heated greenhouse facility. The facility must be a greenhouse with the primary purpose of agricultural use. The heat curtain must be a new curtain installed where none previously existed or a new curtain that is replacing an existing curtain that is no longer functional. The heat curtain must be installed above the conditioned area where the gas heat source provides hot air to plant and seed species. The heat curtain must have a natural gas savings rating that meets or exceeds 40%. The heat curtain must have a warranty/product life of five years. The installation must allow the curtain to be automatically or manually moved into place. | Yes
The square footage of the new heat curtain cannot exceed the square footage of the greenhouse floor. Additionally, any overhang and overlap of curtain material cannot be included in the square footage calculation. | Yes
The installation of infrared (IR) film must meet the following requirements: The IR film must be installed in a gas-heated greenhouse facility. The heating equipment type (building HVAC) must be specified in the implementation of the measure. The facility must be a greenhouse with the primary purpose of agricultural use. The film must be infrared, anti-condensate, polyethylene plastic with a minimum thickness of six thousandths of an inch. The IR film shall not be installed on the walls of the greenhouse. | Yes
The program should collect and verify the vintage of the building and the refrigeration multiplex system. | Yes | Date of Construction
The program should collect and verify the vintage of the building and the refrigeration multiplex system. The offerings are ineligible for multiplex systems majorly upgraded or installed after July 1, 2014 since the Title-24 code mandates the floating controls since July 1, 2014. | Yes | Date of Installation
The unit energy savings (UES) of anti-sweat heater (ASH) controls are based upon the installation of controllers on existing ASHs on low-temperature (case temperature below 32 °F) and medium-temperature case temperature (at or above 32 °F) display cases. | Yes | Temp Below 32F
The unit energy savings (UES) of anti-sweat heater (ASH) controls are based upon the installation of controllers on existing ASHs on low-temperature (case temperature below 32 °F) and medium-temperature case temperature (at or above 32 °F) display cases. | Yes
To qualify, the display case must be equipped with humidity-sensing controls that reduce the amount of power supplied to the heaters as the store dew point (DP) temperature decreases.. | Yes | Humidity Sensing Controls
Typically, power reduction occurs when relative humidity levels reach 55% and lower. Power reduction should decrease by at least 2% for every percentage the humidity falls below 55%. | Yes | Power Reduction
Equivalent technologies that can reduce or turn off ASHs based on the amount of condensation formed on the inner glass pane may also qualify. | Yes
This measure cannot be used in conjunction with the new refrigeration display case with doors. This measure cannot be used in conjunction with the special doors with low/no anti-sweat heat on low-temperature display case. | Yes | Doors Anti Sweat Heat Controls
This measure cannot be used in conjunction with the new refrigeration display case with doors. | Yes | Display Case Doors New
The program should collect and verify the vintage of the building and the refrigeration multiplex system. | No | Date of Construction
Equivalent technologies that can reduce or turn off ASHs based on the amount of condensation formed on the inner glass pane may also qualify. | Yes | ASH Controls
This measure cannot be used in conjunction with the new refrigeration display case with doors. This measure cannot be used in conjunction with the special doors with low/no anti-sweat heat on low-temperature display case. | No | Doors Anti Sweat Heat Controls
This measure cannot be used in conjunction with the new refrigeration display case with doors. | Yes | Temp Below 32F
Preponderance of evidence (POE) must be documented including: Customer/site information, specifications of existing equipment, proof the existing fan motor is still operating as intended, existing fan motor nameplate data with manufacturer date to confirm RUL, Replacement Motor nameplate information, if the equipment was replaced as a direct result of recommendations provided by the PA. | Yes | POE Docs
This measure cannot be used in conjunction with the following measures: SWAP011 Vending and Beverage Merchandise Controller SWCR002 Low-Temperature Display Case Doors With No Anti-Sweat Heaters SWCR018 Reach-In Refrigerator or Freezer, Commercial SWCR019 Low-Temperature Coffin To Reach-In Display Case Conversion SWCR021 Medium or Low-Temperature Display Case With Doors SWCR020 Medium-Temperature Open Display Case Retrofit | Yes
This measure is applicable in conditioned spaces in any existing commercial building type of any vintage. | Yes
The motor is installed as an evaporator fan motor in a refrigerated display case | Yes
Program implementers are encouraged to collect data on motor products installed under the rebate program, such as the type of display case receiving a new motor, motor size, motor cost, and labor cost. | Yes | Fridge Type
The installed motor is a permanent magnet electronically commutated motor (ECM) or permanent magnet synchronous AC (PMS) motor/fan. | Yes
The motor must be described as a low‐power or high efficiency model by the manufacturer | Yes | Motor Model
The new motor is the available product most closely matched to the original motor's speed and shaft output power (equivalent size) | Yes | Match Output power
Program implementers are encouraged to collect data on motor products installed under the rebate program, such as the type of display case receiving a new motor, motor size, motor cost, and labor cost. | Yes | Motor Size
Due to limited quantitative results in studies pertaining to refrigerated display cases on the market spread of motor efficiency within rather than across motor types (and motor size classes), program implementers are also encouraged to collect data on motor type and motor efficiency ratings that could be used in future programs to specify a high‐efficiency level for each motor type. | Yes | Motor Efficiency
Program implementers are encouraged to collect data on motor products installed under the rebate program, such as the type of display case receiving a new motor, motor size, motor cost, and labor cost. | Yes | Material Cost
Program implementers are encouraged to collect data on motor products installed under the rebate program, such as the type of display case receiving a new motor, motor size, motor cost, and labor cost. | Yes | Labor Cost
Pre-inspection of existing equipment is required. | Yes | Site Pre-Inspection
The existing motor system must be fully functional with no signs of replacement in the 12 months following the project application date. | Yes
This measure is applicable in any existing commercial building type 2008 and older. This is based on the assumption that walk-in equipment is at least as new as the building. | Yes | Date Installed
This measure cannot be used in conjunction with the evaporative fan controller for walk-in coolers and freezers. | Yes
The measure excludes motors greater than ½ horsepower. | Yes | Motor Size
The highest quality data collection would include associated motor sizes (nominal W) and a table of material and labor costs for each size of motor being installed. | Yes | CFM
To improve quality of cost-effectiveness calculations, programs implementing this measure should collect data on actual costs for materials and labor. The highest quality data collection would include associated motor sizes (nominal W) and a table of material and labor costs for each size of motor being installed. | Yes | Material Cost
To improve quality of cost-effectiveness calculations, programs implementing this measure should collect data on actual costs for materials and labor. The highest quality data collection would include associated motor sizes (nominal W) and a table of material and labor costs for each size of motor being installed. | Yes | Labor Cost
The automatic closer must be installed on a walk-in cooler or freezer that was manufactured before January 1, 2009. | Yes | Date of Manufacture
The measure case is specified as the installation of an automatic door closer on a walk-in cooler or a walk-in freezer door that was not previously equipped with one. | Yes | Existing Auto Close
The automatic door closer must be installed on the main insulated opaque door(s) of an existing walk-in cooler or freezer. | Yes | Location of Install
The automatic door closer must firmly close the door when it is within one inch of full closure. | Yes | Firm Close
- | Yes | Model Number
This measure is applicable to any existing non-residential building type in commercial sector, and the vintage categories listed below: Prior to 1978 (represented by typical year “1975”) 1978 through 1992 (“1985”) 1993 through 2001 (“1996”) 2002 through 2005 (“2003”) 2006 through 2009 (“2007”) 2010 through 2013 (“2011”) In addition, the following installations are ineligible: New construction installations | Yes | Building vintage
- | Yes | Building vintage
This measure is applicable to any existing non-residential building type in commercial sector, and the vintage categories listed below: Prior to 1978 (represented by typical year “1975”) 1978 through 1992 (“1985”) 1993 through 2001 (“1996”) 2002 through 2005 (“2003”) 2006 through 2009 (“2007”) 2010 through 2013 (“2011”) The program should collect and verify the vintage of the building and the refrigeration multiplex system. The offerings are ineligible for multiplex systems majorly upgraded or installed after July 1, 2014 since the Title-24 code mandates the floating controls since July 1, 2014. | Yes | Multiplex System Vintage
- | Yes | Refrigeration multiplex system
Products cannot be used in conjunction with measures that already incorporate floating head pressure controls. | Yes
In addition, the following installations are ineligible: Projects that only reprogram a controller; new hardware must be installed. | Yes
The controls only apply to refrigeration systems having multiplex compressor systems with existing control of the SCT at a fixed setpoint. The controls are added to float head pressure down to a lower pressure when conditions permit (i.e., changes control from fixed setpoint to floating setpoint). | Yes | Setpoint Controls
The new SCT setpoint must follow the ambient temperature by controlling condenser fans with variable-speed drives or by staging condenser fans. | Yes | Setpoint Adjust
In addition, the following installations are ineligible: Any improvements that will increase system energy use. | Yes
Additionally, the calculation of the design cooling load (tons) is to be based on connected display cases, walk-in coolers and freezers, cooled storage, and prep areas only. Sub-cooler loads and air conditioning loads are ineligible for consideration. | Yes | Design tons
This measure is applicable to any existing non-residential building type in commercial sector, and the vintage categories listed below: Prior to 1978 (represented by typical year “1975”) 1978 through 1992 (“1985”) 1993 through 2001 (“1996”) 2002 through 2005 (“2003”) 2006 through 2009 (“2007”) 2010 through 2013 (“2011”) In addition, the following installations are ineligible: New construction installations | No
This measure is applicable to any existing non-residential building type in commercial sector, and the vintage categories listed below: Prior to 1978 (represented by typical year “1975”) 1978 through 1992 (“1985”) 1993 through 2001 (“1996”) 2002 through 2005 (“2003”) 2006 through 2009 (“2007”) 2010 through 2013 (“2011”) In addition, the following installations are ineligible: New construction installations | Yes
In addition, the following installations are ineligible: Any improvements that will increase system energy use. | No
Measure Description | Yes | Insulation on Bare Suction Pipes
The eligibility requirements are as follows: • The refrigeration suction pipe on existing equipment must be no more than 1-5/8 inches in diameter. • This measure is applicable to bare suction pipes insulated with closed-cell nitrite rubber or equivalent with at least ¾-inch for medium-temperature and 1-inch for low-temperature systems. • Insulation R-values must be greater than or equal to R-3.2 for medium-temperature cooler pipes. • Insulation R-values must be greater than or equal to R-4.3 low-temperature freezer pipes. | Yes | Size
The eligibility requirements are as follows: • The refrigeration suction pipe on existing equipment must be no more than 1-5/8 inches in diameter. • This measure is applicable to bare suction pipes insulated with closed-cell nitrite rubber or equivalent with at least ¾-inch for medium-temperature and 1-inch for low-temperature systems. • Insulation R-values must be greater than or equal to R-3.2 for medium-temperature cooler pipes. • Insulation R-values must be greater than or equal to R-4.3 low-temperature freezer pipes. | Yes | R-value Installed Greater
Measure Description | No | Insulation on Bare Suction Pipes
Measure Description | No | PreExisting Bare Suction Pipe
The retrofit of glass doors, or glass doors with LED lights, for a medium-temperature, open-vertical, refrigerated display case must be added to an existing open-vertical, medium temp display case. The complete removal of the existing display case and replacing it with a new case with glass doors is not eligible | Yes
In addition to retrofitting the doors and door frames, the measure may require changes to the refrigeration system serving the affected display case(s). These changes may include but are not limited to: replacing the expansion valve and/or evaporator pressure regulating valve, adjusting the evaporator temperature/pressure set point, resizing refrigeration piping, replacing the flood back valve on the condenser, resizing the coil/piping on applicable heat reclaim systems, and replacing or removing compressors. These potential changes stem from the significant reduction in the overall refrigeration load. Due to the complexity in determining which system alterations will be required at a site to maintain optimum system performance, a refrigeration contractor with design experience should be consulted before proceeding with the retrofit. | Yes
Anti-sweat heat (ASH) may not be present in the glass doors or door mounting. (Two out of three manufacturers stated that their products did not contain ASH in the door or mullion. Thus, it was decided to specifically prohibit door and frame heat, as it does not appear necessary in medium-temperature applications.) | No | Doors Anti Sweat Heat Controls
Total lighting power in the measure case may not exceed total lighting power in the base case (Several manufacturers interviewed stated that most retrofits include a switch to more efficient LED case lighting, but not an overall increase in lighting power density.) | Yes | Power Density
Eligible Building Types This measure is applicable for the following existing building types: Education – University, Health/Medical – Hospital, Manufacturing – Biotech, and Manufacturing – Pharmaceuticals. | Yes | Building Type
Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | Freezer Type
Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | Setpoint storage temperature range
Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | ENERGY STAR Qualified?
Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | Daily Energy Use
Refrig-Freezer-High Efficiency Ultra-Low Temperature (ULT, -80 °C) Freezers, 15 to <24 ft3 | Yes | Freezer Volume (ft^3)
Refrig-Freezer-High Efficiency Ultra-Low Temperature (ULT, -80 °C) Freezers, 24 to 29 ft3 | Yes | Freezer Volume (ft^3)
No requirement listed | Yes
Eligible products include ENERGY STAR®-qualified commercial reach-in refrigerators and freezers that replace a standard efficiency unit of the same configuration and capacity. | Yes | Energy Star Qualified
Units with remote refrigeration systems do not qualify and used or rebuilt equipment is not eligible. | Yes | Remote Refrigeration System
Eligible products include ENERGY STAR®-qualified commercial reach-in refrigerators and freezers that replace a standard efficiency unit of the same configuration and capacity. | Yes | New Same as Existing
Equipment must be new | Yes | New Equipment
All coffin replacements with a reach-in display case must meet the specifications in the Measure Case Description. The measure is applicable to replace any existing coffin that is less than or equal to code: • If the display width is less than or equal to 3 feet, the coffin must be replaced by a reach-in case that is ⅟4 of the total length of the coffins or less. • If the display width is greater than 3 feet, the coffin must be replaced by a reach-in case that is ⅓ of the total length of the coffin or less. | Yes | Existing Unit Width
All coffin replacements with a reach-in display case must meet the specifications in the Measure Case Description. The measure is applicable to replace any existing coffin that is less than or equal to code: • If the display width is less than or equal to 3 feet, the coffin must be replaced by a reach-in case that is ⅟4 of the total length of the coffins or less. • If the display width is greater than 3 feet, the coffin must be replaced by a reach-in case that is ⅓ of the total length of the coffin or less. | Yes | Existing Unit Length
The replacement case must include triple-pane doors with low or no anti-sweat heat or anti-sweat-heat controls. | Yes | Doors Anti Sweat Heat Controls
- | Yes | New Equipment
The medium-temperature display case must meet or exceed specifications and efficiency requirements in the Measure Case Description and Code Requirements through the use of a high efficiency evaporator coil. | Yes | Evaporator Coil
The new display case must replace an existing medium-temperature, open, vertical refrigerated display case of the same style | Yes | New Same as Existing
The manufacturer spec sheet for the new display case must be submitted to the Program for review to confirm eligibility. | Yes | Manufacturer Cut Sheet Submitted
This measure is applicable for supermarkets and grocery stores with stand-alone and/or multiplex compressor racks that provide refrigeration to remote display cases and walk-in coolers/freezers. This measure is applicable to supermarkets and grocery stores with both medium-temperature and low-temperature open multi-deck refrigeration cases. Must replace an existing, open, multi-deck display case with a new reach-in unit with doors, electronically commutated motor (ECM) evaporator fan(s), and LED lighting. | Yes | Display Case Replace
Refurbished cases are not eligible unless compliant with the 2012 Federal Efficiency Standards (see Code Requirements). | Yes
Medium-temperature cases must have no heat in the door. Heat is allowed in the frames of medium temperature cases. | Yes
Low-temperature case door and frame heaters combined may not consume more than 50 W/ft of case length. | Yes | Doorframe Measurement
The new case length must be less than or equal to the original case length. | Yes | New Case Length
This measure is only for display cases served by a remote refrigeration system. | Yes | Remote Refrigeration System
Specialty deli cases, custom coolers/freezers, and walk-in boxes with reach-in doors are not eligible. | Yes | Category
Display case replacements that are part of large-scale store remodels and any new construction projects should be revised to be custom measures. Large-scale remodels are defined as any project involving 50% of the linear feet of refrigerated casework or 32 linear feet of casework replacements, whichever is less. | Yes | Large Scale Remodel
Salvage, disposal or photographic records of replaced equipment should be part of program application requirements when early replacement or open-to-closed case conversion savings are being utilized to ensure the correct baseline is assumed for these measures. | Yes
All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. * Half-size gas convection ovens are excluded from ENERGY STAR. | Yes | Energy Star Qualified
Used or rebuilt equipment is not eligible. Half-size gas convection is not eligible. | Yes
All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. * Half-size gas convection ovens are excluded from ENERGY STAR. | Yes
Measure Description | Yes | Size
Measure Description | Yes
Energy Efficiency Requirements of Commercial Convection Ovens Table | Yes
All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. | Yes
Energy Efficiency Requirements of Commercial Convection Ovens Table | Yes | EFFICIENCY
All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. | Yes | Idle Energy Rate
Used or rebuilt equipment and other dishwasher types (conveyor, under-counter, flight-type) are not eligible. | Yes
This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Water Consumption
This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate
This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes
Manufacturer | Yes | Manufacturer
Model | Yes | Model
Used or rebuilt equipment is not eligible. | Yes
This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Production Capacity
This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes
This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Idle Energy Rate
This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Efficiency
This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Production Capacity
This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Idle Energy Rate
This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Efficiency
Double-sided griddles and used or rebuilt equipment are not eligible. | Yes
This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | Energy Star Qualified
This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | Size
This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | Idle Energy Rate
This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | EFFICIENCY
New commercial steam cookers must meet the ENERGY STAR Program Requirements for Commercial Steam Cookers, Version 1.2 or the specification in the Measure Case Description. | Yes | Energy Star Qualified
New commercial steam cookers must meet the ENERGY STAR Program Requirements for Commercial Steam Cookers, Version 1.2 or the specification in the Measure Case Description. | Yes | Size
New commercial steam cookers must meet the ENERGY STAR Program Requirements for Commercial Steam Cookers, Version 1.2 or the specification in the Measure Case Description. | Yes | EFFICIENCY
New commercial steam cookers must meet the ENERGY STAR Program Requirements for Commercial Steam Cookers, Version 1.2 or the specification in the Measure Case Description. | Yes | Idle Energy Rate
Water-cooled ice machines and used or rebuilt equipment are not eligible. | Yes
Program qualifying ice machines are defined by equipment type and daily ice harvest rate. The efficiency specifications must meet the requirements listed in the Measure Case Description for batch and continuous machines, per the ENERGY STAR V3.0 Program Requirements for Automatic Commercial Ice Makers. | Yes
The entire AHRI-tested ice making system must be purchased. Remote machines must be purchased with qualifying remote condenser or remote condenser/compressor unit. | Yes | Entire AHRI System Purchased
Only air-cooled machines (self-contained, icemaker heads, or remote condensing) are eligible. Water-cooled ice machines and used or rebuilt equipment are not eligible. | Yes | Air Cooled Unit
Required for defining Energy Use | Yes | Ice Machine Production Type
Required for defining Energy Use | Yes | Production Per Day
The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use
Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use
Any cabinets considered in this measure must have an electric resistance heating element, passive holding cabinets with no heating elements are not eligible. | Yes | Gas_Electric
Used or rebuilt equipment are not eligible. | Yes
Qualifying cabinets must not exceed the maximum idle energy rate of 25 W/ft3 for full-size cabinets and 35 W/ft3 for half-size cabinets, in accordance with the American Society for Testing and Materials (ASTM) Standard Test Method for the Performance of Hot Food Holding Cabinets (F2140). | Yes | Idle Energy Rate
This measure includes new full-size (≥ 15 ft3) and half-size (< 15 ft3) insulated food holding cabinets. | Yes | Size
Eligible holding cabinets must be listed on the Food Service Technology Center (FSTC) qualified product list (https://fishnick.com/saveenergy/rebates/). | Yes | FSTC Listed
All measures must be electric hot food holding cabinets that are fully insulated (i.e., on all sides) and have solid or transparent doors designed to maintain the temperature of hot food that has been cooked using a separate appliance. This measure does not include cook-and-hold or retherm equipment. | Yes
Used or rebuilt equipment are not eligible. | Yes | New Equipment
This measure does not include cook-and-hold or retherm equipment. Any cabinets considered in this measure must have an electric resistance heating element, passive holding cabinets with no heating elements are not eligible. | Yes
This measure includes new commercial gas conveyor ovens that exceed baking energy efficiency of ≥ 42% and have an idle energy rate ≤ 57,000 Btu/hr, utilizing ASTM Standard F1817. | Yes | Size
This measure includes new commercial gas conveyor ovens that exceed baking energy efficiency of ≥ 42% and have an idle energy rate ≤ 57,000 Btu/hr, utilizing ASTM Standard F1817. | Yes | Idle Energy Rate
This measure includes new commercial gas conveyor ovens that exceed baking energy efficiency of ≥ 42% and have an idle energy rate ≤ 57,000 Btu/hr, utilizing ASTM Standard F1817. | Yes | EFFICIENCY
This measure is a new commercial on-demand hand-wrap machine that replaces a conventional or always-on hand-wrap machine. The measure must use either a mechanical or optical control system. | Yes | Control System
This measure is a new commercial on-demand hand-wrap machine that replaces a conventional or always-on hand-wrap machine. The measure must use either a mechanical or optical control system. | Yes | Replace
This measure is a new commercial on-demand hand-wrap machine that replaces a conventional or always-on hand-wrap machine. The measure must use either a mechanical or optical control system. | Yes | On Demand Hand Wrap Machine
- | No | Manufacturer
- | No | Model
Used or rebuilt equipment are not eligible. | No | New Equipment
This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | No | Type
This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | No | Energy Star Qualified
This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | No | Idle Energy Rate
This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | No | EFFICIENCY
Used or rebuilt equipment are not eligible. | Yes | New Equipment
This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | Type
This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | Energy Star Qualified
This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | Idle Energy Rate
This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | EFFICIENCY
Used or rebuilt controls are not eligible. | Yes
This measure pertains to the purchase and installation of a new commercial kitchen exhaust hood control system installed in an existing or a new dedicated commercial kitchen exhaust hood and makeup air system. Specific requirements include: • The measure requires the installation of temperature sensor(s) in the hood exhaust collar or within the hood, and/or an optic sensor on the end of the hood or within the hood that senses cooking conditions and allows the system to automatically vary the rate of exhaust and make-up (ventilation) air by adjusting unit fan speeds accordingly. • The installation of a DCKV must include a temperature or optic sensor that senses cooking conditions. • The control system must be used in conjunction with a variable-speed drive (VSD) on the fan motor. • Installations in a new exhaust hood must have a total kitchen hood airflow ≤ 5,000 cfm. • If installed in an existing exhaust hood > 5,000 cfm, the existing hood must have been installed before July 1, 2014, when the 2013 California Building Energy Efficiency Standards (Title 24) standards came into effect. See Code Requirements | Yes
- | No | HP
Good to have | Yes | Size
Used or rebuilt equipment are not eligible. | Yes
This measure is restricted to operations with natural gas water heaters only. | Yes | Gas PRSV
This measure is defined as a new commercial-grade PRSV with a maximum flow rate ≤ 1.07 gpm that replaces a PRSV with a maximum flow rate of 1.20 gpm for a spray force of > 5.0 ozf and ≤ 8.0 ozf; and as a new commercial-grade PRSV with a maximum flow rate ≤ 0.75 gpm that replaces a PRSV with a maximum flow rate of 1.00 gpm for a spray force of < 5.0 ozf. | Yes | Gas PRSV flow rate
Used or rebuilt equipment is not eligible. | Yes
This measure includes new commercial gas single and double rack ovens tested to meet or exceed baking energy efficiency of 50%. | Yes | Size
This measure includes new commercial gas single and double rack ovens tested to meet or exceed baking energy efficiency of 50%. | Yes | EFFICIENCY
The replacement automatic conveyor broiler must have a catalyst and an input rate less than 80 kBtu/hr or a dual stage or modulating gas valve with a capability of throttling the input rate below 80 kBtu/hr. | Yes | Existing Conveyor Input Rate
The existing (base case) broiler must be an automatic conveyor broiler than can maintain a temperature above 600 °F with a tested idle rate greater than: • 40 kBtu/hr for a belt narrower than 20" • 60 kBtu/hr for a belt between 20 and 26" • 70 kBtu/hr for a belt wider than 26" | Yes | Existing Conveyor Temp
The conveyor broiler must be replaced by a conveyor broiler similar in size or smaller. | Yes | Existing Conveyor Replaced
Installation shall comply with all policies, codes and regulations within the installation territory. | Yes
Used or rebuilt equipment is not eligible. | Yes | New Equipment
Other dishwasher types (conveyor, door-type, flight-type) are not eligible. | Yes | Undercounter dishwasher
This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption
This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate
This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | EFFICIENCY
This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes
The measure case (replacement) underfired broiler must have an input rate ≤ 22 kBtu/hr/len-ft while maintaining a surface temperature of 600 °F, per ASTM F1695 standard. | Yes | ASTM standard
The base case broiler must be similar size or larger than the replacement unit. | Yes | Broiler size
To qualify as a high performance conveyor toaster, the unit must meet the energy per sandwich requirement specified in the Measure Case Description. | Yes
E-5152 Data Collection Requirements | Yes | RefNum
E-5152 Data Collection Requirements | Yes | Measure Size Category
E-5152 Data Collection Requirements | Yes | RetailPrice
Required for SW Program | Yes | ZC
Required for SW Program | Yes | ClimateZone
Wall furnaces that are direct-vent systems that mount on an outside wall are not eligible. | Yes | -
Gravity wall furnaces ≤ 19,000 Btu/hr and ≥ 60,000 Btu/hr are not eligible | Yes | Gas Input Rating (Btu/hr)
Fan type wall furnaces ≤ 19,000 Btu/hr and ≥ 42,000 Btu/hr are not eligible | Yes | Gas Input Rating (Btu/hr)
E-5152 Data Collection Requirements | Yes | AFUE
The purchase invoice must be provided as a proof that the wall furnace has been purchased to replace a previously existing unit. Additionally, the customer must agree to a post measure installation inspection. | Yes | -
The customer must agree to a post installation inspection. | Yes
Proof of purchase of a gravity wall furnace manufactured with an integrated intermittent pilot light must be provided. | Yes
Eligibility requirements for this measure are: • This measure pertains to gravity wall furnaces manufactured with integrated IPL controls, furnaces with a standing pilot light, and any fireplace with standing pilot light. • A furnace manufactured with integrated IPL controls can only replace a gravity wall furnace. • The IPL controls shall be capable of either using a battery or voltage line to effectively operate as intended. | Yes
Implementation and installation requirements are: • For direct install installations, the wall furnace or fireplace insert shall be functional prior to the IPL retrofit. • For direct install installations, the IPL control cannot replace an existing functional or non- functional pilot light control on a furnace or fireplace insert. • Any technology manufacturer qualifies for measure offerings specified, if safety and all other regulations are met and the technology is commercially available. | Yes
Retire | Yes | Cap-kBtuh
Retire | Yes | OA Reset Control (degrees in Fahrenheit)
Good to have | Yes | Rated Input (Btuh)
Retire | Yes | Size
The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%)
The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes
The boiler must be used for space heating to induce human comfort, as defined by the California Appliance Efficiency Regulations (Title 20) and Building Energy Efficiency Standards (Title 24). | Yes | Title 24
The installation address must have a commercial natural gas account. | Yes
This measure is applicable for the following existing and new commercial and multifamily installations. | Yes
| Yes | Serial Number
| Yes | RefNum
| Yes | RetailPrice
| Yes | ZC
| Yes | ClimateZone
The installation address must have a commercial natural gas account. | Yes | -
This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | -
E-5152 Data Collection Requirements | Yes | Rated Input (Btuh)
The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Combustion Efficiency (%)
Good to have | Yes | Nominal Capacity (Tons)
Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton)
Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton)
All measures related to constant speed screw, constant speed centrifugal, and frictionless chillers are excluded due to the stringency of the tiers specified for the 2020 update of the Database of Energy Efficient Resources (DEER) and equipment availability in the market. | Yes
Required for defining Energy Use | Yes | Host Equipment
This measure does not apply if the rooftop unit (RTU) has a fully operational and/or non-snapdisc sensor and is adjusted to the appropriate changeover setpoint based on the number of thermostat stages available for cooling. | Yes
This measure requires field documentation of the existing conditions that verify the measure was necessary and that the measure was successfully applied. | Yes | Field docs
Additional technician verification of thermostat wiring and the number of cooling stages that should be performed to ensure that the first stage of cooling is dedicated to economizer operation and two-stage thermostat operation is enabled where possible. | Yes | Tech verification
The controller changeover setpoint should be adjusted appropriately based on the available number of thermostat cooling stages. | Yes | Changeover Setpoint
Contractors and technicians that implement the measure must meet all certification and training requirements in accordance with program requirements. | Yes | Cert and Train
Contractors and technicians that implement this measure must ensure that the existing unit does not already have the supply fan in automatic mode or switched OFF during unoccupied periods. This measure does not apply if the unoccupied supply fan operation is already set to “Auto” or intermittent. | Yes | Switched Off
The measure SWHC009C (cDXHP) excludes building type WRf. | Yes
Measure offering SWHC009D (cPVVG) excludes building type Asm, EPr, ERC, Gro, MLI, RFF, RSD, RtL, RtS, SCn, WRf | Yes
The measure is only applicable for classrooms in education primary schools (EPr), education secondary schools (ESe), and education re-locatable classrooms (ERC). This measure is not applicable for education community colleges, and education universities, unless these buildings have relocatable classrooms with packaged HVAC units. This measure is applicable to all vintages. | Yes | Installation Epr
The measure requires installation of an HVAC occupancy sensing thermostat in the classroom. This control equipment includes, but is not limited to: • An occupancy sensing thermostat • An occupancy sensor (wired or wireless) • Wiring (if wired) • Signal receiver and power pack (if wireless) | Yes | System Include
The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Yes
Good for Tracking | Yes | RefNum
- | Yes | Evaporator Manufacturer
- | Yes | Evaporator Model
Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes | System Type
Good to have for tracking | Yes | Serial Number
Good to have for tracking | Yes | RetailPrice
Required for UpDeemed Programs | Yes | ZC
Required for UpDeemed Programs | Yes | ClimateZone
Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes
Central systems and domestic hot water systems are not eligible. Package terminal air conditioning units, which are units manufactured for installation through a wall or window and are usually ≤ 2 tons, are not eligible. | Yes
Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes
Field inspections should be performed to verify the condenser/unit model number for quality assurance purposes. | Yes
The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Yes | -
Data collection requirements for midstream and upstream deliveries, when possible, the program administrator (PA) shall claim the “specific building type savings” in which the equipment will be installed and submit that information at claims level on CEDARS website. In cases where there is no “building type” information available for a given project, program administrator shall claim the weighted savings of “Com” building type.” | Yes | -
Data Collection Requirements For upstream and midstream programs, data collection requirements are as follows: R1503 Site ID - A unique identifier for the installed location of the incentivized equipment Equipment ID - A unique identifier for each unit of incentivized equipment on the site Measure Size Category - General size or capacity range specific to each measure type Equipment manufacturer Equipment model number Rated capacity Rated efficiency unit - The engineering unit basis for the efficiency or performance rating Rated efficiency - Efficiency or performance rating value for the rated efficiency unit basis Quantity per sales transaction, project or site Existing equipment type (i.e., AC or HP) for the NR MAT | Yes | Site ID
Data Collection Requirements For upstream and midstream programs, data collection requirements are as follows: R1503 Site ID - A unique identifier for the installed location of the incentivized equipment Equipment ID - A unique identifier for each unit of incentivized equipment on the site Measure Size Category - General size or capacity range specific to each measure type Equipment manufacturer Equipment model number Rated capacity Rated efficiency unit - The engineering unit basis for the efficiency or performance rating Rated efficiency - Efficiency or performance rating value for the rated efficiency unit basis Quantity per sales transaction, project or site Existing equipment type (i.e., AC or HP) for the NR MAT | Yes | Equipment ID
Data Collection Requirements For upstream and midstream programs, data collection requirements are as follows: R1503 Site ID - A unique identifier for the installed location of the incentivized equipment Equipment ID - A unique identifier for each unit of incentivized equipment on the site Measure Size Category - General size or capacity range specific to each measure type Equipment manufacturer Equipment model number Rated capacity Rated efficiency unit - The engineering unit basis for the efficiency or performance rating Rated efficiency - Efficiency or performance rating value for the rated efficiency unit basis Quantity per sales transaction, project or site Existing equipment type (i.e., AC or HP) for the NR MAT | Yes | Measure Size Category
All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type
Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | System Type
E-5152 Data Collection Requirements | Yes | Evaporator Manufacturer
E-5152 Data Collection Requirements | Yes | Evaporator Model
Required for UpDeemed Programs | No | Refrigerant Type
Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | -
Central systems and domestic hot water systems are not eligible. Package terminal air conditioning units, which are units manufactured for installation through a wall or window and are usually ≤ 2 tons, are not eligible. | No | -
E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh)
Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER
Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER
Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | COP
Field inspections should be performed to verify the condenser/unit model number for quality assurance purposes. | Yes | -
Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes | -
Central systems and domestic hot water systems are not eligible. Package terminal air conditioning units, which are units manufactured for installation through a wall or window and are usually ≤ 2 tons, are not eligible. | Yes | -
Good to have | Yes | -
Need to have for validation | Yes | -
Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | -
Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type
E-5152 Data Collection Requirements | No | Refrigerant Type
Need to have for validation | No | Efficiency Type
Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER
This measure is applicable for the following nonresidential building types: Education – Secondary School Education – Community College Education – University Health/Medical – Hospital Health/Medical – Nursing Home Lodging – Hotel Office – Large Retail – Multistory Large Grocery – Grocery | Yes | -
This measure requires the installation of a VSD and associated controls on a motor driving a ventilation fan. Eligibility requirements include: • The fan must be ≤ 100 hp. • As an add-on equipment installation, the VSD must be applied to the HVAC supply or return air system. • Any other throttling devices, such as inlet vanes or bypass dampers, and throttling valves, must be removed or permanently disabled. | Yes | Input Rating (HP)
This measure requires the installation of a VSD and associated controls on a motor driving a ventilation fan. Eligibility requirements include: • The fan must be ≤ 100 hp. • As an add-on equipment installation, the VSD must be applied to the HVAC supply or return air system. • Any other throttling devices, such as inlet vanes or bypass dampers, and throttling valves, must be removed or permanently disabled. | Yes | VFD Installed Existing HVAC Supply_Return
This measure requires the installation of a VSD and associated controls on a motor driving a ventilation fan. Eligibility requirements include: • The fan must be ≤ 100 hp. • As an add-on equipment installation, the VSD must be applied to the HVAC supply or return air system. • Any other throttling devices, such as inlet vanes or bypass dampers, and throttling valves, must be removed or permanently disabled. | Yes | Throttling Devices
Replacement of multiple-speed or variable speed motors (VSM) are not eligible. | Yes | Installation Include VSM
Variable frequency drives on cooling tower fans are not eligible. | Yes | VFD Installed Cooling Tower Fans
The energy and demand impacts of this measure are applicable only to commercial buildings with chiller equipment serving space comfort. Other chiller measures serving non-space comfort and/or processes and/or industrial applications shall be evaluated and incentivized under custom programs. | Yes
Per Section 140.4 (j) of the 2019 California Building Energy Efficiency Standards (Title-24), chilled water plants shall not have more than 300 tons provided by air cooled chillers, except where the water quality at the building site fails to meet the manufacturer specifications for the use of water-cooled chillers, chillers that are used to charge a thermal energy storage system with a design temperature of less than 40 °F or systems serving healthcare facilities. | Yes
Required for determining eligibility | Yes | Capacity (Tons)
Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency Rating
Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value
The energy and demand impacts of this measure are applicable only to commercial buildings with chiller equipment serving space comfort. Other chiller measures serving non-space comfort and/or processes and/or industrial applications shall be evaluated and incentivized under custom programs. | Yes | ChillerPurpose
Per Section 140.4 (j) of the 2019 California Building Energy Efficiency Standards (Title-24), chilled water plants shall not have more than 300 tons provided by air cooled chillers, except where the water quality at the building site fails to meet the manufacturer specifications for the use of water-cooled chillers, chillers that are used to charge a thermal energy storage system with a design temperature of less than 40 °F or systems serving healthcare facilities. | Yes | Size Exemption
Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | FL EER
Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | IPLV
This measure requires field documentation of the existing conditions that verify the measure was necessary and that the measure was successfully applied. Contractors and technicians that implement these measures must ensure that the existing unit does not already have these measures. This measure must replace existing equipment with the addition of controls for existing units. | Yes
Terms and conditions are noted below. Other terms and conditions are set by individual programs. • The existing system must be packaged single zone DX cooling unit with gas heat, cooling only unit, or heat pump. • The existing system must have a constant volume supply fan. • The existing system must have an operable airside economizer installed, and economizer high limit must be optimized for the climate per Title 24 2016 Table 140.4-B, adapted below in Table 2 for reference. • Maintenance, and repairs to economizer should be completed prior to or in conjunction with this measure. | Yes
This measure does not apply if the rooftop unit (RTU) has a fully operational and/or non-snapdisc sensor and is adjusted to the appropriate changeover setpoint based on the number of thermostat stages available for cooling. | Yes
This measure does not apply if the unoccupied supply fan operation is already set to “Auto” or intermittent. | Yes
Implementation requires proper setup of the damper limits and fan speeds in order to provide ventilation in accordance with Title 24 2016 (see Code requirements). Total unit airflow must be verified for at least one of the fan speeds. The percentage of outdoor air must be verified for each of the unit operating modes, including heating and cooling for each stage as well as the ventilation only mode. | Yes
This measure is applicable for all nonresidential buildings served by unitary direct expansion (DX) and split systems that do not serve process or refrigeration loads. The target market for this measure includes commercial buildings served by packaged single zone HVAC units, sometimes referred to as rooftop units (RTUs). | Yes
This measure is applicable for package rooftop HVAC systems in the following nonresidential building types. The measure is eligible for all vintages (old, existing, recent, and new). | Yes
Good to have for data collection | Yes | Capacity (Tons)
- | Yes | Size
Only “A” and “B” V-belts, the two types typically used in rooftop units, are applicable for this measure. | Yes | Belt Type
A cogged V-belt can be installed on supply air and return air fans in rooftop units that do not already have a cogged V-belt. | Yes | Cogged V Belt
A cogged V-belt can be installed on supply air and return air fans in rooftop units that do not already have a cogged V-belt. | Yes | Belt Type
This measure is applicable for package rooftop HVAC systems in the following nonresidential building types. The measure is eligible for all vintages (old, existing, recent, and new). Assembly, Education - Community College, Education - Primary School, Education - Secondary School, Education - University, Education - Relocatable Classroom, Health/Medical - Hospital, Lodging - Hotel, Lodging - Motel, Manufacturing - Bio/Tech, Manufacturing - Light Industrial, Health/Medical - Nursing Home, Office Large, Office Small, Restaurant - Fast Food, Restaurant - Sit-Down, Retail - Multistory Large, Retail - Small, Storage - Conditioned, Grocery | Yes
All existing building vintages are eligible for all building types; new construction is only available for nonresidential building types. Eligible building types include: Health/Medical - Nursing Home, Lodging - Hotel, Lodging - Guest Rooms, Lodging - Motel, Manufacturing - Bio/Tech, Manufacturing - Light Industrial, Office - Large, Office - Small, Restaurant - Fast-Food, Restaurant - Small, Warehouse - Refrigerated, Residential Multi-Family (Common), Residential Multi-Family (Dwelling Unit), Residential Single Family. | Yes
Ductless mini-split AC are not eligible. | Yes | Mini-Split AC
The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes
The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | EER
The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating
The measure case is defined as a package terminal air conditioner (PTAC) or a package terminal heat pump (PTHP) that is through-the-wall, self-contained, with a cooling capacity ≤ 2 tons (≤ 24 kBtu/hr) and an energy efficient rating (EER) that is 20% higher than the base case. | Yes | EER Exceed Code
Ductless mini-split AC are not eligible. | Yes | High Eff PTAC DX Unit Installed
Required for measure case description check, Ductless mini-split AC are not eligible. | Yes | Mini-Split AC
Required for measure case description check, Ductless mini-split AC are not eligible. | Yes
The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Capacity (BTU/hr)
Both automated (logic-based) fan controllers and manually set time-delay fan controllers are eligible. | Yes | Type
The installation of a manually set time-delay fan controller requires the invoice and/or installation contract that verifies the equipment was installed by a qualified HVAC contractor. | Yes | Manually Set Time Delay
This measure only applies to a fully functional central residential air conditioning unit equipped with cooling/evaporator (DX) coils. | Yes | Working HVAC
All installations shall comply with all current applicable regulations, code, and standards including (but not limited to) the California Building Energy Efficiency Standards (Title 24), the California Appliance Efficiency Regulations (Title 20), and the National Electrical Code (NEC). | Yes | Code
A fan controller used for solely optimizing and improving heating efficiency including those for gas furnaces is not eligible. | Yes | Fan Controller
The baseline air conditioning system cannot be equipped with a hardware based built-in delay controller. | Yes | Baseline AC
Eligibility requirements for this measure include: • The customer must have natural gas distributed to the installation address. • The new furnace must replace an existing gas furnace. | Yes
This measure must meet the minimum AFUE efficiency ratings in the Measure Case Description. | Yes
A brushless DC motor, also known as an electronically commutated motor (ECM) may be eligible for the high-efficiency furnace with a variable speed motor (VSM). | Yes
A licensed contractor must verify the furnace has a built-in VSM, if applicable. | Yes
A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | Yes
Eligibility requirements for this measure include: • The customer must have natural gas distributed to the installation address. • The new furnace must replace an existing gas furnace. | Yes | ActiveGas
Eligibility requirements for this measure include: • The customer must have natural gas distributed to the installation address. • The new furnace must replace an existing gas furnace. | No | -
A brushless DC motor, also known as an electronically commutated motor (ECM) may be eligible for the high-efficiency furnace with a variable speed motor (VSM). | No | -
E-5152 Data Collection Requirements | Yes | Capacity (BTU/hr)
This measure must meet the minimum AFUE efficiency ratings in the Measure Case Description. | Yes | AFUE
A licensed contractor must verify the furnace has a built-in VSM, if applicable. | No | -
A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | No | -
The HVAC system must be functional/operable and drawing power. | Yes | Operational
The HVAC system shall be capable of delivering a supply air flow rate of at least 350 cfm/ton. The minimum 350 cfm/ton airflow requirement ensures that the refrigerant system can be properly diagnosed and charged as part of a maintenance service. If the system is not delivering 350 cfm/ton upon initial inspection, an assessment should be made to determine if the system will be able to deliver 350 cfm/ton by implementing repairs related to airflow. If it is determined that the supply fan and duct system in place do not have the capability to deliver at least 350 cfm/ton with or without airflow repairs, the savings in this measure are invalid. | Yes | Air Flow Rate
The replacement brushless fan motor (BFM) motor capacity and rated voltage shall match that of existing fan motor being replaced. | Yes | New Match Existing
The replacement BFM motor and motor controls assembly shall be “UL Listed.” | Yes | UL Listed
The replacement BFM motor shall have a warranty of at least two years from date of installation. | Yes | Warranty
The measure shall include HVAC system start-up. During the start-up, the installer shall ensure that system maintain programmed level airflows under both cooling and/or heating and that these are adequate. | Yes | HVAC Start Up
The installation (as applicable) shall comply with all applicable regulations including but not limited to California Building Energy Efficiency Standards (Title-24), California Electrical Code, and NEC, and any applicable local jurisdiction regulations. See Code Requirement | Yes | Regulations
This measure only supports HVAC (evaporator) fan motors with nominal capacities of ½-hp and/or less typically serving HVAC systems with nominal capacities of 3.5 ton (or less). | Yes | HVAC EVAP Fan
The measure applies to units with shaded pole (SHP) or permanent split capacitor (PSC) motors currently installed. As stated previously, the replacement motor is to be a brushless direct current motor with selectable speed control designed to replace a PSC motor in a residential direct drive fan application. | Yes | Replacement
The customer must use the thermostat to control heating and/or cooling equipment supplied by fuels provided by the program administrator: • For single-fuel utilities (or dual-fuel utilities in a portion of their service area where they only supply one fuel), only savings for the applicable delivered fuel may be claimed • Eligible heating equipment: gas forced-air furnace, electric forced-air furnace, heat pump • Eligible cooling equipment: central air conditioning | Yes | Eligible Home
Unknown | Yes | Purchase Date
Unknown | Yes | Receipt
The smart thermostat must be in full compliance with the ENERGYSTAR® Program Requirements and Product Specification for Connected Thermostats products Version 1.0 or later. R950 | Yes | Energy Star
The program administrator (PA) shall employ QA/QC procedures to ensure that the thermostat is installed in an eligible home and is attached to the type of HVAC equipment that is being incentivized, whether it is for natural gas or electricity savings. | Yes
The PA shall confirm that the customer has a newly purchased smart thermostat. At minimum, the PA shall obtain a copy of the thermostat sales receipt and the PA shall confirm the purchase date is on or after the program start date. | Yes
The PA shall determine customer eligibility prior to rebate payment. Upon request, all data associated with determining eligibility shall be provided to Energy Division of the California Public Utilities Commission (CPUC). All PAs shall extend this requirement to all third-party vendors that assist PAs with determining customer eligibility. To the extent that they are used to determine eligibility, data regarding dates of purchase, location of home, customer HVAC equipment type, pre-installation HVAC energy use, etc. shall be made available. | Yes
The smart thermostat must be in full compliance with the ENERGYSTAR® Program Requirements and Product Specification for Connected Thermostats products Version 1.0 or later. | Yes | Energy Star ID
To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Building type. For upstream or midstream measures where building type is not available, the “Res” building type shall be assumed. Climate zone Existing HVAC system type In any event, data collection shall fully comply with both general and device eligibility requirements. | Yes | Existing Equipment Type
Per Impact Evaluation of Smart Thermostats. Residential Sector - Program Year 2019 guidance, direct install projects already equipped with smart thermostat technology and/or included the installation of smart thermostat technology shall not be bundled with (or include the installation of) fan control technology to avoid potential double counting of energy savings attributions from both technologies. R1587 (Table 6-1) Program exclusions are expected to be re-evaluated since future impact evaluations will include savings attributions from bundled measures. | Yes | Fan Delay
The program administrator (PA) shall employ QA/QC procedures to ensure that the thermostat is installed in an eligible home and is attached to the type of HVAC equipment that is being incentivized, whether it is for natural gas or electricity savings. | Yes | -
The PA shall confirm that the customer has a newly purchased smart thermostat. At minimum, the PA shall obtain a copy of the thermostat sales receipt and the PA shall confirm the purchase date is on or after the program start date | Yes | -
The PA shall determine customer eligibility prior to rebate payment. Upon request, all data associated with determining eligibility shall be provided to Energy Division of the California Public Utilities Commission (CPUC). All PAs shall extend this requirement to all third-party vendors that assist PAs with determining customer eligibility. To the extent that they are used to determine eligibility, data regarding dates of purchase, location of home, customer HVAC equipment type, pre-installation HVAC energy use, etc. shall be made available. | Yes | -
This measure is not eligible for supply fan motors rated < 1 hp and > 3 hp (nominal). This measure is not eligible for other fans, such as the return fan or outdoor air fan of a packaged HVAC unit. | Yes | Supply Fan Replacement
This measure must replace the existing 1 to 3 hp supply fan motor in a packaged HVAC system. | Yes | Existing Fan Power
The new motor and controls must be UL Listed. | Yes | UL Listed Motor
The installation of this measure shall meet all applicable regulations, including but not limited to the current California Building Energy Efficiency Standards (Title 24), federal code, and the National Electrical Code® (NEC). | Yes | Codes and Regulations
This measure is not eligible for supply fan motors rated < 1 hp and > 3 hp (nominal). This measure is not eligible for other fans, such as the return fan or outdoor air fan of a packaged HVAC unit. | Yes | Supply Fan Replacement
The installation of this measure shall meet all applicable regulations, including but not limited to the current California Building Energy Efficiency Standards (Title 24), federal code, and the National Electrical Code® (NEC). | No | Codes and Regulations
In support of the next revision to this workpaper, additional data should to be gathered to determine if motors with horsepower ratings greater than 3 HP can be included as measure offerings. This includes the following: • The application for software-controlled SRMs highlighted by the 2018 ET study is in air conditioning supply fans. Other applications may be studied for suitability. • Based on the initially available set of datasheets, the 5 HP SRM falls below the NEMA Premium® rating of 89.5% for a 4-pole (1800 RPM) induction motor. As additional SRM products become available, efficiency rating tests (following the appropriate standard test procedures identified by the manufacturer) as well as data on full-load VSD losses for the comparable baseline equipment should be collected. | Yes | SoftwareSRM
In support of the next revision to this workpaper, additional data should to be gathered to determine if motors with horsepower ratings greater than 3 HP can be included as measure offerings. This includes the following: • The application for software-controlled SRMs highlighted by the 2018 ET study is in air conditioning supply fans. Other applications may be studied for suitability. • Based on the initially available set of datasheets, the 5 HP SRM falls below the NEMA Premium® rating of 89.5% for a 4-pole (1800 RPM) induction motor. As additional SRM products become available, efficiency rating tests (following the appropriate standard test procedures identified by the manufacturer) as well as data on full-load VSD losses for the comparable baseline equipment should be collected. | Yes | Total hp
This measure is applicable for the nonresidential buildings served by unitary direct expansion (DX) systems listed below. This measure applies to existing building vintages. Assembly Asm Community College ECC University EUn Grocery Gro Hospital Hsp Nursing Home Nrs Hotel Htl Bio/Tech Manufacturing MBT Light Industrial Manufacturing MLI Large Office OfL Small Office OfS Sit-Down Restaurant RSD Fast-Food Restaurant RFF Department Store Rt3 Big Box Retail RtL Small Retail RtS Conditioned Storage SCn Refrigerated Warehouse WRf | Yes
This measure is applicable only in Climate Zones 12, 13, and 15. | Yes
The HVAC packaged units and the evaporative pre-cooler system and controls must meet the following requirements: • Host packaged unit must have a cooling capacity at least 20 tons • For the Add-on Equipment (AOE) measure, the existing packaged unit on which the evaporative pre-cooler system will be installed must be less than 10 years old • A water treatment system must be used in conjunction with the evaporative pre-cooler system to maintain water quality and performance • Real time monitoring of the evaporative pre-cooler system must be implemented to ensure the system is working properly • As a standard procedure, the contractor must perform condenser coil cleaning prior to installation of the pre-cooler system. | Yes
1 Asm Assembly 2 Com Commercial 3 ECC Education - Community College 4 EPr Education - Primary School 5 ERC Education - Relocatable Classroom 6 ESe Education - Secondary School 7 EUn Education - University 8 Gro Grocery 9 Hsp Health/Medical - Hospital 10 Htl Lodging - Hotel 11 MBT Manufacturing Biotech 12 MLI Manufacturing Light Industrial 13 Mtl Lodging - Motel 14 Nrs Health/Medical - Nursing Home 15 OfL Office - Large 16 OfS Office - Small 17 RFF Restaurant - Fast-Food 18 RSD Restaurant - Sit-Down 19 Rt3 Retail - Multistory Large 20 RtL Retail - Single-Story Large 21 RtS Retail - Small 22 SCn Storage - Conditioned 23 WRf Refrigerated Warehouse | Yes | -
For units from 65,000 Btu/h to less than 135,000 Btu/h rated capacity: • ≥12.0 EER • ≥19.0 IEER | Yes | EER
For units from 65,000 Btu/h to less than 135,000 Btu/h rated capacity: • ≥12.0 EER • ≥19.0 IEER | Yes | IEER
For units from 135,000 Btu/h to less than 240,000 Btu/h rated capacity: • ≥12.0 EER • ≥17.5 IEER | Yes | IEER
For both size categories: • Must contain advanced compressor capacity control (either a variable speed compressor, tandem compressors on a single refrigeration circuit, or multiple-step compressors) • Must contain a multi-speed (three steps or greater) indoor fan • Gas-furnace heating section (no requirements on thermal efficiency) • Must be a commercial unitary air conditioner subject to 10 CFR §431.97 | Yes | CompressorControl
For both size categories: • Must contain advanced compressor capacity control (either a variable speed compressor, tandem compressors on a single refrigeration circuit, or multiple-step compressors) • Must contain a multi-speed (three steps or greater) indoor fan • Gas-furnace heating section (no requirements on thermal efficiency) • Must be a commercial unitary air conditioner subject to 10 CFR §431.97 | Yes | MultiSpeed
Central chilled water hydronic systems and domestic hot water systems are not eligible. | Yes | ChilledWater
For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes
In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single family, multi-family or mobile homes), and cooling and heating efficiency. | Yes
The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes
For midstream delivery the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions, and the program administrator shall adjust claimed savings based upon these survey results. | Yes
This measure is not eligible when there is no natural gas to electricity fuel substitution for heating and/or when the measures include a non-regulated fuel. New construction measures are only eligible under certain conditions listed in the above section. Ground up constructions are not eligible. | Yes
Per CPUC Decision 19-08-009 , building infrastructure costs which include panel upgrades or gas line installations/upgrades required to facilitate these fuel substitution measures shall be collected for 10% of each downstream and direct install measures. | Yes
In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | -
In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | ZC
In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | Capacity
In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER
In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF
In addition, preponderance of evidence (POE) must be documented for accelerated replacement measure application types. Notably, programs shall document if the existing equipment (AR) was replaced as a direct result of information, recommendations, and support provided by the program administrator (PA), and programs shall require the collection and submission of documentation to ensure proper conformance with eligibility and implementation requirements. The following are the types of information that will be required for all projects: Customer/site information Specifications of existing equipment Proof that the existing air conditioner and gas furnace are still operating as intended Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life Replacement central heat pump information | Yes
For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes
This measure involves fuel substitution and the implementer must replace an existing central air conditioner and a natural gas furnace. Care must be taken that the existing gas lines are capped off and meet the local code requirements. | No
This measure is not applicable for new construction installations. However new services, as defined in Fuel Substitution Technical Guidance for Energy Efficiency, are eligible. R1087 (Page 3) New service measures are only eligible for downstream and direct install delivery types when: Measures are installed in new areas of an existing building, Measures are installed in a major renovation of an existing building, or Measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. | Yes
Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | Capacity
Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER
Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF
Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER
Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP
Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | No | -
Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | -
Preponderance of evidence (POE) must be documented. Notably, programs shall document if measure was replaced as a direct result of information, recommendations, and support provided by the Program Administrator, and programs shall require the collection and submission of documentation to ensure proper conformance to eligibility and implementation requirements. The following are the types of information that will be required for all projects: − Customer/site information − Specifications of existing equipment − Proof that the existing air conditioner and gas furnace are still operating as intended − Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life − Replacement central heat pump information To document POE, the provided Preponderance of Evidence (POE) survey12 or similar, should be completed. | Yes
Implementer should confirm and provide required documentation to verify that measure implementation meets one of the following conditions: • measures are installed in new areas of an existing building, • measures are installed in a major renovation of an existing building, or • measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. Required documentation can include ONE of the following: • Existing utility bills for the building, • City approved permitting, • City approved Mechanical, or Electrical, or Architecture site drawings, or • Title-24 compliance report | Yes
For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes
For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | InfraCosts
This measure requires the installation of an air-to-water RTU air conditioner unit for a fast food restaurant that is capable of utilizing waste heat to preheat incoming water from the main. See Measure Case Description. | Yes | -
This measure requires the installation of an air-to-water RTU air conditioner unit for a fast food restaurant that is capable of utilizing waste heat to preheat incoming water from the main. See Measure Case Description. | Yes | HeatUse
Only those air conditioning and heat pump systems covered by AHRI 210/240 2008 are eligible. Efficiency values must be certified by Air-conditioning Heating and Refrigeration Institute (AHRI) as verified by the AHRI certification number. | Yes
For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes
For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes | ZC
For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes | ClimateZone
Preponderance of evidence (POE) must be documented. Notably, programs shall document if measure was replaced as a direct result of information, recommendations, and support provided by the Program Administrator, and programs shall require the collection and submission of documentation to ensure proper conformance to eligibility and implementation requirements. The following are the types of information that will be required for all projects: Customer/site information Specifications of existing equipment Proof that the existing air conditioner and gas furnace are still operating as intended Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life Replacement central heat pump information To document POE, the provided Preponderance of evidence (POE) survey, or similar, should be completed | Yes
For split systems the certification will specify an evaporator coil model and may specify additional components. In some cases, a furnace is specified in the certificate. In this case since the furnace is specified as part of the AC system it will not be eligible for a separate incentive. | Yes
For midstream and upstream delivery types, when possible, the program administrator (PA) shall claim the “specific building type savings” in which the equipment will be installed and submit that information at claims level on CEDARS website. In cases where there is no “building type” information available for a given project, program administrator shall claim the weighted savings of “Com” building type. | No | -
The energy and demand impacts of this measure are applicable only to commercial building applications with chiller equipment serving space conditioning. Chiller serving non-space comfort and/or processes and/or industrial applications is not eligible. | Yes | ChillerPurpose
Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | Capacity (Tons)
Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | EER
Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | IPLV
Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Existing ballast manufacturer
Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Existing ballast model number
Due to testing considerations, only a product that can operate from an electronic instant start ballast is eligible. Re-ballast is not eligible. Replacement lamps designed to operate off of existing magnetic ballasts or off of other types of electronic ballasts are not eligible. | Yes
Title-24 Code Requirements for Lighting Alterations | Yes
Even though POE is not explicitly required for approval by the California Public Utilities Commission (CPUC), all program administrators and third-party program implementers are required to collect data, as stated in the Date Collection Requirements section, that will satisfy POU requirements. R843 This technology is dependent upon the existing condition baseline, and the data collection requirements are intended to provide sufficient evidence of the disposal method and replacement of the existing products, including verification of the ballast and the compatibility. | Yes
Good to have | No
Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Total number of fixture on site
Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Number of fixtures sampled
Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Number of lamps per fixture
Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Number of ballasts per fixture
Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Existing fluorescent lamp wattage
Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Disposal method of tubes
De-lamping is not eligible. | Yes
Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes
The lamp must be listed under the Primary Use Category “Replacement Lamps (“plug and play”) (UL Type A)” or “Dual Mode Internal Driver (UL Type A and Type B)” on the current Design Lights Consortium qualified product list (https://www.designlights.org/search/). | Yes
LED tube must be 4-foot and designated as UL Type A or UL Type A+B, but must be configured as a UL Type A. | Yes
TLEDs must be on the current DLC qualified products list and have a listed efficacy of 145 LPW or higher. | Yes
Program Requirements for LED T8 Lamps Table | Yes
The LED T8 Lamp specification sheet must list all of the compatible ballast model numbers to ensure proper operation of the measure. | Yes
The measure must replace a lumen equivalent lamp/fixture of higher wattage. (See Measure Case Description). | Yes | Watts
The measure must replace a lumen equivalent lamp/fixture of higher wattage. (See Measure Case Description). | Yes | Replace Higher Wattage
The measure must be on the DesignLights Consortium (DLC) qualified product list (QPL) (https://www.designlights.org/search/). The product efficacy must meet or exceed the specified “measure case” efficacy based on the “rated” or “measured” efficacy in the DLC database. This requirement is to ensure the efficacy reported by the manufacturer has been confirmed by a third-party entity. | Yes
Only premium fixtures will qualify for the measure case descriptions | Yes
The LED fixture or retrofit kit must be listed in the Technical Requirements table (V5) by the DLC under the General Category “High Bay” and under the Primary Use Designations as follows: R1300 • High-Bay Aisle Luminaires • High-Bay Luminaires for Commercial and Industrial Buildings • Low-Bay Luminaires for Commercial and Industrial Buildings • Retrofit Kits for High-Bay Luminaires for Commercial and Industrial Buildings • Retrofit Kits for Low-Bay Luminaires for Commercial and Industrial Buildings | Yes
DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes
To ensure that code requirements for lighting power and controls are being met, the following data submission requirements must be met for all delivery types and measure application types. •Documentation showing that the retrofitted space has achieved a lighting power density that is < 80% of allowable Title 24 LPD for that space type. •Title 24 compliance documentation verifying the existence of required automated shut-off controls compliant with 2019 Title 24 §130.1(c)1-8 Auto-Shut-off Control. •Only for AR measures, the customer must confirm that existing automated control functionality remains intact after installation. (See Preponderance of Evidence Requirements below.) | Yes | Code Exemptions
All program administrators and third-party program implementers are required to collect data as stated in the Date Collection Requirements section that will satisfy POE requirements. The data collection requirements are intended to provide establish programmatic evidence and include questions about existing system functionality, reasons for retrofitting to LED, and potential future plans without provided incentives. | Yes | POE Docs Submitted
Good to have | No | POE Contact
Existing lamps and ballasts must be fully demolished and properly disposed. “Abandon-in-place” demolition of existing ballasts is not eligible. | Yes | Disposal Method Tube
The LED tube must be 4-foot and designated as UL Type B, UL Type A+B, or UL Type C. UL Type A+B (dual mode) lamps must be installed in a Type B configuration with the existing ballast removed. | Yes | UL Type Config
The LED tube must be compatible with the installed system lighting controls. For example, if the lighting system includes dimming controls, the new LED tube must be dimmable and compatible with the installed dimming system. | Yes | Compatible with existing controls
De-lamping is not eligible. | Yes | Fixtures Delamped
The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Total number of fixtures on site
The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Number of fixtures sampled
The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Percent Sampled
The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Number of lamps per fixture
The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Existing Watts
The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Auto Control Types
Program Requirements for LED T8 Lamps Table | Yes
The LED tube must be 4-foot and designated as UL Type B, UL Type A+B, or UL Type C. UL Type A+B (dual mode) lamps must be installed in a Type B configuration with the existing ballast removed. | Yes
The lamp must be listed under the Primary Use Category “Internal Driver/Line Voltage (UL Type B) Lamps”, “Dual Mode Internal Driver (UL Type A and Type B)”, “2-Lamp External Driver (UL Type C) Lamps”, “3-Lamp External Driver (UL Type C) Lamps”, “4-Lamp External Driver (UL Type C) Lamps” on the current Design Lights Consortium qualified product list (https://www.designlights.org/search/). | Yes
Must meet a minimum efficacy requirement stated in the Measure Case Description. | Yes
- | Pending | Manufacturer
- | Pending | Model
The measure is applicable for all existing agriculture facilities of any vintage. | Pending
A fan must have been tested by the Bioenvironmental and Structural Systems Laboratory (BESS Lab) ventilation fan testing facility at the University of Illinois to the specifications provided in the Base Case Description, and it must meet the minimum allowable cfm/W. (This value is a tradeoff between trying to encourage the highest practical efficiencies and still allowing most manufacturers to have at least one offering within the accepted range.) | Pending
This measure is only applicable to the winery industry for process end-use applications. | Pending
This measure involves the installation of a variable frequency drive (VFD) on an existing glycol pump motor. Chilled fluid, other than glycol, can be considered only if the unit energy savings (UES) is equal to or exceeds the UES of this measure. | Pending
Application of this measure is for the addition of a VFD on an existing glycol pump motor. The existing glycol pump(s) must operate at constant speed. | Pending
The VFD must have automated controls based on pressure feedback, fluid temperature feedback, and/or flow rate feedback. | Pending
The customer must provide documentation that the VFD is not installed on a back-up pump or redundant pump. | Pending
This measure is only applicable to the winery industry for process end-use applications. | Yes
This measure involves the installation of a variable frequency drive (VFD) on an existing glycol pump motor. Chilled fluid, other than glycol, can be considered only if the unit energy savings (UES) is equal to or exceeds the UES of this measure. | Yes
Application of this measure is for the addition of a VFD on an existing glycol pump motor. The existing glycol pump(s) must operate at constant speed. | Yes
The VFD must have automated controls based on pressure feedback, fluid temperature feedback, and/or flow rate feedback. | Yes
The customer must provide documentation that the VFD is not installed on a back-up pump or redundant pump. | Yes
For a normal replacement (NR) installation, the existing backup generator is eligible if it is not currently fitted with a circulating block heater or device utilizing similar electro-mechanical system to heat and circulate generator block pre-warming fluid. | Yes | Electro-Mechanical system
A new generator installation (i.e., new construction, NC), for which the base design prescribes a pre-heating device (e.g., thermosiphon heater) other than a circulating block heater or similar device is eligible to upgrade from base design to efficient design including a circulating block heater. | Yes
Additional eligibility requirements regarding the installation include: • Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician). • Installer should follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. • Installation shall meet all applicable regulations including but not limited to latest NFPA Code 110 for Emergency Power Systems and NEC. | Yes | Qualified Tech
Additional eligibility requirements regarding the installation include: • Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician). • Installer should follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. • Installation shall meet all applicable regulations including but not limited to latest NFPA Code 110 for Emergency Power Systems and NEC. | Yes | Installation Requirements
Additional eligibility requirements regarding the installation include: • Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician). • Installer should follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. • Installation shall meet all applicable regulations including but not limited to latest NFPA Code 110 for Emergency Power Systems and NEC. | Yes
This measure is applicable to the following non-residential building types, of any vintage: Assembly; Manufacturing - Bio/Tech; Education - Community College; Manufacturing - Light Industrial; Education - Primary School; Office - Large; Education - Relocatable Classroom; Office - Small; Education - Secondary School; Restaurant - Fast-Food; Education - University; Restaurant - Sit-Down; Grocery; Retail - Multistory Large; Health/Medical - Hospital; Retail - Single-Story Large; Health/Medical - Nursing Home; Retail - Small; Lodging - Guest Rooms; Storage - Conditioned; Lodging - Hotel; Storage - Unconditioned; Lodging - Motel; Warehouse - Refrigerated | Yes
Additional eligibility requirements regarding the installation include: • Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician). • Installer should follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. • Installation shall meet all applicable regulations including but not limited to latest NFPA Code 110 for Emergency Power Systems and NEC. | No | NFPA Code
This measure is applicable to the following non-residential building types, of any vintage: Assembly; Manufacturing - Bio/ - Community College; Manufacturing - Light Industrial; Education - Primary School; Office - Large; Education - Relocatable Classroom; Office - Small; Education - Secondary School; Restaurant - Fast-Food; Education - University; Restaurant - Sit-Down; Grocery; Retail - Multistory Large; Health/Medical - Hospital; Retail - Single-Story Large; Health/Medical - Nursing Home; Retail - Small; Lodging - Guest Rooms; Storage - Conditioned; Lodging - Hotel; Storage - Unconditioned; Lodging - Motel; Warehouse - Refrigerated | Yes
- | Pending
Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending | Fan Power Rating
Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending
The customer must have an existing electrically operated fixed-speed fan installed on site or plans to install a new electrically operated fixed-speed fan. The existing baghouse, fan, and motor must be in proper operating condition. The baghouse fan motor must be compatible with a variable speed drive (VSD).1 | Pending
There must be no previous VSD or failed VSD installed on the baghouse existing fan motor. This measure cannot be used for the following fan applications: • HVAC fan • An individual fan motor rated less than 10 hp or higher than 150 hp • A two-speed fan motor • A fan motor with an existing VSD | Pending
The installed VSD must be controlled based on static pressure, airflow rate (cfm), or velocity at the lowest required rate to keep particulates suspended in the air stream. The VSD is recommended to meet requirements as specified by IEEE Standard 519-2014.2. | Pending
The fan/blower must not be a designed high-pressure blower. High pressure blowers have designed capacities of less than 150 cfm per rated horsepower. (Applicable only to fan motors larger than 50 hp.) | Pending
This measure cannot be used for the following fan applications: • HVAC fan • An individual fan motor rated less than 10 hp or higher than 150 hp • A two-speed fan motor • A fan motor with an existing VSD | Pending
This measure is applicable to steam boilers only. The steam boiler must have an input rating ≤ 20 million Btu/hr. Hot water boilers are not eligible. | Pending
The boiler manufacturer, model, and spec sheet should be submitted for verification. | Pending
For a dual-stage economizer: • The disposal of combustion condensate must meet local codes regarding sanitary drain or storm sewer. • Some applications may require a neutralizer for the acidic combustion condensate. | Pending
There are no boiler efficiency eligibility requirements for the measure, for both single stage and two stage economizers. The efficiency gains were averaged from past custom projects and meeting these efficiencies (estimated improvement at 2% and 8% for single and dual stage economizer, respectively) is not a requirement for rebate. Good to have | Pending
Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Natural Gas Heated
Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Pool Area SF
Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | R Value
This measure applies to outdoor and indoor heated swimming pools that do not already have pool cover. Energy efficiency programs are to target pools without existing pool covers. | Yes | Existing Pool Cover
Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Pool Cover Requirements
Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Pool Cover Size
Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Olympic Size_Storage Reel System
Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Pool Cover Warranty
The primary target building types for this measure are existing schools/colleges (educational institutions), city (municipal) recreational centers, home owner associations (e.g., condominiums with common pools), private/health clubs, and multifamily residences (apartment buildings). | Yes
New construction installations are not eligible. | Yes
Only main filtration pumps are eligible. | Yes | Installed on Main Pump
Only one-for-one pump replacements are eligible. | Yes | Replacement
Both base case and measure case pool pumps must be between 1 hp and 3 hp, with horsepower referring to the (rated) nameplate horsepower before service factor is applied. | Yes | Size
The variable speed drive (VSD) pump must replace an existing single- or two-speed pool pump and meet base case and measure case requirements, as specified in the Base Case Description and Measure Case Description, respectively. | Yes | VSD Replace
Nominal capacity of the new VSD pump should match the capacity of the pump being replaced (recommended). | Yes | VSD Capacity Match
The VSD pump must be configured to meet program pump configuration requirements. | Yes | VSD Configuration
For models that require an automatic control system capable of controlling both high and low speeds, a controller must be installed. | Yes | Controller Installed
Measure implementation must be completed with both the customer and the installation contractor acknowledgement of energy savings settings. | Yes | Customer_Contractor
The installation contractor shall follow all manufacturer installation requirements and comply with all applicable regulations. The installation shall meet all applicable standards and regulations including (but not limited to) NEC and the California Title 24 and Title 20 regulations (see Code Requirements). | Yes | Contractor Instructions
Pumps being replaced must be disposed of rather than refurbished and sold. | Yes | Disposal
Equipment and materials must meet or exceed all applicable local, state and federal standards. | Yes | Equipment Standards
The installation must be completed by a utility-approved contractor or a contractor with the appropriate license and training. All direct installation with downstream delivery installations must be completed by a utility-approved contractor. Utility-approved contractors will complete both technical and program-related training to ensure proper installation. Each approved contractor will be trained such that they can properly collect and submit the correct (and corresponding) information for both accelerated replacement (AR) and normal replacement (NR) measures. | Yes | Approved Contractor
Self-Installed Measures: Measure B shall be specified on applications for which the client installs their own variable speed pump, or if no certified contractor is used to install the equipment. | No
The variable speed pool pump or motor must be a new | Yes | New Equipment
Program Exclusions: New parts installed in existing units and Motor-only replacements | No
For accelerated replacement application types, the customer must be approached by a direct install implementer. | No
Preponderance of evidence (POE) will be assessed at the program-level based on the direction outlined in the “Accelerated Replacement Using Preponderance of Evidence” of the T1 Working Group Report prepared for the California Public Utilities Commission (CPUC). Additional information and documentation to ensure conformance to eligibility and implementation requirements, include (but are not limited to) the following: Customer/site information Existing equipment Replacement equipment Permits and associated documentation Pump commissioning information | No
Risk mitigation | No
All accelerated replacement measures require third-party baseline verification and data gathering in full compliance with the established POE requirements. | No
Program Exclusions: Pool Pumps installed in a spa or jacuzzi at a single-family residence. | No
Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased
Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump
Program Exclusions: Products won as prizes | Yes | Equipment Prize
Only one variable-speed pool pump and motor rebate per residence. | No
Filtration settings must be configured to operate outside peak hours, as defined by the utility. | No
• Customers must acknowledge and confirm operation on application form in order to be eligible for rebate. | No
Only one rebate is allowed per spa OR wading pool pump. | No
A maximum of three rebates are allowed per customer property/site for main filtration pump(s). Incentive applications for more than one main filtration pump require supporting documentation verifying existing condition per Authority Having Jurisdiction. | No
During pool operating hours, the VSD setting must be “right sized” to meet turn-over requirements as specified by the 2019 Title 24 standards, Chapter 31B “Public Swimming Pools,” Section 3124B. (See Code Requirements). | Yes | VSD Setting
During Pool Operating Hours: Variable speed drive setting must be “right sized” to meet turnover requirements as specified by California Code of Regulations, Title 24, Building Standards Code (2016): Chapter 31B “Public Swimming Pools,” Section 3124B. | Yes | VSD Setting
During pool non-operating hours, the VSD setting must be configured to at least 50% of full-speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting
During Pool Non-Operating Hours: Variable speed drive setting must be configured to at least 50% of full speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting
Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit
Health code requirements and inspections must be passed successfully. | Yes | Health Inspection
EH&S Department approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved
EH&S approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved
The customer, as part of the incentive application process shall acknowledge that the replacement pool pump VSD has been configured to achieve energy savings and agreed to have the pump filtration settings programmed for reduced flow during pool non-operating hours. | No
The customer shall agree not to modify and/or alter in any way programmed settings on the pump VSD to ensure persistence of the measure savings. | No
This measure is available for swimming pool heating and the unit must replace pre-existing pool heater. | Yes | Existing Heater
The commercial pool heater must be certified to meet the following requirements: • The heater must have TE ≥ 84% • The heater must have an ON/OFF switch and no pilot light | Yes | EFFICIENCY
The commercial pool heater must be certified to meet the following requirements: • The heater must have TE ≥ 84% • The heater must have an ON/OFF switch and no pilot light | Yes | ON_OFF Switch
This measure is applicable to all heated pools installed in commercial facilities, such as schools, colleges, universities, YMCA/YWCA, public facilities, hotels/motels, health clubs, and spas. This measure is also applicable for multifamily properties, such as homeowner associations and other multifamily complexes. | Yes
This measure is applicable for any existing single family, multifamily with two or more units, or mobile home that uses air-cooled, direct expansion (DX) cooling and gas heating, heat pump, or gas heating with no cooling. | Yes
Up to two duct tests must be conducted: the first or “test-in” is a system check to determine whether the duct system tightness meets the California Title 24 specifications. | Yes
If the Test-in shows that duct leakage exceeds minimum tightness specifications, and the technicians correct the situation, then a second test or “test-out” must be conducted to verify proper duct tightness was achieved. | Yes
If some or all of the existing ductwork is beyond repair and sections must be replaced, the sections that must be replaced must be less than 40 linear feet in total per Section 150.2(b) of the 2019 California Building Energy Efficiency Standards (Title 24) | Yes
...or the replaced ductwork must be installed and tested in accordance with the applicable requirements in 2019 Title 24 Section 150.2(b)1D | Yes
To identify these measures as part of an existing HVAC system, the program implementer must record existing duct leakage through comprehensive field testing. The testing can be performed while the system is pressurized using a duct blower fan to ensure the target leakage thresholds are achieved. Duct sealing shall be performed on the unpressurized system. After installation, testing shall be performed to ensure the target leakage thresholds are achieved. Photos and test results can serve as documentation that the work was performed on an existing HVAC system. | Yes
Programs often bundle Quality Maintenance (QM) measures. The following prerequisites must be met before the QM treatments, such as airflow adjustments, can be implemented to ensure an HVAC system is running optimally. | Yes
• The unit must be drawing power. | Yes
• The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted. | Yes
• The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees. | Yes
• An assessment and report are required in accordance with Air Conditioning Contractors of America (ACCA) Standard 48 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations. | Yes
This measure is applicable for any existing single family, multifamily with two or more units, or mobile home that uses air-cooled, direct expansion (DX) cooling and gas heating, heat pump, or gas heating with no cooling. To confirm that the correct vintage savings are being used, the building age should be verified. See below for details on DEER 2020 vintage years for Old and Median (Existing) vintage buildings : | Yes
In order to verify compliance with measure requirements and the correct measure selection, the following information must be collected for each installation: • Building information such as: building type, vintage (year), and climate zone • HVAC System type, capacity in tons (for systems with cooling) or kBtuh (for systems with no heating), make and model number • Duct testing information include: o Type of duct test conducted o Pre and post install duct leakage rate percentages o Duct sealing material used | Yes
Per Resolution E-5082 “duct connections must not be sealed with duct tape (cloth-backed rubber adhesive tapes). Mastic or aerosol sealant materials are preferred, and butyl tape can be used where mastic or aerosol are impractical.” | Yes
Programs often bundle Quality Maintenance (QM) measures. The following prerequisites must be met before the QM treatments, such as airflow adjustments, can be implemented to ensure an HVAC system is running optimally. | Yes | QM Eligibility
• An assessment and report are required in accordance with Air Conditioning Contractors of America (ACCA) Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations. | Yes
This measure is applicable for any existing single family, multifamily with two or more units, or mobile home that uses air-cooled, direct expansion (DX) cooling and gas heating, heat pump, or gas heating with no cooling. | Yes
To confirm that the correct vintage savings are being used, the building age should be verified. See below for details on DEER 2020 vintage years for Old and Median (Existing) vintage buildings: • Old: Before 2002 for non-mobile homes, before 1995 for mobile homes • Median (Existing): 2002 to 2016 for non-mobile homes, 1995 to 2005 for mobile homes | Yes
Up to two duct tests must be conducted: the first or “test-in” is a system check to determine whether the duct system tightness meets the California Title 24 specifications. | Yes | Test-In
If the Test-in shows that duct leakage exceeds minimum tightness specifications, and the technicians correct the situation, then a second test or “test-out” must be conducted to verify proper duct tightness was achieved. | Yes | Test-Out
If some or all of the existing ductwork is beyond repair and sections must be replaced, the sections that must be replaced must be less than 40 linear feet in total per Section 150.2(b) of the 2019 California Building Energy Efficiency Standards (Title 24) | Yes | Ductwork Length
...or the replaced ductwork must be installed and tested in accordance with the applicable requirements in 2019 Title 24 Section 150.2(b)1D | No | Ductwork Code Requirement
To identify these measures as part of an existing HVAC system, the program implementer must record existing duct leakage through comprehensive field testing. The testing can be performed while the system is pressurized using a duct blower fan to ensure the target leakage thresholds are achieved. Duct sealing shall be performed on the unpressurized system. After installation, testing shall be performed to ensure the target leakage thresholds are achieved. Photos and test results can serve as documentation that the work was performed on an existing HVAC system. | Yes | Duct Leakage
• The unit must be drawing power. | Yes | Power Check
- | Yes | Make
Legacy property, set to expire 12/31/21 | Yes | Actual QTY
Legacy property, set to expire 12/31/21 | Yes | Base Case Measure Code
Legacy property, set to expire 12/31/21 | Yes | Base Case Measure Description
Legacy property, set to expire 12/31/21 | Yes | Cap-Tons
Legacy property, set to expire 12/31/21 | Yes | End Use
Legacy property, set to expire 12/31/21 | Yes | Location
Legacy property, set to expire 12/31/21 | Yes | Refrigerant applied
Legacy property, set to expire 12/31/21 | Yes | Serial Number
Legacy property, set to expire 12/31/21 | Yes | Size
The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Air Flow Rate
The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Operational
The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | COAT
The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Assessment_Report
The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | QM Service Agreement
This measure is applicable for residential single family, multifamily, and double-wide mobile homes that use central air-cooled direct expansion (DX) cooling and gas heating. | Yes | DX Cooling_Gas Heat
The contractor must provide the amount and percent refrigerant charge added to or removed from the system to verify the applicable measure. | Yes
Legacy property | Yes | End Use
Legacy property | Yes | Location
Legacy property | Yes | Serial Number
Legacy property | Yes | Sticker Number
The Return Duct Retrofit measure shall be installed by a residential HVAC contractor in a mobile home where there is an existing open belly return with a supply system in the ceiling. The Crossover Duct Replacement measure shall be installed by a residential HVAC contractor in an extended mobile home where two or more sections of the home has been joined. The crossover duct connects the supply ducting of two or more sections. | Yes
The Return Duct Retrofit measure shall be installed by a residential HVAC contractor in a mobile home where there is an existing open belly return with a supply system in the ceiling. | Yes
The ducting must be deteriorated, damaged, or not installed correctly to be eligible for this measure. | Yes
Installed return ducts shall be made from either galvanized steel, tinplated steel, or aluminum, or shall be listed as Class 0 or Class 1 air ducts under Underwriters' Laboratories, Inc. Standard for Air Ducts, UL181-1972. | Yes
Return ducts in unconditioned spaces shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. | Yes | Return Duct
The crossover duct shall be supported and or prevented from ground contact. If located in interior areas, not exposed to outdoor air, crossover ducts shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. If the crossover duct is installed in an area that is exposed to outdoor air, such as outside the building’s envelope, the ducts shall be insulated with material having effective thermal resistance (R) of not less than 8.0. | Yes | Duct Location
Return ducts in unconditioned spaces shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. | Yes
The crossover duct shall be supported and or prevented from ground contact. If located in interior areas, not exposed to outdoor air, crossover ducts shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. If the crossover duct is installed in an area that is exposed to outdoor air, such as outside the building’s envelope, the ducts shall be insulated with material having effective thermal resistance (R) of not less than 8.0. | Yes
Belly return systems shall be verified by a pre and post total leakage duct test at 25 pascals on the return side of the duct system only. This shall be achieved by separating the supply from return side of the duct system by sealing at the air handler/furnace, typically at the filter slot to eliminate supply side leakage from the test. | Yes
The existing faucet must have a flow rate of at least 2.2 gpm. | Yes | Existing Flow Rate
Revisit | Yes | Flow Rate
Revisit | Yes | Natural Gas WH
For accelerated replacement application types, the retrofit faucet must have an existing faucet aerator. For all other application types, the faucet must not have an aerator installed. | Yes | Existing Aerator
The measure is not applicable to new faucets that meet or exceed the 2016 California Appliance Efficiency Regulations (Title 20) code requirement of 1.2 gpm flow rate for lavatory faucet and 1.8 gpm flow rate for kitchen faucet. | No | Title 20
Good to have | Yes | Existing Flow Rate
Good to have | Yes | Flow Rate
Measure Description | Yes | Natural Gas WH
To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers • Customer/site information • Make/model of pre-existing equipment and/or • Performance/flowrate measurements of pre-existing equipment, and/or • Photograph of pre-existing equipment in place and operating | Yes | Preponderance of Evidence
Thermostatic shower valve (TSV): Any TSV certified by applicable standards (e.g., ANSI, ASPE, etc.) is eligible. | Yes | Certified
The make and model number and a copy of the customer receipt must be submitted with the application. | Yes | Receipt
This measure is not applicable where recirculation pumps are used or where potential crossover between hot water and cold water may occur. | Yes | Recirculation Pump
The measure is not applicable where tankless water heaters are used; instantaneous tankless water heaters may have different effect on savings with temperature-initiated flow-restriction valves. | Yes | Tankless
The measure is not applicable where the showerhead is installed in tub/shower combination systems. (However, note that the gross savings installation adjustment (GSIA) factor accounts for expected leakage. See Gross Savings Installation Adjustment.) | Yes
- | No | LFR Served By Gas
- | No | Existing Flow Rate
- | No | Flow Rate
Eligibility requirements for the laminar flow restrictor measure include: • The device must be installed only in health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation/inspection requirements. • The device must meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation. • The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | No | LFR Labeled Vandal
Eligibility requirements for the laminar flow restrictor measure include: • The device must be installed only in health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation/inspection requirements. • The device must meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation. • The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | No | Meets Code
Eligibility requirements for the laminar flow restrictor measure include: • The device must be installed only in health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation/inspection requirements. • The device must meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation. • The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | No
Eligible building types for this measure are health care facilities and/or medical buildings of any vintage that adhere to the Office of Statewide Health Planning and Development (OSHPD) regulations in the State of California that also utilize natural gas-powered water heating equipment. These facilities include (but are not limited to): • Hospitals (large regional or local) • Emergency rooms • In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals • Doctor offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.) • Clinics and nursing homes | No
New construction health care facilities are not eligible. | No
Savings limited to gas fired water heaters only | Yes | LFR Served By Gas
Measure Description | Yes | Flow Rate
Eligibility requirements for the laminar flow restrictor measure include: • The device must be installed only in health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation/inspection requirements. • The device must meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation. • The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | Yes | LFR Labeled Vandal
Eligibility requirements for the laminar flow restrictor measure include: • The device must be installed only in health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation/inspection requirements. • The device must meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation. • The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | Yes | Meets Code
Eligible building types for this measure are health care facilities and/or medical buildings of any vintage that adhere to the Office of Statewide Health Planning and Development (OSHPD) regulations in the State of California that also utilize natural gas-powered water heating equipment. These facilities include (but are not limited to): • Hospitals (large regional or local) • Emergency rooms • In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals • Doctor offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.) • Clinics and nursing homes | Yes
New construction health care facilities are not eligible. | Yes
For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers, Customer/site information, Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating | Yes
Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description and must comply with emission limits per air district, if applicable. Note that Tier 2 & 3 hot water heaters are condensing and often require flue modifications to handle the condensate. • Only gas-for-gas replacement installations are eligible. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use. • Have an input rating of at least 4,000 Btu/hr/gal of stored water. | Yes | Emission Limits Boiler
Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description and must comply with emission limits per air district, if applicable. Note that Tier 2 & 3 hot water heaters are condensing and often require flue modifications to handle the condensate. • Only gas-for-gas replacement installations are eligible. Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use. • Have an input rating of at least 4,000 Btu/hr/gal of stored water. | Yes | Replacing Gas_Gas
This measure does not include water heaters or hot water boilers used for space conditioning, industrial (process) end-use applications, pools, or spas. | Yes | Boiler Use
Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description and must comply with emission limits per air district, if applicable. Note that Tier 2 & 3 hot water heaters are condensing and often require flue modifications to handle the condensate. • Only gas-for-gas replacement installations are eligible. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use. • Have an input rating of at least 4,000 Btu/hr/gal of stored water. | Yes
This measure cannot be used to supply hot water to a circulation loop without an intermediary hot water storage tank. | Yes | Circulation Loop
Good to have | Yes | Energy Factor
Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description and must comply with emission limits per air district, if applicable. Note that Tier 2 & 3 hot water heaters are condensing and often require flue modifications to handle the condensate. • Only gas-for-gas replacement installations are eligible. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use. • Have an input rating of at least 4,000 Btu/hr/gal of stored water. | Yes | Input Rating
To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. | Yes
For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. | Yes
Measure Description | Yes | Energy Factor
Measure Description | Yes | EFFICIENCY
For normal replacement (NR) measure application type, only gas-for-gas replacements are eligible | Yes | Replacing Gas_Gas
Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use • Have an input rating of at least 4,000 Btu/hr per gallon of stored water | Yes | Input Rating
Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use • Have an input rating of at least 4,000 Btu/hr per gallon of stored water | Yes
Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use • Have an input rating of at least 4,000 Btu/hr per gallon of stored water This measure does not include water heaters or hot water boilers used for space conditioning, industrial (process) end-use applications, pools, or spas. | Yes | Primary Use Domestic Water
This measure cannot be used to supply hot water to a circulation loop without an intermediary hot water storage tank. | Yes
- | Yes | Market Cost
Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes | Replacing Gas_Gas
Water heaters or hot water boilers used for space conditioning, industrial (process) end-use applications, pools, or spas are not eligible. | Yes
Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes
Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes | Input Rating
Water boilers must have an input rating ≤ 200,000 kBtu/hr. The combustion efficiency must have a documented combustion efficiency of 85% or greater under full load conditions. Steam boilers must have an input rating ≤ 200,000 kBtu/hr. The combustion efficiency must have a documented combustion efficiency of 83% or greater under full load conditions. | Yes | EFFICIENCY
This measure is not applicable to boilers used for space heating, domestic hot water, pools, or spas, and is not eligible for domestic hot water or space heating. | Yes | Boiler Use
This measure is not eligible for new construction installations. | Yes
Eligible building types include all existing commercial, agriculture, and industrial (nonresidential) buildings of any vintage. This measure is available to industrial end-use customers that manufacture a saleable product, typically (but not limited to) NAICS codes 31, 32, and 33. | Yes
Only gas-for-gas normal replacements or for new construction installations are eligible. Normal replacements must replace a storage water heater with another storage water heater. | Yes | Existing Equipment Type
Only storage water heaters as defined by the California Energy Commission qualify, and they must: Be used primarily for domestic hot water. Water heaters used for space conditioning, process end use applications, pools or spas are not eligible. | Yes | Primary Use Domestic Water
Eligible water heaters must comply with the measure case specification (see Measure Case Description). “Storage water heater” means a water heater that heats and stores water within the appliance at a thermostatically-controlled temperature for delivery on demand, and that has an input less than 4,000 Btu/hr/gal of stored water. | Yes | Input Rating
Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity
Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF
For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: targeted segment of the market or customers, Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating | Yes | POE Docs
If necessary, customer must provide proof of unit efficiency (e.g., manufacturer’s equipment specification sheet). | Yes | -
Equipment must comply with the test methods referenced in the California Building Energy Efficiency Standards (Title 24) and the California Appliance Efficiency Regulations (Title 20). | No | -
Additionally, the equipment must meet minimum emissions requirements as defined by local air quality management districts. See Code Requirements. | No | -
For new construction (NC), the baseline can be a gas-fired water heater. But, energy savings and measure cost are estimated and reported as the difference between the corresponding heat pump water heater and the baseline electric resistance water heater. (See also Base Case Description.) | Yes
Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes
A new heat pump water heater with storage capacity less than 45 gallons does not qualify. | Yes
Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type
The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity
To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF
To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | FHR
This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type
This measure qualifies only for central hot-water systems used primarily for domestic hot-water heating. | Pending
Central hot water systems with demand-controlled recirculation pump are not eligible. | Pending
Facilities that must maintain hot water temperature of 140°F to control Legionella bacteria are not eligible. Local, state, and federal regulations must be followed to avoid the risk of Legionella growth and scalding. | Pending
Data to be collected will include manufacturer and model numbers of controllers installed. Controller invoice amount and installation cost will be required to be collected to calibrate cost data. | Pending | Data Collection
Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type
Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type
The manufacturer specification sheet must be submitted with the application. | Yes | Manufacturer Cut Sheet Submitted
A minimum of one inch of pipe insulation must be added to existing bare commercial or industrial steel or copper pipe. | Yes | Pipe Insulation Added
The hours of operation must be indicated on the top of the application. | Yes | Hours of operation
The minimum qualifying pipe diameter is ½-inch. | Yes | Size
If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG
The length of insulation to be installed with each pipe size must be indicated. | No | Length
Insulation required by California Building Energy Efficiency Standards (Title 24) or employee safety laws (Occupational Safety and Health Administration, OSHA) is not eligible. | Yes | Title 24
Replacement of damaged (existing) insulation is not eligible. | Yes | Existing Insulation
The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Manufacturer
The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Model
The tank must be coupled to gas-fired commercial, industrial, agriculture, or multifamily central equipment that transfers heat to the contained liquid or solution. | Yes | Coupled Tank
The following conditions and applications are not eligible: • Tanks with pre-existing insulation • Replacement of old or damaged insulation • Tanks insulated to prevent burns. • Insulation for exposed hot-water tanks within seven feet of the floor that are not otherwise guarded in such manner as to prevent contact. The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Existing Insulation
The following conditions and applications are not eligible: • Tanks with pre-existing insulation • Replacement of old or damaged insulation • Tanks insulated to prevent burns. • Insulation for exposed hot-water tanks within seven feet of the floor that are not otherwise guarded in such manner as to prevent contact. | Yes | Insulation Required to Prevent Burns
The following conditions and applications are not eligible: • Tanks with pre-existing insulation • Replacement of old or damaged insulation • Tanks insulated to prevent burns. • Insulation for exposed hot-water tanks within seven feet of the floor that are not otherwise guarded in such manner as to prevent contact. The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Exposed Hot Water Tanks
The insulation thickness and process temperature (tank solution temperature) will determine the energy savings. The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Tank Temp
The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Insulation material type
The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Insulation Material k-value rating
The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Type of tank material
- | Yes | Usage
- | Yes | Tank Location
This energy efficiency measure is applicable to an existing faucet in a commercial building that has a flow rate of 1.67 gpm or greater. | Yes
Only facilities that utilize natural gas water heating equipment are eligible to receive incentives for this measure. | Yes
Faucets at health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation (e.g. hospitals, clinics, skilled nursing facilities) are not applicable for this measure. The use of aerators is banned in the health care industry due to aerator flow control methods and components. The mixing of air and water within the aerator allows airborne bacteria to become waterborne and, in warm stagnant conditions, promote bacterial growth. Non-aerating laminar flow restrictors (LFRs) must be installed on faucets in these facilities | Yes
Make and model number must be included with a copy of the invoice. | Yes | Manufacturer
Make and model number must be included with a copy of the invoice. | Yes | Model
The measure for the installation of low flow showerheads is applicable for the accelerated replacement of the existing showerhead of 2.5 gpm flow rate or greater with a low-flow showerhead of 1.8 gpm or lower flow rate. The installed low-flow showerhead shall meet the requirements of test procedure ANSI/ASME A112.18.1-2000, Section 5.5 The measure for the installation of flow control valves is applicable for the add-on equipment onto an existing showerhead with the flow rate of 2.5 gpm or greater, reducing the flow rate to 1.5 gpm or lower. | Yes | Existing Flow Rate
This measure is excluded from newly constructed buildings, additions to existing buildings, and alterations to existing buildings. | Yes | Unit Installed Building Type
The facility must have natural gas as the water heating source fuel. | Yes | Natural Gas WH
For accelerated replacement measure application type (MAT), this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers Customer/site information Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating Specific documentation requirements will be determined by the program administrator and will be specified in the program implementation plan. Program influence evidence can be demonstrated through one of the three alternatives listed in Section 7.3 of POEV 2.0. This measure establishes the program-level evidence of program influence by adopting the net-to-gross (NTG) ratio from prior program evaluation results. | Yes
Eligibility requirements for this measure include the following: • The building must have a hot water recirculation system that can be turned OFF entirely for a set period of the day and/or week. • The building must have a centralized, gas-fired, hot-water system with a constant-flow, fractional-horsepower, uncontrolled recirculation pump. • The timer device must have seven-day (or better) scheduling capabilities. • There is no restriction on manufacturer or brand-naming. | Yes
This measure is applicable to existing buildings and is limited to the commercial building types specified below. • Healthcare – outpatient • Service – fitness • Office – large • Office – small • Education – primary • Education - secondary | Yes
This measure is excluded from newly constructed buildings, additions to existing buildings, and alterations to existing buildings. | Yes
Revisit | Yes | Receipt
Revisit | Yes | IAPMO
Revisit | Yes | Tankless
Revisit | Yes | Wall Mounted Diverter
For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Electrification Infrastructure
For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Electrification Measures
For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Electrification Measures Costs
For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Heater Fuel
Existing base equipment must be disposed. | Yes | Disposal Method
NC is only eligible for downstream delivery under the following conditions. These are defined as new services in fuel substitution technical guidance: Measures are installed in new areas of an existing building, Measures are installed in a major renovation of an existing building, or Measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. | Yes | New Area
In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, and proposed building type where the product will be installed. | Yes | Input Rating
Preponderance of evidence (POE) must be documented for all accelerated replacement application types. Notably, programs shall document if measure was replaced as a direct result of information, recommendations, and support provided by the program administrator, and programs shall require the collection and submission of documentation to ensure proper conformance to eligibility and implementation requirements. The following are the types of information that will be required for all projects: Customer/site information Specifications of existing equipment Proof that water heater is still operating as intended Existing water heater nameplate data with manufacturer date to confirm remaining useful life Replacement water heater information To document POE, the implementer must complete the provided the survey, or similar. R1539 | Yes | POE Docs
Program eligibility requirements for the addition of insulation to hot water and cold water pipes, within the first three feet of a storage water heater include: | Yes | Insulation Addition
A minimum of 1-inch of pipe insulation must be added to existing bare pipe | Yes | Minimum Thickness
Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam | Yes | Type
Must be installed by an authorized implementer | Yes | Approved Contractor
Must verify no existing pipe insulation as the existing condition | Yes | Existing Insulation
This measure is not applicable for commercial or industrial applications. This measure is not eligible for new construction applications as defined by the California Plumbing Code. | Yes | New Construction
To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity
The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF
To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | FHR
Replacement of an "instantaneous" or "tankless" water heater does not qualify. | Yes | Disposal Method
To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | No | -
To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | ZC
To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | ClimateZone
Deployment of the program may require rebates or financial incentives to participants that exceed the incremental measure cost (IMC). Incentives or rebates that exceed the IMC for a measure must be justified by individual program administrators (PAs) in addendum to measure submissions to document program implementation practice prior to program implementation. | Yes | -
The VFD must be installed on the pump motor with a minimum operation of 1,000 hours per year. | Yes
To substantiate conformance with program requirements, the customer must supply an invoice or other supporting documentation that includes the following: • Quantity of VFDs • Type (well and/or booster) • Horsepower rating of motor(s) and VFD(s) • Area map showing physical location of pumps • Manufacturer make/models of each VFD installed | Yes
To substantiate conformance with program requirements, the customer must supply an invoice or other supporting documentation that includes the following: • Quantity of VFDs • Type (well and/or booster) • Horsepower rating of motor(s) and VFD(s) • Area map showing physical location of pumps • Manufacturer make/models of each VFD installed The customer must have an existing electrically operated agricultural booster or well pump installed on site or plans to install a new agricultural booster or well pump. | Yes
The variable frequency drive (VFD) must be used to adjust operation of a pump to meet flow/pressure requirements and not be used simply as a soft starter or for cavitation control. | Yes
The pumping application must currently have the means to vary the pressure/flow (i.e. throttle valve, control valve, etc.). | Yes
The VFD must be installed on a pressurized irrigation system (no flood irrigation). | Yes
This measure cannot be used for the following pumping applications: • A well pump used to fill a reservoir, • A well pump discharging directly into a canal, and/or • A mixed flow pump (high volume, low head). | Yes

## Property Field Names
Row Labels | Distinct Count of Workpaper ID
Model | 95
Manufacturer | 93
Building Type | 23
Serial Number | 21
CA Climate Zone | 20
Zip Code | 20
Equipment ID | 18
Site ID | 18
Retail Price | 13
Is the equipment new (not used or rebuilt)? | 12
AHRI Reference Number | 11
New Equipment | 10
Measure Size Category | 9
Flow Rate of Installed Unit (gpm) | 6
Who was the party that filled out the POE documentation? | 6
Does the facility utilize natural gas water heating equipment? | 5
Min. Cooking Energy Efficiency (%) | 5
Uniform Energy Factor (UEF) | 5
End Use | 4
ENERGY STAR Qualified? | 4
Existing Flow Rate (gpm) | 4
Heating Seasonal Performance Factor (HSPF) | 4
Location | 4
After implementation air flow rate? (cfm/ton) | 3
Base Case Measure Code | 3
Base Case Measure Description | 3
Before implementation condenser over ambient temperature (COAT) ? (degrees) | 3
Building infrastructure costs (i.e. panel upgrades or gas installation/upgrades) | 3
Building Vintage | 3
Cap-Tons | 3
Condenser Serial Number | 3
Cooling Capacity (kBtu/hr) | 3
Cooling Capacity (kBtuh) | 3
Customer existing baseline fuel type | 3
Does premise have central air-cooled direct expansion (DX) cooling and gas heating? | 3
Existing water heater type | 3
Has Customer agreed to the QM Service Agreement? | 3
Is the unit operational? | 3
Itemized invoices submitted with upgrade costs for additional electrification measures? | 3
Kelvin Correlated Color Temperature (CCT) | 3
List other electrification measures installed | 3
Make | 3
Photograph(s) of existing cooling and heating equipment submitted? | 3
Refrigerant successfully applied and meets manufacturer recommended levels | 3
Refrigerant Type | 3
Replacing gas unit with gas unit? | 3
SEER | 3
Thermal Efficiency (%) | 3
Was a copy of the purchase receipt submitted? | 3
Before implementation of the measure was an assessment and report created in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations? | 2
Capacity (tons) | 2
Cap-kBtuh | 2
Coefficient of Performance (COP) | 2
Combustion Efficiency (%) | 2
Condenser Manufacturer | 2
Condenser Model | 2
Contractor provided load calculations showing new unit is sized correctly for the load? | 2
Cooling Capacity (tons) | 2
CRI | 2
Dishwasher type | 2
Disposal method of tube | 2
Does the facility utilize tankless water heaters? | 2
EER | 2
ENERGY STAR Qualified | 2
Energy Star unique ID | 2
Evaporator Manufacturer | 2
Evaporator Model | 2
Existing Equipment Type | 2
Existing Equipment within +/- 5% of the replacement equipment Cooling Capacity (kBtuh)? | 2
First Hour Rating (FHR) | 2
Greenhouse facility specialty | 2
Greenhouse is heated by natural gas (not propane)? | 2
Has all Preponderance of Evidence (POE) been submitted as defined by the workpaper? | 2
Has all Preponderance of Evidence (POE) including existing system controls functionality with replacements, reasons for retrofitting to LED, and future plans without incentives been documented and submitted? | 2
Has all the preponderance of evidence required by the measure package been uploaded in EECP? | 2
Has all the preponderance of evidence required by the workpaper been uploaded in EECP? | 2
Have POE requirements in the measure package been included in uploaded documentation? | 2
Have the fixtures been delamped? | 2
Idle Energy Rate (Btu/Hr) | 2
Idle Energy Rate (kW) | 2
IEER | 2
Input Rating (btu/hr/gallon of stored water) | 2
Input rating (kBtu/hr) | 2
Integrated Part Load Value (IPLV) | 2
Is Equipment Gas or Electric? | 2
Is the lamp listed on the most recent version of the DesignLights Consortium (DLC) list? | 2
L70 Lumen Maintenance Hours | 2
Labor cost for replacement motor | 2
Market Cost | 2
Material cost for replacement motor | 2
Max Idle Energy Rate (Btu/hr) | 2
Max Idle Energy Rate (kW) | 2
Max washing energy (kWh/rack) | 2
Minimum Warranty | 2
New Construction | 2
Oven Size | 2
Power Factor | 2
Pre-Existing Conditions: Fluorescent Lamp Wattage (W) | 2
Pre-Existing Conditions: Number of Fixtures Sampled | 2
Pre-Existing Conditions: Number of Lamps per Fixture | 2
Pre-Existing Conditions: Total number of fixtures on site | 2
Primary Use Category | 2
Replacement like-for-like (i.e. air conditioner for an air conditioner or heat pump for heat pump)? | 2
Replacement motor size (W) | 2
Retailor or distributor zip code | 2
Size (kBtu/hr) | 2
Storage Capacity (gallons) | 2
System Type | 2
The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | 2
Total Harmonic Distortion | 2
Uniform Energy Factor | 2
Was the customer approached directly by a direct installation implementer? | 2
Was the installation of the measure completed by a utility-approved contractor? | 2
- | 1
Is the boiler used for space heating, domestic hot water, pools, or spas? | 1
Min Cooking Efficiency (%) | 1
4-ft LED Tube Type | 1
A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | 1
A map of the pump service area has been submitted? | 1
Additional QM measures (i.e. airflow adjustments) being installed in conjunction with this measure? | 1
AFUE % | 1
AFUE (%) | 1
AHRI certification number | 1
All measures related to constant speed screw, constant speed centrifugal, and frictionless chillers are excluded due to the stringency of the tiers specified for the 2020 update of the Database of Energy Efficient Resources (DEER) and equipment availability in the market. | 1
Amount of refrigerant added or removed | 1
Annual Energy Use (kWh/yr) | 1
Annual Fuel Utilization Efficiency, AFUE (%) | 1
Any maintenance or repairs to economizer? If so, what was done? | 1
Are other Quality Maintenance (QM) measures (i.e. airflow adjustments) being installed with this measure? | 1
Are the display cases any of the following: specialty deli cases, custom coolers/freezers, and walk-in boxes with reach-in doors? | 1
Are the display cases served by a remote refrigeration system? | 1
Are the dryers on the site premise? | 1
Are the glass doors being installed on an existing vertical display case? | 1
Are the new motor and controls UL Listed? | 1
Are the refrigeration display case doors new? | 1
Are there any other throttling devices, such as inlet vanes or bypass dampers, and throttling valves still operating? | 1
At least 1-in of insulation added to existing bare commercial or industrial steel or copper pipe? | 1
Automatic Conveyor Broilers Belt Width (in) | 1
Back-up generator size (kW) | 1
base case and measure case pool pumps? (hp) | 1
Before implementation of the measure was an assessment and report created in accordance with ACCA Standard 43 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations? | 1
Before installation of the measure was the existing backup generator fitted with a circulating block heater or device utilizing similar electro-mechanical system to heat and circulate generator block pre-warming fluid? | 1
Belt Type Installed | 1
Boiler used for space comfort (not domestic or process hot water)? | 1
Building has hot water recirculation system that can be turned OFF for a set period time? | 1
Building is a fast food restaurant (RFF)? | 1
Building type is existing Agricultural facility (any vintage)? | 1
Building Type is Residential Multifamily? | 1
Building type one of the following: Asm, EPr, ERC, Gro, MLI, RFF, RSD, RtL, RtS, SCn, WRf? | 1
Building Vintage (construction year) | 1
Capacity (BTU/hr) | 1
Capacity of largest dryer (lbs) | 1
Capacity of largest washing machine (lbs) | 1
Chiller used for space conditioning, not for processes or industrial applications? | 1
Climate Zone | 1
Code Exemption for: Retrofitting < 10% in an enclosed space or <= 50 total per floor or tenant? | 1
Combined Energy Efficiency Ratio (CEER) | 1
Compressor(s) control type | 1
Contractor license number | 1
Conveyer Width (in) | 1
Cooking Energy Rate (kW) | 1
Cooling Capacity (BTU/h) | 1
Crossover duct insulation thermal resistance (R) | 1
Crossover duct location | 1
Customer has (or plans to have) existing, operational, and VSD compatible fixed speed fan? | 1
Customer has an active natural gas account? | 1
Data to be collected will include manufacturer and model numbers of controllers installed. Controller invoice amount and installation cost will be required to be collected to calibrate cost data. | 1
Date of Construction | 1
Date of installation or major upgrade to refrigeration multiplex system | 1
Design cooling load for connected display cases, walk-in coolers and freezers, cooled storage, and prep areas only (sub-coolers and air conditioning loads ineligible) (tons) | 1
Did both the customer and the installation contractor acknowledge the energy savings setting of the installed measure? | 1
Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | 1
Did equipment and materials meet or exceed all applicable local, state and federal standards? | 1
Did existing fans (not HVAC related) previously have VSD controls? | 1
Did the existing unit have the supply fan in automatic mode or switched OFF during unoccupied periods? | 1
Did the installation contractor follow all manufacturer installation requirements and comply with all applicable standards and regulations including (but not limited to) NEC and the California Title 24 and Title 20 regulations (see Code Requirements).? | 1
Did the installed heater replace an existing pool heater? | 1
Did the installed unit replace a conventional or always-on hand-wrap machine? | 1
Did the installed variable speed drive (VSD) pump replace an existing single- or two-speed pool pump? | 1
Did the Installer follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the circulating block heater to function at optimal energy efficiency? | 1
Did the pipes have existing pipe insulation ? | 1
Did the walk-in cooler or freezer have an existing automatic closer installed? | 1
Display case equipped with humidity-sensing controls based on the store dew point temperature? | 1
Do the contractors and technicians that implement the measure meet all certification and training requirements in accordance with program requirements? | 1
Do the installed doors have low/no anti-sweat heat controls in conjunction with the installed controls? | 1
Do the low-temperature case door and frame heaters combined consume more than 50 W/ft of case length? | 1
Do the medium-temp cases have heat in the door (answer No if there is only heat in the door frame)? | 1
Do the retrofit doors have ASH controls installed? | 1
Documentation submitted showing VFD is not for backup pump? | 1
Does the customer already have a smart thermostat or fan delay controller installed? | 1
Does power reduction decrease by at least 2% for every percentage the humidity falls below 55%? | 1
Does the automatic door closer firmly close the door when it is within one inch of full closure? | 1
Does the base design prescribe a pre-heating device other than a circulating block heater? | 1
Does the boiler installation comply with emission limits per air district, if applicable? (Note that Tier 2 hot water heaters are condensing and often require flue modifications to handle the condensate.) | 1
Does the boiler supply hot water to a circulation loop without an intermediary hot water storage tank? | 1
Does the chiller serve space conditioning equipment? | 1
Does the chiller serve space conditioning/comfort equipment? | 1
Does the control system use a Variable Speed Drive (VSD) on the fan motor? | 1
Does the dryer make use of a common dedicated steam system? | 1
Does the EER of the installed unit exceed code by at least 20%? | 1
Does the equipment type match the Measure Case Description (Air Conditioner or Heat Pump) and is not a ductless mini-split air conditioner? | 1
Does the existing dryer use natural gas? | 1
Does the existing refrigeration system have a multiplex compressor system with saturated condensing temperature (SCT) controls at a fixed setpoint? | 1
Does the existing wall furnace or fireplace insert have pilot light controls? | 1
Does the faucet have an existing aerator installed? | 1
Does the freezer have an ENERGY STAR certification? | 1
Does the ice machine match the measure case equipment type? | 1
Does the installation comply with all applicable regulations, including but not limited to the current California Building Energy Efficiency Standards (Title 24), federal code, and the National Electrical Code® (NEC)? | 1
Does the installation comply with all applicable regulations? | 1
Does the installation comply with all current applicable regulations, code, and standards? | 1
Does the installation include the replacement of multiple-speed or variable speed motors (VSM)? | 1
Does the installed automatic conveyor broiler have a catalyst and an input rate less than 80 kBtu/hr or a dual stage or modulating gas valve with a capability of throttling the input rate below 80 kBtu/hr? | 1
Does the installed case include triple-pane doors with low or no anti-sweat heat or anti-sweat-heat controls? | 1
Does the installed cover have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard)? | 1
Does the installed device meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation? | 1
Does the installed heater have an ON/OFF switch and no pilot light? | 1
Does the installed timer device have seven-day (or better) scheduling capabilities? | 1
Does the installed unit have a remote refrigeration system? | 1
Does the installed unit only provide hot water when there is a hot water draw from the end use? | 1
Does the installed unit only provide hot water when there is a hot water draw from the end use? | 1
Does the installed unit use a mechanical or optical control system? | 1
Does the manufacturer describe the motor as a low-power or high efficiency model? | 1
Does the measure include addition of insulation to hot water and cold-water pipes within the first 3 feet of a storage water heater? | 1
Does the new saturated condensing temperature (SCT) setpoint adjust based on the ambient temperature by controlling condenser fans with variable-speed drives or by staging condenser fans? | 1
Does the nominal capacity of the new VSD pump match the capacity of the pump being replaced? | 1
Does the piping have existing insulation that is damaged or being replaced? | 1
Does the pool cover come with a minimum 5 year warranty? | 1
Does the pump serve a glycol loop? | 1
Does the replacement BFM motor capacity and rated voltage match that of the existing fan motor being replaced? | 1
Does the replacement BFM motor have a warranty of at least two years from date of installation? | 1
Does the shower have a wall-mounted diverter? | 1
Does the split system have a furnace in the AHRI certification that has already received a rebate? | 1
Does the submitted lamp specification sheet list the installed ballast model number showing it to be compatible with the installed lamp? | 1
Does the system include following? 1.An occupancy sensing thermostat 2. An occupancy sensor (wired or wireless) 3. Wiring (if wired) 4. Signal receiver and power pack (if wireless) | 1
Does the tank have existing insulation (in any condition) or evidence of prior insulation being installed ? | 1
Does the unit have a condenser over ambient temperature (COAT) of at least 3 degrees F? | 1
Does the water heater meet all Title 24 and Title 20 testing methods? | 1
Does this fixture/retrofit kit replace a lumen equivalent lamp/fixture of higher wattage? | 1
Does this project meet one of the Code Exemptions: Retrofitting < 10% of luminaires in an enclosed space or retrofitting <= 50 total luminaires per floor or tenant space? | 1
Domestic hot water loop temperature (F) | 1
Domestic hot water served by central system? | 1
Drum Capacity (lbs) | 1
Dual stage economizer: condensate meets sanitary and acidic neutralization of combustion codes? | 1
Duct sealant material | 1
Ductwork installed and tested in accordance with requirements in 2019 Title 24 Section 150.2(b)1D? | 1
Ductwork length > 40-ft been installed and tested in accordance to 2019 Title 24 Section 150.2(b)1D? | 1
During pool operating hours, was the VSD setting “right sized”? | 1
During start-up, system maintains programmed level airflows under both cooling and/or heating? | 1
Economizer efficiency / effectiveness (%) | 1
Economizer manufacturer | 1
Economizer model | 1
Efficacy, Lumens/Watt (LPW) | 1
Efficiency type used for equipment eligibility | 1
Eligible building types include residential single-family, double-wide mobile homes, and in-unit multifamily residences as well as multifamily common area laundry. | 1
Energy Efficiency Rating (EER) | 1
Energy Efficiency Ratio (EER) | 1
Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | 1
Energy per Bun (W/bun) | 1
ENERGY STAR Certification | 1
EnergyStar Certification | 1
EnergyStar Connected Product | 1
Equipment Efficiency (EER) | 1
Equipment type | 1
Exhaust hood airflow (cfm) | 1
Existing air conditioning equipment type | 1
Existing ballast manufacturer | 1
Existing ballast model number | 1
Existing domestic hot water system had demand-controlled recirculation pump? | 1
Existing equipment manufacture date | 1
Existing equipment removed and disposed of rather than refurbished and sold? | 1
Existing Faucet Flow Rate (gpm) | 1
Existing motor was fully functional with no sign of replacement in 12 months from project app. date? | 1
Existing packaged HVAC supply fan motor power (hp) | 1
Existing pump has means to vary the pressure or flow (i.e. throttle valve, control valve, etc.)? | 1
Existing RTU could adjust the changeover setpoint based on the number of thermostat cooling stages? | 1
Existing system can adjust to changeover setpoint based on thermostat stages available for cooling? | 1
Existing system has a constant volume supply fan? | 1
Existing system has operable economizer with high limit set per Title 24 2016 Table 140.4-B? | 1
Existing system is packaged single zone DX cooling w/ gas heat, cooling only, or heat pump? | 1
Existing water heater was a storage tank style and disposed of (not retrofitted)? | 1
Facility sector | 1
Fan cfm/watt | 1
Fan flow rate (CFM) | 1
Fan motor type | 1
Fixture/retrofit kit listing in the Technical Requirements table (V5) on DLC under Classification | 1
Fixture/retrofit kit listing in the Technical Requirements table (V5) on DLC under Primary Use Designations? | 1
For hot water circulation loops, is there an intermediary hot water storage tank? | 1
For models that require an automatic control system capable of controlling both high and low speeds, was a controller installed? | 1
For NC, select the 'new services' condition | 1
Freezer Type | 1
Fryer Type | 1
Full Load Energy Efficiency (kW/ton) | 1
Full Load Energy Efficiency Rating (EER) | 1
Gas heating equipment type | 1
Gas Input Rating (Btu/hr) | 1
Has a field inspection been performed to verify the condenser and if applicable evaporator make and model? | 1
Has a site Pre-Inspection been completed and documentation uploaded in EECP? | 1
Has all POE documentation been submitted as defined in the workpaper? | 1
Has all Preponderance of Evidence (POE) been presented including: Customer site information, Make/model of pre-existing equipment, Make/model of replacement equipment, Permits and associated documentation, and Pump commissioning information? | 1
Has all Preponderance of Evidence (POE) been included as defined in the workpaper? | 1
Has only one rebate been applied per spa or wading pool? | 1
Has only one variable-speed pool pump and motor been installed at the residence? | 1
Has photographic evidence or documentation of the test-in and test-out procedures been uploaded? | 1
Has real time monitoring been implemented to ensure proper operation of the system? | 1
Has required Preponderance of Evidence (POE) been submitted in accordance with the workpaper? | 1
Has the contractor performed condenser coil cleaning prior to installation of the pre-cooler system? | 1
Has the customer agreed not to modify and/or alter, in any way, programmed settings on the pump VSD to ensure persistence of the measure savings? | 1
Has the customer agreed to a post installation inspection? | 1
Has the customer confirmed the operation of the replacement equipment on the application form? | 1
Has the customer received less than or equal to the three maximum rebates per property/site for the main filtration pumps (includes pools, spas, and wading pools)? | 1
Has the customer, as part of the incentive application process, acknowledged that the replacement pool pump VSD has been configured to achieve energy savings and agreed to have the pump filtration settings programmed for reduced flow during pool non-operating hours? | 1
Has the existing equipment been properly disposed of and not abandoned in place? | 1
Has the lighting power density increased with a replacement or retrofit of the LED lighting systems in the display case? | 1
Has the manufacturer cut sheet been submitted? | 1
Has the manufacturer specification sheet been submitted to prove the equipment efficiency? | 1
Has this measure been combined with another refrigeration measure? | 1
Have all POE requirements spelled out in the workpaper been included in the program documentation? | 1
Have any improvements been made that would increase system energy use? | 1
Have existing conditions been recorded and measures are were NOT previously installed? | 1
Have the filtration settings been configured to operate outside peak hours, as defined by the utility? | 1
Heat curtain gas savings rating (%) | 1
Heat Pump Manufacturer | 1
Heat Pump Model | 1
Heat pump water heater storage capacity (gallons) | 1
Heat used to preheat service hot water (not domestic hot water)? | 1
Heating System Capacity (kBtuh) | 1
Heavy Load Cooking Efficiency (%) | 1
Holding cabinet fully insulated (i.e., on all sides) and has solid or transparent doors? | 1
Host equipment type? | 1
Hot water is central, gas-fired, constant-flow, fractional horsepower, uncontrolled recirc pump? | 1
Hours of operation of the hot water system | 1
How much of the pool does the new pool cover encompass? (%) | 1
HP | 1
HPWH First Hour Rating (FHR) | 1
HPWH Manufacturer | 1
HPWH Model | 1
HPWH Storage Capacity (gallons) | 1
HVAC System Cooling Capacity (tons) | 1
HVAC type is a packaged VAV with gas furnace (cPVVG)? | 1
Ice making system type | 1
Idle Energy Rate (watts) | 1
If customer chose Accelerated Replacement, have written/photographic records disposal been provided? | 1
If humidity is not monitored, ASH controls turn off based on the condensation formed on inner glass? | 1
If installed in a conditioned space, existing space heating fuel type | 1
If not a glycol loop, do the unit energy savings exceed the measure case savings? | 1
If site had electrification measures, have itemized infrastructure costs invoices been submitted? | 1
If site required electric infrastructure upgrades, have itemized invoices with costs been submitted? | 1
If the pool is Olympic sized, is there a storage reel system? | 1
If UL Type A + B Configuration, was the existing ballast removed? | 1
IMC | 1
In the installed insulation required by California Building Energy Efficiency Standards (Title 24) or employee safety laws (Occupational Safety and Health Administration, OSHA)? | 1
Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | 1
Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | 1
Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | 1
Input Capacity (BTU/hr) | 1
Input Rating (btu/hr/gallon) | 1
Input rating (HP) | 1
Installation complies with all policies, codes and regulations within the site territory? | 1
Installation contractor | 1
Installation date of existing hood | 1
Installation includes temperature sensor(s) and/or an optic sensor to adjust fan speeds? | 1
Installation is part of a new service defined in Fuel Substitution Technical Guidance for EE? | 1
Installation meets latest NFPA Code 110 for Emergency Power Systems and NEC installation guidelines? | 1
Installed an electronically commutated motor (ECM) or permanent magnet synchronous (PMS) motor/fan? | 1
Installed broiler has an input rate <= 22 kBtu/hr/len-ft with a surface temperature of 600 °F? | 1
Installed in a commercial domestic (or “service”) hot water application in a NonRes facility? | 1
Installed in a NAICS code 31, 31, or 33? | 1
Installed to a functional HVAC unit with cooling/evaporator (dx) coils? | 1
Insulated Holding Cabinet Size (square feet) | 1
Insulation is being installed on bare suction pipes for medium temperature, walk-in coolers | 1
Insulation manufacturer specification sheet submitted with the application? | 1
Insulation material k-value rating | 1
Insulation material type | 1
Integrated Energy Efficiency Ratio (IEER) | 1
Integrated Modified Energy Factor (IMEF) | 1
Integrated Part Load Value (kW/ton) | 1
Integrated pilot light controls are capable of using a battery or voltage line to operate? | 1
Integrated Water Factor (IWF) | 1
IR Film only installed on the roof (not on the walls)? | 1
Is a natural gas-fired boiler or water heater supplying hot water to the laundry equipment? | 1
Is a water treatment system used with the evaporative pre-cooler system? | 1
Is an existing, open, multi-deck display case being replaced with a new reach-in unit with doors, electronically commutated motor (ECM) evaporator fan(s), and LED lighting? | 1
Is new equipment/hardware being installed (i.e. not reprogramming an existing controller)? | 1
Is the ballast existing and an electronic instant start type? | 1
Is the base case broiler a similar size or larger than the replacement unit? | 1
Is the baseline air conditioning system equipped with a hardware based built-in delay controller? | 1
Is the building an existing commercial building? | 1
Is the building type: commercial facilities, such as schools, colleges, universities, YMCA/YWCA, public facilities, hotels/motels, health clubs, and spas. This measure is also applicable for multifamily properties, such as homeowner associations and other multifamily complexes? | 1
Is the case temperature above 32F? | 1
Is the case temperature below 32F? | 1
Is the device installed in a health care facility subject to the OSHPD code and regulation/inspection requirements? | 1
Is the equipment a ductless mini-split air conditioner? | 1
Is the existing belt a cogged V-belt? | 1
Is the existing building considered a Health Care facility as defined by OSHPD? | 1
Is the existing conveyor broiler being replaced by a conveyor broiler similar in size or smaller? | 1
Is the existing faucet served by a natural gas fired water heater in an existing building? | 1
Is the existing unit a low temp coffin with a display width greater than 3 feet? | 1
Is the existing unit a standard efficiency unit of the same configuration and capacity? | 1
Is the existing wall furnace or fireplace insert in working condition (not requiring major repairs)? | 1
Is the facility: • Hospitals (large regional or local) • Emergency rooms • In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals • Doctor offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.) • Clinics and nursing homes | 1
Is the fan controller used for solely optimizing and improving heating efficiency including those for gas furnaces? | 1
Is the fan/blower a designed high-pressure blower (design capacity <= 150 cfm/hp)? | 1
Is the griddle double-sided? | 1
Is the hot water boiler used for space conditioning, industrial (process) end-use applications, pools, or spas? | 1
Is the hot water for the installed commercial-grade PRSV supplied from natural gas water heaters? | 1
Is the HVAC system functional/operable and drawing power? | 1
Is the HVAC type a DX Heat Pump (cDXHP) and the building a refrigerated warehouse (WRf)? | 1
Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | 1
Is the installed equipment a residential-style electric storage water heater? | 1
Is the installed equipment rented or leased? | 1
Is the installed holding cabinet listed on the Food Service Technology Center (FSTC) qualified product list (https://fishnick.com/saveenergy/rebates/)? | 1
Is the installed LFR served by natural gas water heating equipment? | 1
Is the installed product certified by International Association of Plumbing and Mechanical Officials (IAPMO)? | 1
Is the installed smart thermostat in full compliance with the ENERGYSTAR Program Requirements and Product Specification for Connected Thermostats Products Version 1.0 or later? | 1
Is the installed unit a reach-in case that is "1/4" of the total length of the coffin or less? | 1
Is the installed unit an on-demand hand-wrap machine? | 1
Is the insulation for exposed hot-water tanks within seven feet of the floor that are not otherwise guarded in such manner as to prevent contact? | 1
Is the insulation required to prevent burns or is the tank located where burns can be sustained? | 1
Is the insulation R-values of the installed insulation greater than or equal to R-3.2? | 1
Is the insulation R-values of the installed insulation greater than or equal to R-4.3? | 1
Is the LFR labeled as “Vandal Proof” or can not be removed without a proprietary tool, except for dialysis and scrub sink locations? | 1
Is the max flow/capacity of the modulating valve greater than or equal to that of the dryer? | 1
Is the measure a one-for-one pump replacement? | 1
Is the measure an HVAC (evaporator) fan motor with nominal capacity of ½-hp (or less) typically serving HVAC systems with nominal capacities of 3.5 ton (or less)? | 1
Is the measure replacing a shaded pole or permanent split capacitor (PSC) motor with a brushless direct current motor with selectable speed control? | 1
Is the motor installed on a refrigerated display case? | 1
Is the new case length less than or equal to the original case length? | 1
Is the new lighting compatible with the existing lighting controls type (i.e. dimming controls with dimmable LED)? | 1
Is the new motor closely matched to the original motor's speed and shaft output power? | 1
Is the Ozone system installed on a laundry system equipped with a tunnel washer? | 1
Is the ozone transfer into the water via venturi injection or bubble diffusion? | 1
Is the pool heated with natural gas? | 1
Is the pre-existing condition bare suction pipe on a low-temperature, walk-in freezer? | 1
Is the primary target building type for this measure an existing schools/colleges (educational institutions), city (municipal) recreational centers, home owner associations (e.g., condominiums with common pools), private/health clubs, and multifamily residences (apartment buildings)? | 1
Is the pump a mixed flow pump with high volume and low head? | 1
Is the pump is used as a well pump to fill a reservoir or discharging into a canal? | 1
Is the replacement brushless fan motor (BFM) motor and motor controls assembly “UL Listed.”? | 1
Is the return duct in a conditioned space? | 1
Is the setpoint storage temperature range between -70 °C and -80 °C (-94 °F and -112 °F)? | 1
Is the showerhead is installed in tub/shower combination system? | 1
Is the tank that was insulated coupled to gas-fired commercial, industrial, or agriculture equipment that transfers heat to the contained liquid or solution? | 1
Is the TSV certified by applicable standards (e.g., ANSI, ASPE, etc.) ? | 1
Is the unit an air cooled ice maker? | 1
Is the unit being installed in a newly constructed buildings, additions to existing buildings, and alterations to existing buildings? | 1
Is the unit drawing power? | 1
Is the VFD being installed on an existing HVAC supply or return air system | 1
Is the VFD being installed on cooling tower fans? | 1
Is there an existing pool cover in use? | 1
Is this a cook-and-hold retherm equipment? | 1
Is this a Heat Pump clothes dryer? | 1
Is this an electric resistance, passive, or cook-and-hold retherm equipment? | 1
Is this measure being installed on a new construction project? | 1
Is this measure for an HVAC fan? | 1
L90 Lumen Maintenance Hours | 1
Large-scale remodels are defined as any project involving 50% of the linear feet of refrigerated casework or 32 linear feet of casework replacements, whichever is less. Are the display case replacements part of large-scale store remodels? | 1
Lease term 5-years (not annual renewal) and copy of lease agreement uploaded | 1
LED Tube Type | 1
Length of ductwork replaced (linear feet) | 1
Length of piping in linear feet | 1
List other electrification measures installed with the heat pump water heater | 1
Lumens | 1
Manufacturer date of walk-in cooler? | 1
Manufacturer date of walk-in freezer? | 1
Manufacturer specification sheet submitted with the application? | 1
Max Daily Potable Water Use Limit (gal/100 lbs. ice) | 1
Max Idle Energy Rate (Btu/h) | 1
Max Idle Energy Rate (W) | 1
Max Idle Energy Rate (W/ft2/hr) | 1
Max Idle Energy Rate (watts/ft3) | 1
Max. Estimated Annual Energy Use (kWh/yr) | 1
Max. Water Consumption (gallons/cycle) | 1
Maximum daily energy consumption(MDEC) (kWh/day/ft3) | 1
Maximum Daily Energy Use (kWh/100 lbs. ice) | 1
Maximum Water Consumption (Gallons per Rack) | 1
Measure combined with evaporative fan controller for walk-in coolers and/or freezers? | 1
Measure installed in conjunction with floating head pressure controls? | 1
Measure installed on a newly constructed, additions or alterations to an existing building? | 1
Measure is installed for wine processing? | 1
Minimum HVAC delivery air flow rate (cfm/ton) | 1
Model Number | 1
Modified Energy Factor J2 (MEF) | 1
Motor Manufacturer | 1
Motor Model | 1
Natural gas must be supplied by a California utility. | 1
New Faucet Flow Rate (gpm) | 1
New gravity wall furnace is replacing an existing gravity wall furnace? | 1
Nominal Capacity (tons) | 1
Number of Guest Rooms | 1
OA Reset Control (F) | 1
Only eligible for Single Family Homes, did the customer perform self-installation of the new pump? | 1
Oven Mode Cooking Efficiency (%) | 1
Oven Mode Idle Energy Rate (Btu/hr) | 1
Oven Mode Idle Energy Rate (watts) | 1
Oven Production Capacity (lbs/hr) | 1
PA shall confirm that the customer has a newly purchased smart thermostat. At minimum, the PA shall obtain a copy of the thermostat sales receipt and the PA shall confirm the purchase date is on or after the program start date. | 1
Pan Capacity | 1
Percent OA verified for heating and cooling for each stage as well as ventilation only mode? | 1
Percent of refrigerant added or removed | 1
Photograph of existing heating equipment submitted? | 1
Photograph of open belly return duct submitted? | 1
Photograph showing deterioration, damage, or poor installation of crossover duct submitted? | 1
Pipe Diameter (in) | 1
Post leakage rate (%) | 1
Pre leakage rate (%) | 1
Pre-Existing Conditions: Automated controls type in retrofitted spaces | 1
Pre-Existing Conditions: Number of Ballasts per Fixture | 1
Pre-Existing Conditions: Percent of Fixtures Sampled | 1
Preheat Energy (Btu/hr) | 1
Preheat Energy (watts) | 1
Preheat Energy Rate (kW) | 1
Preheat Time (mins) | 1
Primarily used for domestic water? | 1
Proc-lbs | 1
Product has a warranty >= 5 years | 1
Product qualification method? | 1
Production Capacity (lb/hr) | 1
Production Capacity (units/hr) | 1
Production Per Day (lbs) | 1
Proof of purchase submitted showing Integrated intermittent pilot light in the wall furnace? | 1
Proposed furnace is replacing an existing gas furnace? | 1
Pump annual hours of operation (hr/yr) | 1
Pump horsepower (hp) | 1
Pump type | 1
Purchase date of newly installed thermostat | 1
QM1: Is the HVAC system drawing power? | 1
QM2: For refrigerant charge adjustments, does the unit deliver supply air of at least 350 cfm/ton? | 1
QM3: Does the unit have a condenser over ambient temperature (COAT) of at least 3 degrees F? | 1
QM4: Has a report been submitted meeting ACCA Standard 4 prior to any treatments being applied? | 1
Quantity (sq ft) of heat curtain does not include overlap or exceed sq ft of the floor? | 1
R value (ft2-hr-F/Btu) | 1
Rated equipment capacity (kBtu/hr) | 1
Rated Input (Btuh) | 1
Rated-HP | 1
Refrigerant charge adjustments, unit has been tested to deliver supply air of at least 350 cfm/ton? | 1
Refrigeration Multiplex System | 1
Refrigeration suction pipe diameter on existing equipment in inches | 1
Replacement duct material | 1
Replacement fixture/retrofit kit on the most recent version of the DLC qualified product list? | 1
Replacement motor efficiency (%) | 1
Report been submitted in accordance with ACCA Standard 4 prior to any treatments being applied? | 1
Required NC document(s) submitted as outlined in the measure package? | 1
Return duct insulation thermal resistance (R) | 1
Seasonal Energy Efficiency Ratio (SEER) | 1
Seasonal Energy Efficiency Ratio (SEER) value | 1
Select the most appropriate building vintage | 1
Select the most appropriate Multiplex compressor system vintage | 1
Size ( kBtu/hr) | 1
Size (Btu/hr) | 1
Size (gallons) | 1
Size of Recirculation Pump Motor | 1
Sizing exemption for chillers > 300 tons | 1
Software used to control SRM | 1
Steam boiler input rating (MMBtu/hr) | 1
Steam boiler manufacturer | 1
Steam boiler model | 1
Steam boiler spec sheet submitted? | 1
Steam Mode Cooking Efficiency (%) | 1
Steam Mode Idle Energy Rate (Btu/hr) | 1
Steam Mode Idle Energy Rate (watts) | 1
Steam Pressure (psig) | 1
Steam Production Capacity (lbs/hr) | 1
Sticker Number | 1
System Efficacy, Lumens/Watt (LPW) as listed on DLC | 1
System Efficacy, Lumens/Watt (LPW) listed on DLC | 1
System is served by chilled water or serves domestic hot water? | 1
System used for comfort/space cooling, not process or refrigeration loads? | 1
Temperature inside the tank (F) | 1
Test-in Duct Leakage Rate (%) | 1
Test-out Duct Leakage Rate (%) | 1
The greenhouse curtain must be a single layer plastic curtain | 1
The installation address must have a commercial natural gas account. | 1
The IR film must be infrared, anti-condensate, polyethylene plastic with a minimum thickness of six thousandths of an inch. | 1
The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. | 1
The PA shall confirm that the customer has a newly purchased smart thermostat. At minimum, the PA shall obtain a copy of the thermostat sales receipt and the PA shall confirm the purchase date is on or after the program start date. | 1
The PA shall determine customer eligibility prior to rebate payment. Upon request, all data associated with determining eligibility shall be provided to Energy Division of the California Public Utilities Commission (CPUC). All PAs shall extend this requirement to all third-party vendors that assist PAs with determining customer eligibility. To the extent that they are used to determine eligibility, data regarding dates of purchase, location of home, customer HVAC equipment type, pre-installation HVAC energy use, etc. shall be made available. | 1
The program administrator (PA) shall employ QA/QC procedures to ensure that the thermostat is installed in an eligible home and is attached to the type of HVAC equipment that is being incentivized, whether it is for natural gas or electricity savings. | 1
The purchase invoice must be provided as a proof that the wall furnace has been purchased to replace a previously existing unit. Additionally, the customer must agree to a post measure installation inspection. | 1
The submitted product specifications should match the measure description in EECP including the Tier, Size, Venting type, Fuel type, and Voltage (if fuel type is electric) | 1
Thermal efficiency of installed heater (%) | 1
This equipment must be installed by a qualified HVAC Contractor. Please verify the invoice and/or installation contract that verifies the equipment was installed by a qualified HVAC contractor has been submitted. | 1
This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | 1
This measure is not eligible when there is no natural gas to electricity fuel substitution for heating and/or when the measures include a non-regulated fuel. New construction measures are only eligible under certain conditions listed in the above section. Ground up constructions are not eligible. | 1
Total dryer capacity affected (lbs) | 1
Total hp that can benefit from this measure above the max power rating offered by the measure (>3hp) | 1
Total unit airflow has been verified for at least one of the fan speeds? | 1
Total washing machine capacity (lbs) | 1
Type of fan controller installed? | 1
Type of insulation | 1
Type of insulation for hot water pipes installed | 1
Type of refrigerated display case the motor is being installed on | 1
Type of tank material (steel, fiberglass, etc.) | 1
Unit has multi-speed indoor fan and gas furnace heating? | 1
Unoccupied supply fan operation already set to “Auto” or intermittent? | 1
Usage | 1
VFD installed on an existing constant speed pump motor? | 1
VFD is automated by pressure, fluid temperature, or flow rate feedback? | 1
VFD is installed on a pressurized irrigation system (no flood irrigation)? | 1
VFD is used for flow/pressure control, not for soft start or cavitation? | 1
VFD Manufacturer | 1
VFD Model | 1
Volume (cu. ft.) | 1
Volume less than 7.75 cu. ft. and Height < 36 inches | 1
Volume of freezer in cubic feet? | 1
Volume of reach-in unit (ft3) | 1
VSD controlled by static pressure, airflow, or duct velocity and meets IEEE 519-2014.2 requirements? | 1
VSD Manufacturer | 1
VSD Model | 1
VSD setting percentage during non-operating hours | 1
Wall furnaces that are direct-vent systems that mount on an outside wall are not eligible. | 1
Was a design consultant used for major refrigeration system upgrades as a result of this measure? | 1
Was a High Efficiency Package Terminal Air Conditioner (Non Res) DX Unit installed? | 1
Was a medium-temperature, open, vertical refrigerated display case with a high efficiency evaporator coil installed? | 1
Was a minimum thickness of 1 inch of pipe insulation added to existing bare pipe? | 1
Was a new commercial-grade PRSV with a maximum flow rate = 0.75 gpm installed that replaced an existing PRSV with a maximum flow rate of 1.00 gpm for a spray force of < 5.0 ozf? | 1
Was a new commercial-grade PRSV with a maximum flow rate = 1.07 gpm installed that replaced an existing PRSV with a maximum flow rate of 1.20 gpm for a spray force of > 5.0 ozf and < 8.0 ozf? | 1
Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | 1
Was a pool pump installed in a spa or jacuzzi? | 1
Was a professional installer used to remove and reattach the gas line? | 1
Was add. tech verification of thermostat wiring and number of cooling stages that should be performed to ensure the 1st stage of cooling is dedicated to economizer operation and 2-stage thermostat operation is enabled performed if possible? | 1
Was an undercounter high temperature dishwasher installed (not another dishwasher types such as: conveyor, door-type, flight-type)? | 1
Was entire AHRI-tested ice making system purchased? | 1
Was field documentation of the existing conditions that verify the measure was necessary and that the measure was successfully applied submitted? | 1
Was the automatic door closer installed on the main insulated opaque door(s) of an existing walk-in cooler or freezer? | 1
Was the controller changeover setpoint adjusted appropriately based on the available number of thermostat cooling stages? | 1
Was the equipment fully replaced (i.e. not a part swap or motor only replacement)? | 1
Was the existing broiler an automatic conveyor broiler than could maintain a temperature above 600 °F with a tested idle rate greater than 40 kBtu/hr for a belt narrower than 20 inches? | 1
Was the installation of the circulating block heater performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician)? | 1
Was the installed equipment new? | 1
Was the installed equipment won as a prize? | 1
Was the installed unit the same style as the existing case? | 1
Was the measure installed in a new construction application? | 1
Was the measure installed in an eligible home and attached to the type of HVAC equipment that is being incentivized? | 1
Was the measure installed on a main filtration pump? | 1
Was the measure installed where recirculation pumps are used or where potential crossover between hot water and cold water may occur? | 1
Was the motor installed to replace a supply fan (not a return fan or outdoor air fan) of a packaged HVAC unit? | 1
Was the pump being replaced disposed of rather than refurbished and/or sold? | 1
Was the VSD pump configured to meet program pump configuration requirements? | 1
Was third-party baseline verification and data gathering in full compliance with the established POE requirements performed? | 1
Was this measure installed on a new faucet that met or exceeded the 2016 California Appliance Efficiency Regulations (Title 20) code requirement of 1.2 gpm flow rate for lavatory faucet and 1.8 gpm flow rate for kitchen faucet? | 1
Water consumption of dishwasher in gallons per rack | 1
Water Consumption Rate (gal/hr) | 1
Water heater fuel type | 1
Water heater is primarily used for domestic hot water, not for space conditioning, pools or spas? | 1
Water heater meet all emissions requirements as outlined by local air quality management districts? | 1
Wattage | 1
Were all health code requirements and inspections passed successfully? | 1
What is area in square footage of the pool area | 1
What is the assumed baseline fuel type? | 1
What is the fixture Color Rendering Index (CRI)? | 1
What type of HVAC system does the customer have? | 1
When was the walk-in installed in the building? | 1
Where is the tank located? | 1

## SDG&E Data (searching)
Color Control | Workpaper ID | Revision # | WP Name | WP Offering ID | MeasAppType | DeliveryType | Column1 | System of Record | Sort Order | Source Record (Item from Workpaper requiring Property) | Property Enabled | Property Name | Property - Label | Property - Installation - Control Type | Property - Installation - Values - Custom | Column2 | Validation criteria | Validation Correct Answer | Numeric Type | Min Value | Max Value | Decimal Places | ValidationRule | Validation Checkpoint | Validation Verification | Pass Criteria | Alternate Validation Checkpoint | Alternate Validation Verification | Alternate Pass Criteria | QC and Notes for CPSS | Finalized Date | Sign Off | Comment | Mgmt. Comment | Property Label Len
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Any | Any | Any |  | EECP | 0 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 12
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Any | Any | Any |  | EECP | 0 | Eligible building types include any residential single family, multifamily, and residential double-wide mobile homes. | Yes |  | Building Type | Drop Down List | Residential single family;Multifamily;Double-wide mobile home; | [8 empty] | Inspections | Document the type of residence the unit was installed in (Single Family Home, Multifamily, or Mobile Home) | The building type listed in EECP should match the building type during the inspection | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 13
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Any | Any | Any |  | EECP | 5 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 5
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Any | Any | Any |  | EECP | 10 | The product eligibility requirements for the ENERGY STAR and ENERGY STAR Most Efficient tiers are provided below. See Measure Case Description for a full list of refrigerator model specifications. Must be on the ENERGY STAR qualifying list. | Yes |  | ENERGY STAR Certification | Drop Down List | Yes;No |  |  | Yes |  |  |  |  | Must be Yes | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being EnergyStar certified | The make and model from EECP should be present on the EnergyStar database as being a certified product | Inspections | Photograph the EnergyStar label on the unit | The EnergyStar label should be locatable on the unit or within the nameplate | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 25
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | A | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | B | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | C | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | D | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | E | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | F | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | G | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | H | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | I | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | J | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | K | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | L | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | M | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | N | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | O | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | P | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Q | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | R | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | S | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | T | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | U | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | V | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | W | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | X | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Y | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Z | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AA | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AB | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AC | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AD | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AE | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AF | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AG | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AH | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AI | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AJ | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AK | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AL | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AM | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AN | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AO | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AP | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AQ | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AR | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AS | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AT | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AU | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AV | Any | Any |  | EECP | 15 | ENERGY STAR Most Efficient (15% above the federal standard) • ENERGY STAR Most Efficient qualified refrigerators must use less than or equal to 637 kWh per year. • Top freezers do not have to meet the 15% requirement; only the ≤ 637 kWh/year requirement. | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 | 637 |  | Must be <= 637 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database and be <= 637 kWh/yr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AW | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AX | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AY | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AZ | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BA | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BB | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BC | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BD | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BE | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BF | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BG | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BH | Any | Any |  | EECP | 15 | Good to have | Yes |  | Annual Energy Use (kWh/yr) | Numeric Value |  |  |  |  | General | 0 |  |  | Must be > 0 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) for the make and model | The Annual Energy Use (kWh/yr) from EECP should match what is listed on the EnergyStar database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 26
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | A | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Volume less than 7.75 cu. ft. and Height < 36 inches | Drop Down List | Yes;No; |  |  | Maybe just change to Numeric to capture volume, but then would have to add height… |  |  |  |  | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine the Volume (cu. ft.) and Height (in) for the make and model | The Volume (cu. ft.) listed on the EnergyStar database must be less than 7.75 cu. ft. The Height (in) listed on the EnergyStar database must be less than 36 inches | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 52
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | B | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | C | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Volume less than 7.75 cu. ft. and Height < 36 inches | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine the Volume (cu. ft.) and Height (in) for the make and model | The Volume (cu. ft.) listed on the EnergyStar database must be less than 7.75 cu. ft. The Height (in) listed on the EnergyStar database must be less than 36 inches | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 52
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | D | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Volume less than 7.75 cu. ft. and Height < 36 inches | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine the Volume (cu. ft.) and Height (in) for the make and model | The Volume (cu. ft.) listed on the EnergyStar database must be less than 7.75 cu. ft. The Height (in) listed on the EnergyStar database must be less than 36 inches | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 52
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | E | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | F | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | G | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | H | Any | Any |  | EECP | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Volume less than 7.75 cu. ft. and Height < 36 inches | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine the Volume (cu. ft.) and Height (in) for the make and model | The Volume (cu. ft.) listed on the EnergyStar database must be less than 7.75 cu. ft. The Height (in) listed on the EnergyStar database must be less than 36 inches | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 52
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | I | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | J | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | K | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | L | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | M | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | N | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | O | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | P | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Q | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | R | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | S | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | T | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | U | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | V | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | W | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | X | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Y | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | Z | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AA | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AB | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AC | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AD | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AE | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AF | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AG | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AH | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AI | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AJ | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AK | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AL | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AM | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AN | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AO | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AP | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AQ | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AR | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AS | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AT | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AU | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AV | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Yes |  | Ineligible products for ENERGY STAR Most Efficient refrigerators (15% above federal standard) include: • Sub-Compact refrigerators, all-refrigerators, and freezers. • Keg/beverage centers and wine coolers/chillers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact, Keg/beverage centers, or wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 214
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AW | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AX | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AY | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | AZ | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BA | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BB | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BC | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BD | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BE | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BF | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BG | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | BH | Any | Any |  | QA Checklist | 20 | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Yes |  | Ineligible products for ENERGY STAR +5% include: • Sub-Compact freezers. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Sub-Compact on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 72
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | A | Any | Any |  | QA Checklist | 25 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | C | Any | Any |  | QA Checklist | 25 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | D | Any | Any |  | QA Checklist | 25 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
1 | SWAP001 | 2 | Refrigerator or Freezer, Residential | H | Any | Any |  | QA Checklist | 25 | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Yes |  | Ineligible products for ENERGY STAR refrigerators (10% above federal standard) include: • Keg/beverage centers and wine coolers/chillers. • Refrigerators larger than 7.75 ft3 and 36 inches or more in height do not qualify for a compact refrigerator rebate. | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine the Type, Ice Maker, Capacity (Volume, cu. ft.) of refrigerator match the measure description | The Type must not be listed as Keg/beverage centers and wine coolers/chillers on the EnergyStar database. Ensure the specifications listed on the EnergyStar database align with the measure case description (Type, Ice Maker, Capacity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 256
0 | SWAP003 | 2 | Clothes Dryer, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 12
0 | SWAP003 | 2 | Clothes Dryer, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 5
0 | SWAP003 | 2 | Clothes Dryer, Residential | Any | Any | Any |  | EECP | 3 | Eligible building types include any new or existing residential building, including single family, multifamily units, and double-wide mobile homes. | Yes |  | Building Type | Drop Down List | Residential single family;Multifamily;Double-wide mobile home; | [8 empty] | Inspections | Document the type of residence the unit was installed in (Single Family Home, Multifamily, or Mobile Home) | The building type listed in EECP should match the building type during the inspection | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 13
0 | SWAP003 | 2 | Clothes Dryer, Residential | H | Any | Any |  | EECP | 4 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
0 | SWAP003 | 2 | Clothes Dryer, Residential | I | Any | Any |  | EECP | 5 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
0 | SWAP003 | 2 | Clothes Dryer, Residential | J | Any | Any |  | EECP | 6 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
0 | SWAP003 | 2 | Clothes Dryer, Residential | K | Any | Any |  | EECP | 7 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
0 | SWAP003 | 2 | Clothes Dryer, Residential | L | Any | Any |  | EECP | 8 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
0 | SWAP003 | 2 | Clothes Dryer, Residential | M | Any | Any |  | EECP | 9 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
0 | SWAP003 | 2 | Clothes Dryer, Residential | Any | Any | Any |  | QA Checklist | 10 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) and ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. | Yes |  | The submitted product specifications should match the measure description in EECP including the Tier, Size, Venting type, Fuel type, and Voltage (if fuel type is electric) | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being EnergyStar certified | If the product is deemed certified, verify the product falls within the measure case description (i.e. the Tier, Size, Venting type, Fuel type, and Voltage (if fuel type is electric) should all align between EnergyStar and EECP) | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-08-04 | Kenny Liljestrom |  | Add | 171
1 | SWAP003 | 3 | Clothes Dryer, Residential | Any | Any | Any |  | EECP | 0 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 12
1 | SWAP003 | 3 | Clothes Dryer, Residential | Any | Any | Any |  | EECP | 0 | Eligible building types include any new or existing residential building, including single family, multifamily units, and double-wide mobile homes. | Yes |  | Building Type | Drop Down List | Residential single family;Multifamily;Double-wide mobile home; | [8 empty] | Inspections | Document the type of residence the unit was installed in (Single Family Home, Multifamily, or Mobile Home) | The building type listed in EECP should match the building type during the inspection | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 13
1 | SWAP003 | 3 | Clothes Dryer, Residential | Any | Any | Any |  | EECP | 5 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 5
1 | SWAP003 | 3 | Clothes Dryer, Residential | H | Any | Any |  | EECP | 10 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; |  |  | Yes |  |  |  |  | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
1 | SWAP003 | 3 | Clothes Dryer, Residential | I | Any | Any |  | EECP | 10 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; |  |  | Yes |  |  |  |  | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
1 | SWAP003 | 3 | Clothes Dryer, Residential | J | Any | Any |  | EECP | 10 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; |  |  | Yes |  |  |  |  | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
1 | SWAP003 | 3 | Clothes Dryer, Residential | K | Any | Any |  | EECP | 10 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; |  |  | Yes |  |  |  |  | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
1 | SWAP003 | 3 | Clothes Dryer, Residential | L | Any | Any |  | EECP | 10 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; |  |  | Yes |  |  |  |  | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
1 | SWAP003 | 3 | Clothes Dryer, Residential | M | Any | Any |  | EECP | 10 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) OR ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. Advanced Tier electric clothes dryers must be heat pump clothes dryers. | Yes |  | Is this a Heat Pump clothes dryer? | Drop Down List | Yes;No; |  |  | Yes |  |  |  |  | Must be 'Yes' | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being a Heat Pump type | EnergyStar must indicate the 'Type' as Heat Pump | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 34
1 | SWAP003 | 3 | Clothes Dryer, Residential | Any | Any | Any |  | QA Checklist | 205 | Eligible clothes dryers must comply with the ENERGY STAR (Basic Tier) and ENERGY STAR Most Efficient (Advanced Tier) classification presented in the Measure Case Description. | Yes |  | The submitted product specifications should match the measure description in EECP including the Tier, Size, Venting type, Fuel type, and Voltage (if fuel type is electric) | Text Box | [9 empty] | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being EnergyStar certified | If the product is deemed certified, verify the product falls within the measure case description (i.e. the Tier, Size, Venting type, Fuel type, and Voltage (if fuel type is electric) should all align between EnergyStar and EECP) | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-08-04 | Kenny Liljestrom |  | Add | 171
0 | SWAP004 | 2 | Clothes Washer, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 12
0 | SWAP004 | 2 | Clothes Washer, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 5
0 | SWAP004 | 2 | Clothes Washer, Residential | Any | Any | Any |  | EECP | 3 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | EnergyStar Certification | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being EnergyStar certified | The make and model from EECP should be present on the EnergyStar database as being a certified product | Inspections | Photograph the EnergyStar label on the unit | The EnergyStar label should be locatable on the unit or within the nameplate | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 24
0 | SWAP004 | 2 | Clothes Washer, Residential | Any | Any | Any |  | EECP | 4 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | EnergyStar Connected Product | Drop Down List | Yes;No | [8 empty] | QA Checklist | Use the EnergyStar database to determine if the make and model are labeled as being EnergyStar Connected (i.e. capable of reporting energy usage) | The make and model from EECP should be present on the EnergyStar database as being an EnergyStar Connected product | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 28
0 | SWAP004 | 2 | Clothes Washer, Residential | A | Any | Any |  | EECP | 5 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Volume (cu. ft.) | Numeric Value | [8 empty] | Must be > 2.5 and <= 6.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 2.5 and <= 6.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | A | Any | Any |  | EECP | 6 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Integrated Modified Energy Factor (IMEF) | Numeric Value | [8 empty] | If 'EnergyStar Connected Product' is Yes then must be >= 2.76 If 'EnergyStar Connected Product' is No then must be >= 2.62 | QA Checklist | Use the EnergyStar database to determine the Integrated Modified Energy Factor (IMEF) of the Washing Machine | The Integrated Modified Energy Factor (IMEF) must be listed on EnergyStar as >= 2.76 If the product is an EnergyStar Connected unit, the Integrated Modified Energy Factor (IMEF) must be >= 2.62 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 40
0 | SWAP004 | 2 | Clothes Washer, Residential | A | Any | Any |  | EECP | 7 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [8 empty] | Must be <= 3.2 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 3.2 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | B | Any | Any |  | EECP | 8 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Volume (cu. ft.) | Numeric Value | [8 empty] | Must be > 2.5 and <= 6.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 2.5 and <= 6.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | B | Any | Any |  | EECP | 9 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Integrated Modified Energy Factor (IMEF) | Numeric Value | [8 empty] | If 'EnergyStar Connected Product' is Yes then must be >= 2.76 If 'EnergyStar Connected Product' is No then must be >= 2.62 | QA Checklist | Use the EnergyStar database to determine the Integrated Modified Energy Factor (IMEF) of the Washing Machine | The Integrated Modified Energy Factor (IMEF) must be listed on EnergyStar as >= 2.76 If the product is an EnergyStar Connected unit, the Integrated Modified Energy Factor (IMEF) must be >= 2.62 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 40
0 | SWAP004 | 2 | Clothes Washer, Residential | B | Any | Any |  | EECP | 10 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [8 empty] | Must be <= 3.2 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 3.2 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | G | Any | Any |  | EECP | 11 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Volume (cu. ft.) | Numeric Value | [8 empty] | Must be > 2.5 and <= 6.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 2.5 and <= 6.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | G | Any | Any |  | EECP | 12 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Integrated Modified Energy Factor (IMEF) | Numeric Value | [8 empty] | If 'EnergyStar Connected Product' is Yes then must be >= 2.06 If 'EnergyStar Connected Product' is No then must be >= 1.96 | QA Checklist | Use the EnergyStar database to determine the Integrated Modified Energy Factor (IMEF) of the Washing Machine | The Integrated Modified Energy Factor (IMEF) must be listed on EnergyStar as >= 2.06 If the product is an EnergyStar Connected unit, the Integrated Modified Energy Factor (IMEF) must be >= 1.96 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 40
0 | SWAP004 | 2 | Clothes Washer, Residential | G | Any | Any |  | EECP | 13 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [8 empty] | Must be <= 4.3 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 4.3 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | H | Any | Any |  | EECP | 14 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Volume (cu. ft.) | Numeric Value | [8 empty] | Must be > 2.5 and <= 6.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 2.5 and <= 6.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | H | Any | Any |  | EECP | 15 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Integrated Modified Energy Factor (IMEF) | Numeric Value | [8 empty] | If 'EnergyStar Connected Product' is Yes then must be >= 2.06 If 'EnergyStar Connected Product' is No then must be >= 1.96 | QA Checklist | Use the EnergyStar database to determine the Integrated Modified Energy Factor (IMEF) of the Washing Machine | The Integrated Modified Energy Factor (IMEF) must be listed on EnergyStar as >= 2.06 If the product is an EnergyStar Connected unit, the Integrated Modified Energy Factor (IMEF) must be >= 1.96 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 40
0 | SWAP004 | 2 | Clothes Washer, Residential | H | Any | Any |  | EECP | 16 | ENERGY STAR Residential Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR-qualified top-loading or front-loading model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Top-loading models must have an Integrated Modified Energy Factor (IMEF) ≥ 2.06 and an Integrated Water Factor (IWF) ≤ 4.3. – Front-loading models must have IMEF ≥ 2.76 and an IWF ≤ 3.2. – Qualified machines that satisfy the ENERGY STAR Connected criteria are allowed an IMEF 5% lower than the minimum qualifying standard. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [8 empty] | Must be <= 4.3 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 4.3 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | C | Any | Any |  | EECP | 17 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Volume (cu. ft.) | Numeric Value | [8 empty] | Must be > 2.5 and <= 6.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 2.5 and <= 6.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | C | Any | Any |  | EECP | 18 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Integrated Modified Energy Factor (IMEF) | Numeric Value | [8 empty] | Must be >= 2.92 | QA Checklist | Use the EnergyStar database to determine the Integrated Modified Energy Factor (IMEF) of the Washing Machine | The Integrated Modified Energy Factor (IMEF) must be listed on EnergyStar as >= 2.92 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 40
0 | SWAP004 | 2 | Clothes Washer, Residential | C | Any | Any |  | EECP | 19 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [8 empty] | Must be <= 3.2 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 3.2 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | D | Any | Any |  | EECP | 20 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Volume (cu. ft.) | Numeric Value | [8 empty] | Must be > 2.5 and <= 6.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 2.5 and <= 6.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | D | Any | Any |  | EECP | 21 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Integrated Modified Energy Factor (IMEF) | Numeric Value | [8 empty] | Must be >= 2.92 | QA Checklist | Use the EnergyStar database to determine the Integrated Modified Energy Factor (IMEF) of the Washing Machine | The Integrated Modified Energy Factor (IMEF) must be listed on EnergyStar as >= 2.92 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 40
0 | SWAP004 | 2 | Clothes Washer, Residential | D | Any | Any |  | EECP | 22 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [8 empty] | Must be <= 3.2 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 3.2 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | I | Any | Any |  | EECP | 23 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Volume (cu. ft.) | Numeric Value | [8 empty] | Must be > 2.5 and <= 6.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 2.5 and <= 6.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | I | Any | Any |  | EECP | 24 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Integrated Modified Energy Factor (IMEF) | Numeric Value | [8 empty] | Must be >= 2.92 | QA Checklist | Use the EnergyStar database to determine the Integrated Modified Energy Factor (IMEF) of the Washing Machine | The Integrated Modified Energy Factor (IMEF) must be listed on EnergyStar as >= 2.92 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 40
0 | SWAP004 | 2 | Clothes Washer, Residential | I | Any | Any |  | EECP | 25 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [8 empty] | Must be <= 3.2 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 3.2 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | J | Any | Any |  | EECP | 26 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Volume (cu. ft.) | Numeric Value | [8 empty] | Must be > 2.5 and <= 6.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 2.5 and <= 6.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | J | Any | Any |  | EECP | 27 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Integrated Modified Energy Factor (IMEF) | Numeric Value | [8 empty] | Must be >= 2.92 | QA Checklist | Use the EnergyStar database to determine the Integrated Modified Energy Factor (IMEF) of the Washing Machine | The Integrated Modified Energy Factor (IMEF) must be listed on EnergyStar as >= 2.92 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 40
0 | SWAP004 | 2 | Clothes Washer, Residential | J | Any | Any |  | EECP | 28 | ENERGY STAR Most Efficient Clothes Washer > 2.5 cubic feet – Must be an ENERGY STAR Most Efficient model that is a top-loading or front-loading residential model. – The clothes container volume must be > 2.5 and ≤ 6.0 cubic feet. – Models > 2.5 cubic feet must have an IMEF ≥ 2.92 and an IWF ≤ 3.2. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [8 empty] | Must be <= 3.2 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 3.2 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | E | Any | Any |  | EECP | 29 | ENERGY STAR Commercial Clothes Washer - Owned – Must be an ENERGY STAR-qualified commercial front-loading model. – The clothes container volume must be > 1.6 and < 8.0 cubic feet. – All models must have MEF J2 ≥ 2.2 and IWF ≤ 4.0 | Yes |  | Volume (cu. ft.) | Numeric Value | [8 empty] | Must be > 1.6 and < 8.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 1.6 and < 8.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | E | Any | Any |  | EECP | 30 | ENERGY STAR Commercial Clothes Washer - Owned – Must be an ENERGY STAR-qualified commercial front-loading model. – The clothes container volume must be > 1.6 and < 8.0 cubic feet. – All models must have MEF J2 ≥ 2.2 and IWF ≤ 4.0 | Yes |  | Modified Energy Factor J2 (MEF) | Numeric Value | [8 empty] | Must be >= 2.20 | QA Checklist | Use the EnergyStar database to determine the Modified Energy Factor J2 (MEF J2) of the Washing Machine | The Modified Energy Factor J2 (MEF J2) must be listed on EnergyStar as >= 2.20 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 31
0 | SWAP004 | 2 | Clothes Washer, Residential | E | Any | Any |  | EECP | 31 | ENERGY STAR Commercial Clothes Washer - Owned – Must be an ENERGY STAR-qualified commercial front-loading model. – The clothes container volume must be > 1.6 and < 8.0 cubic feet. – All models must have MEF J2 ≥ 2.2 and IWF ≤ 4.0 | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [8 empty] | Must be <= 4.0 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 4.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | F | Any | Any |  | EECP | 32 | ENERGY STAR Commercial Clothes Washer – Leased – Must be an ENERGY STAR-qualified commercial front-loading model. – The clothes container volume must be > 1.6 and < 8.0 cubic feet. – All models must have MEF J2 ≥ 2.2 and IWF ≤ 4.0 – Lease Term must be for a minimum term of 5 years and term cannot end prior to five years after the qualified measure is installed. Annual renewal leases do not qualify. | Yes |  | Volume (cu. ft.) | Numeric Value | [8 empty] | Must be > 1.6 and < 8.0 | QA Checklist | Use the EnergyStar database to determine the Volume of the Washing Machine | The Volume must be listed on EnergyStar as > 1.6 and < 8.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 16
0 | SWAP004 | 2 | Clothes Washer, Residential | F | Any | Any |  | EECP | 33 | ENERGY STAR Commercial Clothes Washer – Leased – Must be an ENERGY STAR-qualified commercial front-loading model. – The clothes container volume must be > 1.6 and < 8.0 cubic feet. – All models must have MEF J2 ≥ 2.2 and IWF ≤ 4.0 – Lease Term must be for a minimum term of 5 years and term cannot end prior to five years after the qualified measure is installed. Annual renewal leases do not qualify. | Yes |  | Modified Energy Factor J2 (MEF) | Numeric Value | [8 empty] | Must be >= 2.20 | QA Checklist | Use the EnergyStar database to determine the Modified Energy Factor J2 (MEF J2) of the Washing Machine | The Modified Energy Factor J2 (MEF J2) must be listed on EnergyStar as >= 2.20 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 31
0 | SWAP004 | 2 | Clothes Washer, Residential | F | Any | Any |  | EECP | 34 | ENERGY STAR Commercial Clothes Washer – Leased – Must be an ENERGY STAR-qualified commercial front-loading model. – The clothes container volume must be > 1.6 and < 8.0 cubic feet. – All models must have MEF J2 ≥ 2.2 and IWF ≤ 4.0 – Lease Term must be for a minimum term of 5 years and term cannot end prior to five years after the qualified measure is installed. Annual renewal leases do not qualify. | Yes |  | Integrated Water Factor (IWF) | Numeric Value | [8 empty] | Must be <= 4.0 | QA Checklist | Use the EnergyStar database to determine the Integrated Water Factor (IWF) of the Washing Machine | The Integrated Water Factor (IWF) must be listed on EnergyStar as <= 4.0 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 29
0 | SWAP004 | 2 | Clothes Washer, Residential | F | Any | Any |  | EECP | 35 | ENERGY STAR Commercial Clothes Washer – Leased – Must be an ENERGY STAR-qualified commercial front-loading model. – The clothes container volume must be > 1.6 and < 8.0 cubic feet. – All models must have MEF J2 ≥ 2.2 and IWF ≤ 4.0 – Lease Term must be for a minimum term of 5 years and term cannot end prior to five years after the qualified measure is installed. Annual renewal leases do not qualify. | Yes |  | Lease term 5-years (not annual renewal) and copy of lease agreement uploaded | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | Implementer should provide a copy of the lease terms and conditions for review | The lease language must indicate: • A minimum of 5-years continuous • No annual renewal of lease | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 76
0 | SWAP004 | 2 | Clothes Washer, Residential | Any | Any | Any |  | QA Checklist | 36 | Eligible building types include residential single-family, double-wide mobile homes, and in-unit multifamily residences as well as multifamily common area laundry. | Yes |  | Eligible building types include residential single-family, double-wide mobile homes, and in-unit multifamily residences as well as multifamily common area laundry. | Text Box | [9 empty] | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP | Inspections | Document the type of residence the unit was installed in (Single Family Home, Multifamily, or Mobile Home) | The building type listed in EECP should match the building type during the inspection |  | 2021-08-04 | Kenny Liljestrom |  | Add | 163
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the Ozone equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-09 | Kenny Liljestrom |  | Add | 12
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the Ozone equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-09 | Kenny Liljestrom |  | Add | 5
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any |  | EECP | 3 | This measure is applicable for hotels/motels, health centers, nursing homes, and correctional facilities. | Yes |  | Building Type | Drop Down List | hotels/motels;health centers;nursing homes;correctional facility;other | [7 empty] | Must not be 'other' | QA Checklist | Use the building type from the EECP enrollment phase to determine if the project is eligible | The building type should only consist of: hotels/motels, health centers, nursing homes, or correctional facility | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 13
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any |  | EECP | 4 | Eligible ozone laundry products must meet the following requirements: • The washing capacity of each washing machine must be rated at 200 pounds or less. • The customer must have a natural gas-fired boiler or natural gas water heater that supplies hot water to the on-premise laundry (OPL) equipment. • The ozone laundry system(s) must be a new purchased product and installed with a new or existing commercial washing machine(s). • The ozone laundry system(s) must transfer ozone into the water with either the venture injection or bubble diffusion process. | Yes | Capacity | Capacity of largest washing machine (lbs) | Numeric Value | [8 empty] | Must be <= 200 | QA Checklist | Use the manufacturer specification sheets or inspection photos to validate the laundry capacity (lbs) of the largest washing machine connected to the Ozone system; the make and model can be used to locate a manufacturer specification sheet where the laundry capacity (lbs) should be listed | The capacity for EACH washing machine should be <= 200 lbs; the total capacity (combined) of all the washing machines does not have a limitation | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Updated Property label name to be more consistent with workpaper requirement | 2021-06-10 | Kenny Liljestrom |  | Add | 41
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any |  | EECP | 5 | Eligible ozone laundry products must meet the following requirements: • The washing capacity of each washing machine must be rated at 200 pounds or less. • The customer must have a natural gas-fired boiler or natural gas water heater that supplies hot water to the on-premise laundry (OPL) equipment. • The ozone laundry system(s) must be a new purchased product and installed with a new or existing commercial washing machine(s). • The ozone laundry system(s) must transfer ozone into the water with either the venture injection or bubble diffusion process. | Yes |  | Is a natural gas-fired boiler or water heater supplying hot water to the laundry equipment? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Locate and photograph the hot water heater supplying the on premise laundry washers; photograph the water heater nameplate to capture the make, model, and input rating (Btu/hr) or photograph the yellow gas piping fueling the water heater | Ensure the water heater previously serving or still connected to the washing machine is served by a natural gas fired water heater | QA Checklist | Use the submitted invoice or installation report to validate the make and model number of the on site water heater is listed and use those data to locate a manufacturer specification sheet | The manufacturer specification sheet should indicate the unit is a natural gas fired water heater | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 91
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any |  | EECP | 6 | - | Yes | LBS | Total washing machine capacity (lbs) | Numeric Value | [9 empty] | QA Checklist | Use the manufacturer specification sheets or inspection photos to validate the laundry capacity (lbs) of all on premise washing machines connected to the Ozone system; the make and model can be used to locate a manufacturer specification sheet where the laundry capacity (lbs) should be listed | The total capacity (combined) of all the washing machines does not have a limitation | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Revise property label to "Total washing machine capacity (lbs)" | 2021-06-10 | Kenny Liljestrom |  | Add | 36
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any |  | EECP | 7 | Eligible ozone laundry products must meet the following requirements: • The washing capacity of each washing machine must be rated at 200 pounds or less. • The customer must have a natural gas-fired boiler or natural gas water heater that supplies hot water to the on-premise laundry (OPL) equipment. • The ozone laundry system(s) must be a new purchased product and installed with a new or existing commercial washing machine(s). • The ozone laundry system(s) must transfer ozone into the water with either the venture injection or bubble diffusion process. | Yes | Market Cost | Market Cost | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | If this is a legacy property, do not include for this program and possibly remove if not configured for others | 2021-06-10 | Kenny Liljestrom |  | Add | 11
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any |  | EECP | 8 | - | Yes | Number of Guest Rooms | Number of Guest Rooms | Numeric Value | [9 empty] | Inspections | Ask the customer for the number of guest rooms at the facility | The value in EECP should be within 5% of the total number of guest rooms indicated by the customer | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | If this is a legacy property, do not include for this program and possibly remove if not configured for others | 2021-06-10 | Kenny Liljestrom |  | Add | 21
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any |  | EECP | 9 | - | Yes | Serial Number | Serial Number | Text Box | [9 empty] | Inspections | Photograph the Ozone equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Collect the equipment invoice for the product and/or installation report with the Ozone equipment serial number | The listed serial number in EECP should match the nameplate | If this is a legacy property, do not include for this program and possibly remove if not configured for others | 2021-06-10 | Kenny Liljestrom |  | Add | 13
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any |  | EECP | 10 | Eligible ozone laundry products must meet the following requirements: • The washing capacity of each washing machine must be rated at 200 pounds or less. • The customer must have a natural gas-fired boiler or natural gas water heater that supplies hot water to the on-premise laundry (OPL) equipment. • The ozone laundry system(s) must be a new purchased product and installed with a new or existing commercial washing machine(s). • The ozone laundry system(s) must transfer ozone into the water with either the venture injection or bubble diffusion process. | Yes | Size | Proc-lbs | Numeric Value | [8 empty] | Must be <= 200 lbs | QA Checklist | Use the manufacturer specification sheets or inspection photos to validate the laundry capacity (lbs) of all on premise washing machines connected to the Ozone system; the make and model can be used to locate a manufacturer specification sheet where the laundry capacity (lbs) should be listed | The total capacity (combined) of all the washing machines does not have a limitation | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Duplicate property of 'Capacity', possibly remove | 2021-06-10 | Kenny Liljestrom |  | Add | 8
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any |  | EECP | 11 | Eligible ozone laundry products must meet the following requirements: • The washing capacity of each washing machine must be rated at 200 pounds or less. • The customer must have a natural gas-fired boiler or natural gas water heater that supplies hot water to the on-premise laundry (OPL) equipment. • The ozone laundry system(s) must be a new purchased product and installed with a new or existing commercial washing machine(s). • The ozone laundry system(s) must transfer ozone into the water with either the venture injection or bubble diffusion process. | Yes |  | New Equipment | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Collect the equipment invoice for the product | The invoice should list the equipment as new (i.e. not used, rebuilt. or leased) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 13
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any |  | EECP | 12 | Eligible ozone laundry products must meet the following requirements: • The washing capacity of each washing machine must be rated at 200 pounds or less. • The customer must have a natural gas-fired boiler or natural gas water heater that supplies hot water to the on-premise laundry (OPL) equipment. • The ozone laundry system(s) must be a new purchased product and installed with a new or existing commercial washing machine(s). • The ozone laundry system(s) must transfer ozone into the water with either the venture injection or bubble diffusion process. | Yes |  | Is the ozone transfer into the water via venturi injection or bubble diffusion? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Ensure specifications indicate what type of injection system is utilized | The ozone system needs to use either a venturi injection or bubble diffusion process to transfer the ozone to the laundry | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 79
1 | SWAP005 | 1 | Ozone Laundry, Commercial | Any | Any | Any |  | EECP | 13 | Laundry systems equipped with tunnel washers are not eligible. | Yes |  | Is the Ozone system installed on a laundry system equipped with a tunnel washer? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | Inspections | Photo of the washing machine | Ensure the washers are not large scale with tunnel washers (like would be found in a commercial laundry service facility) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 80
0 | SWAP006 | 2 | Dishwasher, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 12
0 | SWAP006 | 2 | Dishwasher, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 5
0 | SWAP006 | 2 | Dishwasher, Residential | Any | Any | Any |  | EECP | 3 | This measure is eligible for all residential building types of any vintage that utilize natural gas water heating equipment. | Yes |  | Water heater fuel type | Drop Down List | Gas;Electric; | [7 empty] | Must be 'Gas' | Inspections | Photograph the domestic water heater nameplate to capture the make and model number, or photograph the yellow pipe gas line going into the water heater | The water heater must use natural gas as the fuel source | QA Checklist | Implementer should provide proof of water heater fuel source in an installation report or proof that a natural gas water heater is used to supply the dishwasher | The water heater must use natural gas as the fuel source | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 22
0 | SWAP006 | 2 | Dishwasher, Residential | Any | Any | Any |  | EECP | 4 | Compact residential dishwashers and commercial dishwashers are excluded from this measure. | Yes |  | Dishwasher type | Drop Down List | Standard;Compact;Commercial; | [7 empty] | Must be 'Standard' | QA Checklist | Use the EnergyStar database to determine the Type of the Dishwasher | The Type must be listed on EnergyStar as Standard | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 15
0 | SWAP006 | 2 | Dishwasher, Residential | Any | Any | Any |  | EECP | 5 | The dishwasher must meet ENERGY STAR Program Requirements for Residential Dishwashers (Version 6.0).3 Please note that the offering is more stringent than the ENERGY STAR Most Efficient criteria. | Yes |  | Max. Estimated Annual Energy Use (kWh/yr) | Numeric Value | [8 empty] | Must be <= 199 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) of the Dishwasher | The Annual Energy Use (kWh/yr) must be listed on EnergyStar as <= 199 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 41
0 | SWAP006 | 2 | Dishwasher, Residential | Any | Any | Any |  | EECP | 6 | The dishwasher must meet ENERGY STAR Program Requirements for Residential Dishwashers (Version 6.0).3 Please note that the offering is more stringent than the ENERGY STAR Most Efficient criteria. | Yes |  | Max. Water Consumption (gallons/cycle) | Numeric Value | [8 empty] | Must be <= 3.5 | QA Checklist | Use the EnergyStar database to determine the Water Use (gallons/cycle) of the Dishwasher | The Water Use (gallons/cycle) must be listed on EnergyStar as <= 3.5 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 38
1 | SWAP006 | 3 | Dishwasher, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 12
1 | SWAP006 | 3 | Dishwasher, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 5
1 | SWAP006 | 3 | Dishwasher, Residential | Any | Any | Any |  | EECP | 3 | This measure is eligible for all residential building types of any vintage that utilize natural gas water heating equipment. | Yes |  | Water heater fuel type | Drop Down List | Gas;Electric; | [7 empty] | Must be 'Gas' | Inspections | Photograph the domestic water heater nameplate to capture the make and model number, or photograph the yellow pipe gas line going into the water heater | The water heater must use natural gas as the fuel source | QA Checklist | Implementer should provide proof of water heater fuel source in an installation report or proof that a natural gas water heater is used to supply the dishwasher | The water heater must use natural gas as the fuel source | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 22
1 | SWAP006 | 3 | Dishwasher, Residential | Any | Any | Any |  | EECP | 4 | Compact residential dishwashers and commercial dishwashers are excluded from this measure. | Yes |  | Dishwasher type | Drop Down List | Standard;Compact;Commercial; | [7 empty] | Must be 'Standard' | QA Checklist | Use the EnergyStar database to determine the Type of the Dishwasher | The Type must be listed on EnergyStar as Standard | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 15
1 | SWAP006 | 3 | Dishwasher, Residential | Any | Any | Any |  | EECP | 5 | The dishwasher must meet ENERGY STAR Program Requirements for Residential Dishwashers (Version 6.0).3 Please note that the offering is more stringent than the ENERGY STAR Most Efficient criteria. | Yes |  | Max. Estimated Annual Energy Use (kWh/yr) | Numeric Value | [8 empty] | Must be <= 199 | QA Checklist | Use the EnergyStar database to determine the Annual Energy Use (kWh/yr) of the Dishwasher | The Annual Energy Use (kWh/yr) must be listed on EnergyStar as <= 199 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 41
1 | SWAP006 | 3 | Dishwasher, Residential | Any | Any | Any |  | EECP | 6 | The dishwasher must meet ENERGY STAR Program Requirements for Residential Dishwashers (Version 6.0).3 Please note that the offering is more stringent than the ENERGY STAR Most Efficient criteria. | Yes |  | Max. Water Consumption (gallons/cycle) | Numeric Value | [8 empty] | Must be <= 3.5 | QA Checklist | Use the EnergyStar database to determine the Water Use (gallons/cycle) of the Dishwasher | The Water Use (gallons/cycle) must be listed on EnergyStar as <= 3.5 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-04 | Kenny Liljestrom |  | Add | 38
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed |  | EECP | 0 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 7
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed |  | EECP | 5 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 12
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | Any |  | EECP | 10 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer in EECP should match what is listed in the invoice or installation report |  | 2022-06-10 | Kenny Liljestrom |  | Add | 12
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | Any |  | EECP | 15 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number in EECP should match what is listed in the invoice or installation report |  | 2022-06-10 | Kenny Liljestrom |  | Add | 5
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed |  | EECP | 20 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number in EECP should match what is listed in the invoice or installation report |  | 2022-06-10 | Kenny Liljestrom |  |  | 13
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed |  | EECP | 25 | The following products are not eligible: packaged terminal air conditioners (PTACs), portable air conditioners, room air conditioner models with electric resistance heat as the primary heat source, and dehumidifiers. | Yes | Equipment Type | Equipment type | Drop Down List | Window AC;Through the wall AC;Other; |  | Not Equal | Other |  |  |  |  | Must not be Other | QA Checklist | Using the make and model, determine the equipment type from the EnergyStar database | The equipment types on EnergyStar should not include any of the following: • packaged terminal air conditioners (PTACs) • portable air conditioners • room air conditioner models with electric resistance heat as the primary heat source • dehumidifiers | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-06-10 | Kenny Liljestrom |  | Add | 14
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed |  | EECP | 30 | The room air conditioner must meet or exceed the current ENERGY STAR efficiency levels and carry the ENERGY STAR qualification, as per specification in the Measure Case Description. | Yes | Energy Star ID | Energy Star unique ID | Text Box | [9 empty] | QA Checklist | Review the EnergyStar database to check for the make and model of the installed equipment | The equipment in EECP should be locatable on the EnergyStar database as being a certified product and should match the make and model of the equipment | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Can we have this qualify via Energy Star within CPSS and not entered yes/no by the 3P? | 2022-06-10 | Kenny Liljestrom |  | Add | 21
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed |  | EECP | 35 | E-5152 Data Collection Requirements | Yes | Capacity | Cooling Capacity (BTU/h) | Numeric Value |  |  |  |  | General | 0 |  | 0 |  | Inspections | Photograph the equipment nameplate to capture the cooling capacity (Btu/hr) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the EnergyStar database to check for the capacity (Btu/hr) of the installed equipment | The equipment in EECP should be locatable on the EnergyStar database as being a certified product and should have a capacity (Btu/hr) that matches EECP |  | 2022-06-10 | Kenny Liljestrom |  |  | 24
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed |  | EECP | 40 | E-5152 Data Collection Requirements | Yes | CEER | Combined Energy Efficiency Ratio (CEER) | Numeric Value |  |  |  |  | General | 0 |  | 1 |  | Inspections | Photograph the equipment nameplate to capture the Combined Energy Efficinecy Ratio (CEER) value | The listed CEER value in EECP should match the nameplate | QA Checklist | Review the EnergyStar database to check for the Combined Energy Efficinecy Ratio (CEER) value of the installed equipment | The equipment in EECP should be locatable on the EnergyStar database as being a certified product and should have a CEER value that matches EECP |  | 2022-06-10 | Kenny Liljestrom |  |  | 39
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed |  | EECP | 190 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value |  |  |  |  | General |  |  | 0 |  | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 8
0 | SWAP007 | 1 | Room Air Conditioner, Residential | Any | Any | UpDeemed |  | EECP | 195 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 15
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the modulating valve nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-05 | Kenny Liljestrom |  | Add | 12
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the modulating valve nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-05 | Kenny Liljestrom |  | Add | 5
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any |  | EECP | 3 | This measure is applicable for all new and existing commercial or multifamily buildings of all vintages. For the commercial sector, this measure will apply to the following building types: general commercial, hotels, motels, small retail, and nursing homes. | Yes |  | Building type | Drop Down List | Multifamily;General commercial;Hotel;Motel;Small retail;Nursing home; | [8 empty] | Inspections | Document the type of building the unit was installed in (Multifamily, General commercial, Hotel, Motel, Small retail, or Nursing home) | The building type listed in EECP should match the building type during the inspection | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 13
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any |  | EECP | 4 | A professional installer will be required for all installations of this product as the inlet natural gas line will have to be removed and reattached during installation. | Yes |  | Was a professional installer used to remove and reattach the gas line? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Request the name of the installer for the gas valve and or contractor license number | Use the installer or contractor license number to determine if the installer is qualified using the Contractor License Board verification website (https://www.cslb.ca.gov/OnlineServices/CheckLicenseII/checklicense.aspx) | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 70
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any |  | EECP | 5 | All applicants must have their dryers on site | Yes | Dryer OnSite | Are the dryers on the site premise? | Drop Down List | Yes;No | [7 empty] | Must be Yes | Inspections | Determine if the dryers are on the site premise for the applicant or at a remote site | The dryers need to be on the same premise as the customers address | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-08-05 | Kenny Liljestrom |  | Add | 35
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any |  | EECP | 6 | A dryer that makes use of a common or dedicated steam system is not eligible. | Yes |  | Does the dryer make use of a common dedicated steam system? | Drop Down List | Yes;No | [7 empty] | Must be No | Inspections | Ask the customer if there is a dedicated steam system onsite to serve the laundry facility; Some dryers are capable of using both steam and natural gas | Document the customers response, there should be no steam serving the dryers | QA Checklist | Use the make and model number of the dryers to determine if that unit is capable of operating with steam; If the dryer is capable of using steam, request via an installation report whether or not the dryer is served by a dedicated steam system | The unit should not be able to operate with steam, but if it can, there should be no steam system onsite or at the least not serving the laundry dryers | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 59
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any |  | EECP | 7 | The natural gas dryer must not be modified by any technology that would reduce the natural gas consumption beyond the manufacturer specifications. | Yes |  | Is the max flow/capacity of the modulating valve greater than or equal to that of the dryer? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 92
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any |  | EECP | 8 | This measure is not eligible for dryers with a capacity greater than 200 lbs or less than 20 lbs. For capacities outside of this range, a custom measure type is recommended. | Yes |  | Capacity of largest dryer (lbs) | Numeric Value | [8 empty] | Must be > 20 and <= 200 | Inspections | Photograph the nameplate on the dryer | Sometimes the capacity is listed on the nameplate of the dryer; if not listed, supply the make and model information to the processor to verify the capacity of the dryer | QA Checklist | Use either the make and model of the dryer to locate the specification sheet and determine the capacity of the unit; or request via an installation report photographs of the dryer nameplate and/or the dryer specification sheet to validate the capacity of the largest dryer | Using either method, determine if the dryer has a maximum capacity (lbs) of > 20 lbs and <= 200 lbs | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 31
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any |  | EECP | 9 | This measure is not eligible for dryers with a capacity greater than 200 lbs or less than 20 lbs. For capacities outside of this range, a custom measure type is recommended. | Yes |  | Total dryer capacity affected (lbs) | Numeric Value | [9 empty] | Inspections | Photograph the nameplates of all the dryers with gas modulating valves | Sometimes the capacity is listed on the nameplate of the dryer; if not listed, supply the make and model information to the processor to verify the capacity of the dryers | QA Checklist | Use either the make and model of the dryer to locate the specification sheet and determine the capacity of the unit; or request via an installation report photographs of the dryer nameplate and/or the dryer specification sheet to validate the capacity of the largest dryer | There are no pass or fail criteria for the property just good information to collect | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 35
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any |  | QA Checklist | 10 | Natural gas must be supplied by a California utility. | Yes |  | Natural gas must be supplied by a California utility. | Text Box | [9 empty] | QA Checklist | Use EECP to determine if the customer purchases natural gas from SDG&E | The customer must be an active account holder and purchase natural gas from SDG&E | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 53
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any |  | EECP | 11 |  | Yes | Natural Gas | Does the existing dryer use natural gas? | Drop Down List | Yes;No | [8 empty] | - | - | - | - | - | - | Engineering request to expire | 2022-01-24 | Kenny Liljestrom |  |  | 40
1 | SWAP012 | 1 | Gas Dryer Modulating Valve, Commercial and Multifamily | Any | Any | Any |  | EECP | 12 |  | Yes | Size | Drum Capacity (lbs) | Numeric Value | [9 empty] | - | - | - | - | - | - | Engineering request to expire | 2022-01-24 | Kenny Liljestrom |  |  | 19
0 | SWBE001 | 2 | Greenhouse Heat Curtain | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 12
0 | SWBE001 | 2 | Greenhouse Heat Curtain | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 5
0 | SWBE001 | 2 | Greenhouse Heat Curtain | Any | Any | Any |  | EECP | 3 | This measure is applicable for agricultural or commercial greenhouse of any vintage for the primary purpose of the production of nursery products, horticultural specialties, or ornamental products | Yes |  | Greenhouse facility specialty | Text Box | [9 empty] | Inspections | Make note of the type of agriculture taking place at the facility | The description in EECP should match the agriculture type of the facility | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 29
0 | SWBE001 | 2 | Greenhouse Heat Curtain | Any | Any | Any |  | QA Checklist | 4 | Eligible products must meet the following requirements: Must be a single-layer interior curtain installed for heat retention. Must be installed in a gas-heated greenhouse facility. The facility must be a greenhouse with the primary purpose of agricultural use. The heat curtain must be a new curtain installed where none previously existed or a new curtain that is replacing an existing curtain that is no longer functional. The heat curtain must be installed above the conditioned area where the gas heat source provides hot air to plant and seed species. The heat curtain must have a natural gas savings rating that meets or exceeds 40%. The heat curtain must have a warranty/product life of five years. The installation must allow the curtain to be automatically or manually moved into place. | Yes |  | The greenhouse curtain must be a single layer plastic curtain | None | [9 empty] | Inspections | Inspect the greenhouse curtain to check for the number of layers of plastic | The curtain should contain only a single layer of material (i.e. not double and triple stacked curtains | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 61
0 | SWBE001 | 2 | Greenhouse Heat Curtain | Any | Any | Any |  | EECP | 5 | Eligible products must meet the following requirements: Must be a single-layer interior curtain installed for heat retention. Must be installed in a gas-heated greenhouse facility. The facility must be a greenhouse with the primary purpose of agricultural use. The heat curtain must be a new curtain installed where none previously existed or a new curtain that is replacing an existing curtain that is no longer functional. The heat curtain must be installed above the conditioned area where the gas heat source provides hot air to plant and seed species. The heat curtain must have a natural gas savings rating that meets or exceeds 40%. The heat curtain must have a warranty/product life of five years. The installation must allow the curtain to be automatically or manually moved into place. | Yes |  | Greenhouse is heated by natural gas (not propane)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | Inspect the gas lines going to the greenhouse heaters | The heaters should be fueled by natural gas; there should not be propane tanks connected to the gas lines fueling the heaters | QA Checklist | Check the customer usage data or history to determine if the facility uses natural gas | The facility must consume natural gas to qualify for this measure |  | 2022-02-28 | Kenny Liljestrom |  |  | 50
0 | SWBE001 | 2 | Greenhouse Heat Curtain | Any | Any | Any |  | EECP | 6 | Eligible products must meet the following requirements: Must be a single-layer interior curtain installed for heat retention. Must be installed in a gas-heated greenhouse facility. The facility must be a greenhouse with the primary purpose of agricultural use. The heat curtain must be a new curtain installed where none previously existed or a new curtain that is replacing an existing curtain that is no longer functional. The heat curtain must be installed above the conditioned area where the gas heat source provides hot air to plant and seed species. The heat curtain must have a natural gas savings rating that meets or exceeds 40%. The heat curtain must have a warranty/product life of five years. The installation must allow the curtain to be automatically or manually moved into place. | Yes |  | Heat curtain gas savings rating (%) | Numeric Value | [8 empty] | Must be >= 40% | QA Checklist | Review the submitted specification sheet and determine the gas or energy savings rating (%) of the product installed | The energy or gas savings rating must be >= 40% as indicated in the specification sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 35
0 | SWBE001 | 2 | Greenhouse Heat Curtain | Any | Any | Any |  | QA Checklist | 7 | Eligible products must meet the following requirements: Must be a single-layer interior curtain installed for heat retention. Must be installed in a gas-heated greenhouse facility. The facility must be a greenhouse with the primary purpose of agricultural use. The heat curtain must be a new curtain installed where none previously existed or a new curtain that is replacing an existing curtain that is no longer functional. The heat curtain must be installed above the conditioned area where the gas heat source provides hot air to plant and seed species. The heat curtain must have a natural gas savings rating that meets or exceeds 40%. The heat curtain must have a warranty/product life of five years. The installation must allow the curtain to be automatically or manually moved into place. | Yes |  | Product has a warranty >= 5 years | None | [9 empty] | QA Checklist | Review the manufacturer specification sheet to find the warranty information | The product should be covered by at minimum a 5-year warranty | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 33
0 | SWBE001 | 2 | Greenhouse Heat Curtain | Any | Any | Any |  | EECP | 8 | The square footage of the new heat curtain cannot exceed the square footage of the greenhouse floor. Additionally, any overhang and overlap of curtain material cannot be included in the square footage calculation. | Yes |  | Quantity (sq ft) of heat curtain does not include overlap or exceed sq ft of the floor? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | Inspect the installed heat curtain | The curtain should not be draped over support structures, nor should the estimated square footage (quantity in EECP) be greater than the floor area of the greenhouse; best estimates are sufficient for the square footage determination | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 87
1 | SWBE002 | 2 | Greenhouse Infrared Film | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 12
1 | SWBE002 | 2 | Greenhouse Infrared Film | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 5
1 | SWBE002 | 2 | Greenhouse Infrared Film | Any | Any | Any |  | EECP | 3 | This measure is applicable for agricultural or commercial greenhouse of any vintage for the primary purpose of the production of nursery products, horticultural specialties, or ornamental products | Yes |  | Greenhouse facility specialty | Text Box | [9 empty] | Inspections | Make note of the type of agriculture taking place at the facility | The description in EECP should match the agriculture type of the facility | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 29
1 | SWBE002 | 2 | Greenhouse Infrared Film | Any | Any | Any |  | EECP | 4 | The installation of infrared (IR) film must meet the following requirements: The IR film must be installed in a gas-heated greenhouse facility. The heating equipment type (building HVAC) must be specified in the implementation of the measure. The facility must be a greenhouse with the primary purpose of agricultural use. The film must be infrared, anti-condensate, polyethylene plastic with a minimum thickness of six thousandths of an inch. The IR film shall not be installed on the walls of the greenhouse. | Yes |  | Greenhouse is heated by natural gas (not propane)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | Inspect the gas lines going to the greenhouse heaters | The heaters should be fueled by natural gas; there should not be propane tanks connected to the gas lines fueling the heaters | QA Checklist | Check the customer usage data or history to determine if the facility uses natural gas | The facility must consume natural gas to qualify for this measure |  | 2022-02-28 | Kenny Liljestrom |  |  | 50
1 | SWBE002 | 2 | Greenhouse Infrared Film | Any | Any | Any |  | EECP | 5 | The installation of infrared (IR) film must meet the following requirements: The IR film must be installed in a gas-heated greenhouse facility. The heating equipment type (building HVAC) must be specified in the implementation of the measure. The facility must be a greenhouse with the primary purpose of agricultural use. The film must be infrared, anti-condensate, polyethylene plastic with a minimum thickness of six thousandths of an inch. The IR film shall not be installed on the walls of the greenhouse. | Yes |  | Gas heating equipment type | Drop Down List | aGF;aRH; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-28 | Kenny Liljestrom |  |  | 26
1 | SWBE002 | 2 | Greenhouse Infrared Film | Any | Any | Any |  | QA Checklist | 6 | The installation of infrared (IR) film must meet the following requirements: The IR film must be installed in a gas-heated greenhouse facility. The heating equipment type (building HVAC) must be specified in the implementation of the measure. The facility must be a greenhouse with the primary purpose of agricultural use. The film must be infrared, anti-condensate, polyethylene plastic with a minimum thickness of six thousandths of an inch. The IR film shall not be installed on the walls of the greenhouse. | Yes |  | The IR film must be infrared, anti-condensate, polyethylene plastic with a minimum thickness of six thousandths of an inch. | None | [9 empty] | QA Checklist | Use the submitted manufacturer specification sheet to ensure the item qualifies based on the following criteria: infrared, anti-condensate, polyethylene plastic with a minimum thickness of six thousandths of an inch | The IR Film must meet these criteria to qualify: - It must be infrared type film - the film must be anti-condensate - the film must be made of polyethylene plastic - the film thickness must be >= 6/1000 (0.006-inches) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 123
1 | SWBE002 | 2 | Greenhouse Infrared Film | Any | Any | Any |  | EECP | 7 | The installation of infrared (IR) film must meet the following requirements: The IR film must be installed in a gas-heated greenhouse facility. The heating equipment type (building HVAC) must be specified in the implementation of the measure. The facility must be a greenhouse with the primary purpose of agricultural use. The film must be infrared, anti-condensate, polyethylene plastic with a minimum thickness of six thousandths of an inch. The IR film shall not be installed on the walls of the greenhouse. | Yes |  | IR Film only installed on the roof (not on the walls)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | Inspect the IR film installation to check the walls and roof | The IR film is only allowed to be installed on the roof to qualify; if IR film is on the walls, the claimed quantity in EECP should align with, using your best estimates, to the square footage of the roof alone | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-28 | Kenny Liljestrom |  |  | 54
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the Anti-Sweat Heater Control box nameplate to capture the manufacturer; the box may be located on the interior of the case or walk-in near the junction box | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-10 | Kenny Liljestrom |  | Add | 12
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the Anti-Sweat Heater Control box nameplate to capture the model number; the box may be located on the interior of the case or walk-in near the junction box | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-10 | Kenny Liljestrom |  | Add | 5
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | Any | Any | Any |  | EECP | 3 | The program should collect and verify the vintage of the building and the refrigeration multiplex system. | Yes | Date of Construction | Date of Construction | Date | [9 empty] | QA Checklist | There is no pass or fail criteria for this property, it is recommended for data collection purposes | There is no pass or fail criteria for this property, it is recommended for data collection purposes | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | This would be in the property information on the application | 2021-06-10 | Kenny Liljestrom |  | Add | 20
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | Any | Any | Any |  | EECP | 4 | The program should collect and verify the vintage of the building and the refrigeration multiplex system. The offerings are ineligible for multiplex systems majorly upgraded or installed after July 1, 2014 since the Title-24 code mandates the floating controls since July 1, 2014. | Yes | Date of Installation | Date of installation or major upgrade to refrigeration multiplex system | Date | [8 empty] | Must be before 7/1/2014 | Inspections | Photograph the of refrigeration system (chiller) nameplate to capture the serial number and, more preferrable, the date of manufacture | Validate the serial number or date of manufacture is consistent with installations dates listed in EECP | QA Checklist | The implementer can verify this information by providing the serial number or construction date of the refrigeration system | The serial number can be cross referenced with the manufacturer or online lookup tables if not provided directly on the nameplate of the system; the system must be older than 7/1/2014 to qualify |  | 2021-06-10 | Kenny Liljestrom |  | Add | 71
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | A | Any | Any |  | EECP | 5 | The unit energy savings (UES) of anti-sweat heater (ASH) controls are based upon the installation of controllers on existing ASHs on low-temperature (case temperature below 32 °F) and medium-temperature case temperature (at or above 32 °F) display cases. | Yes | Temp Below 32F | Is the case temperature below 32F? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Check case temperatures with thermometers installed in the cases or with a handheld thermocouple | The case temperature should be below 32F (or a freezer) | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Can be removed; data in measure description | 2021-06-10 | Kenny Liljestrom |  | Add | 34
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | B | Any | Any |  | EECP | 6 | The unit energy savings (UES) of anti-sweat heater (ASH) controls are based upon the installation of controllers on existing ASHs on low-temperature (case temperature below 32 °F) and medium-temperature case temperature (at or above 32 °F) display cases. | Yes |  | Is the case temperature above 32F? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Check case temperatures with thermometers installed in the cases or with a handheld thermocouple | The case temperature should be above 32F (or a refrigerator) | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Can be removed; data in measure description | 2021-08-03 | Kenny Liljestrom |  | Add | 34
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | Any | Any | Any |  | EECP | 7 | To qualify, the display case must be equipped with humidity-sensing controls that reduce the amount of power supplied to the heaters as the store dew point (DP) temperature decreases.. | Yes | Humidity Sensing Controls | Display case equipped with humidity-sensing controls based on the store dew point temperature? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Update property label so it makes sense | 2021-06-10 | Kenny Liljestrom |  | Add | 94
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | Any | Any | Any |  | EECP | 8 | Typically, power reduction occurs when relative humidity levels reach 55% and lower. Power reduction should decrease by at least 2% for every percentage the humidity falls below 55%. | Yes | Power Reduction | Does power reduction decrease by at least 2% for every percentage the humidity falls below 55%? | Drop Down List | Yes;No; | [8 empty] | QA Checklist | Using the manufacturer spec sheet, identify the controls summary information to check for power reduction based on humidity decrease; if not, the following criteria must be met | The controls must decrease power by 2% for every humidity percentage decrease below 55%; if not, the following criteria must be met | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Validation criteria needs to be updated | 2021-06-10 | Kenny Liljestrom |  | Add | 95
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | Any | Any | Any |  | EECP | 9 | Equivalent technologies that can reduce or turn off ASHs based on the amount of condensation formed on the inner glass pane may also qualify. | Yes |  | If humidity is not monitored, ASH controls turn off based on the condensation formed on inner glass? | Drop Down List | Yes;No;N/A; | [7 empty] | If Power Reduction is 'No' then Must be 'Yes' | QA Checklist | Using the manufacturer spec sheet, identify the controls summary information to check for shut off controls based on condensation formed on the inner glass | If the above criteria passed, disregard the measure property; the manufacturer spec sheet should list the controls as having the ability to shut off the anti-sweat heating elements based on the amount of condensation formed on the glass door | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-03 | Kenny Liljestrom |  | Add | 100
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | B | Any | Any |  | EECP | 10 | This measure cannot be used in conjunction with the new refrigeration display case with doors. This measure cannot be used in conjunction with the special doors with low/no anti-sweat heat on low-temperature display case. | Yes | Doors Anti Sweat Heat Controls | Do the installed doors have low/no anti-sweat heat controls in conjunction with the installed controls? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-06-10 | Kenny Liljestrom |  | Add | 103
0 | SWCR001 | 1 | Anti-Sweat Heater Controls | Any | Any | Any |  | EECP | 11 | This measure cannot be used in conjunction with the new refrigeration display case with doors. | Yes | Display Case Doors New | Are the refrigeration display case doors new? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | Inspections | Photos of case doors, look for anything indicating doors are not new | The doors must not looked like they have been replaced within the last couple months | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 45
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the Anti-Sweat Heater Control box nameplate to capture the manufacturer; the box may be located on the interior of the case or walk-in near the junction box | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-06 | Kenny Liljestrom | Effective Date 1/1/2022 | Add | 12
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the Anti-Sweat Heater Control box nameplate to capture the model number; the box may be located on the interior of the case or walk-in near the junction box | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-06 | Kenny Liljestrom | Effective Date 1/1/2022 | Add | 5
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any |  | QA Checklist | 3 | The program should collect and verify the vintage of the building and the refrigeration multiplex system. | No | Date of Construction | Date of Construction | Date | [9 empty] | EECP | There is no pass or fail criteria for this property, it is recommended for data collection purposes | There is no pass or fail criteria for this property, it is recommended for data collection purposes | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-08-06 | Kenny Liljestrom | Property removed from EECP, put on QA Checklist instead since this data is captured at the enrollment level | Add | 20
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any |  | QA Checklist | 4 | The program should collect and verify the vintage of the building and the refrigeration multiplex system. | Yes | Date of Construction | Date of Construction | Date | [9 empty] | QA Checklist | There is no pass or fail criteria for this property, it is recommended for data collection purposes | There is no pass or fail criteria for this property, it is recommended for data collection purposes | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Updated property source to QA Checklist from EECP; Building vintage is captured at the enrollment level | 2022-01-04 | Kenny Liljestrom |  |  | 20
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any |  | EECP | 5 | The program should collect and verify the vintage of the building and the refrigeration multiplex system. The offerings are ineligible for multiplex systems majorly upgraded or installed after July 1, 2014 since the Title-24 code mandates the floating controls since July 1, 2014. | Yes | Date of Installation | Date of installation or major upgrade to refrigeration multiplex system | Date | [8 empty] | Must be before 7/1/2014 | Inspections | Photograph the of refrigeration system (chiller) nameplate to capture the serial number and, more preferrable, the date of manufacture | Validate the serial number or date of manufacture is consistent with installations dates listed in EECP | QA Checklist | The implementer can verify this information by providing the serial number or construction date of the refrigeration system | The serial number can be cross referenced with the manufacturer or online lookup tables if not provided directly on the nameplate of the system; the system must be older than 7/1/2014 to qualify |  | 2021-08-06 | Kenny Liljestrom | Effective Date 1/1/2022 | Add | 71
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any |  | EECP | 6 | To qualify, the display case must be equipped with humidity-sensing controls that reduce the amount of power supplied to the heaters as the store dew point (DP) temperature decreases.. | Yes | Humidity Sensing Controls | Display case equipped with humidity-sensing controls based on the store dew point temperature? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Update property label so it makes sense | 2021-08-06 | Kenny Liljestrom | Effective Date 1/1/2022 | Add | 94
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any |  | EECP | 7 | Typically, power reduction occurs when relative humidity levels reach 55% and lower. Power reduction should decrease by at least 2% for every percentage the humidity falls below 55%. | Yes | Power Reduction | Does power reduction decrease by at least 2% for every percentage the humidity falls below 55%? | Drop Down List | Yes;No; | [8 empty] | QA Checklist | Using the manufacturer spec sheet, identify the controls summary information to check for power reduction based on humidity decrease; if not, the following criteria must be met | The controls must decrease power by 2% for every humidity percentage decrease below 55%; if not, the following criteria must be met | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Validation criteria needs to be updated | 2021-08-06 | Kenny Liljestrom | Effective Date 1/1/2022 | Add | 95
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any |  | EECP | 8 | Equivalent technologies that can reduce or turn off ASHs based on the amount of condensation formed on the inner glass pane may also qualify. | Yes | ASH Controls | If humidity is not monitored, ASH controls turn off based on the condensation formed on inner glass? | Drop Down List | Yes;No;N/A; | [7 empty] | If Power Reduction is 'No' then Must be 'Yes' | QA Checklist | Using the manufacturer spec sheet, identify the controls summary information to check for shut off controls based on condensation formed on the inner glass | If the above criteria passed, disregard the measure property; the manufacturer spec sheet should list the controls as having the ability to shut off the anti-sweat heating elements based on the amount of condensation formed on the glass door | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom | Effective Date 1/1/2022 | Add | 100
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | B | Any | Any |  | EECP | 9 | This measure cannot be used in conjunction with the new refrigeration display case with doors. This measure cannot be used in conjunction with the special doors with low/no anti-sweat heat on low-temperature display case. | No | Doors Anti Sweat Heat Controls | Do the installed doors have low/no anti-sweat heat controls in conjunction with the installed controls? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-08-06 | Kenny Liljestrom | Property updated to QA checklist in order to place a level of trust with the implementers since this is difficult to near impossible to verify | Add | 103
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | B | Any | Any |  | QA Checklist | 9 | This measure cannot be used in conjunction with the new refrigeration display case with doors. This measure cannot be used in conjunction with the special doors with low/no anti-sweat heat on low-temperature display case. | Yes | Doors Anti Sweat Heat Controls | Do the installed doors have low/no anti-sweat heat controls in conjunction with the installed controls? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-08-06 | Kenny Liljestrom | Effective Date 1/1/2022 | Add | 103
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any |  | EECP | 11 | This measure cannot be used in conjunction with the new refrigeration display case with doors. | Yes | Display Case Doors New | Are the refrigeration display case doors new? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | Inspections | Photos of case doors, look for anything indicating doors are not new | The doors must not looked like they have been replaced within the last couple months | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom | Effective Date 1/1/2022 | Add | 45
1 | SWCR001 | 2 | Anti-Sweat Heater Controls | Any | Any | Any |  | EECP | 12 | This measure cannot be used in conjunction with the new refrigeration display case with doors. | Yes | Temp Below 32F | Is the case temperature below 32F? | Drop Down List | Yes;No | [8 empty] | - | - | - | - | - | - | Engineering request to expire | 2022-01-24 | Kenny Liljestrom |  |  | 34
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-03 | Kenny Liljestrom |  | Add | 12
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-03 | Kenny Liljestrom |  | Add | 5
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any |  | EECP | 3 | Preponderance of evidence (POE) must be documented including: Customer/site information, specifications of existing equipment, proof the existing fan motor is still operating as intended, existing fan motor nameplate data with manufacturer date to confirm RUL, Replacement Motor nameplate information, if the equipment was replaced as a direct result of recommendations provided by the PA. | Yes | POE Docs | Has all the preponderance of evidence required by the workpaper been uploaded in EECP? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Check EECP for any POE related documents | Preponderance of evidence (POE) must be documented including: • Customer/site information, specifications of existing equipment • proof the existing fan motor is still operating as intended • existing fan motor nameplate data with manufacturer date to confirm RUL • Replacement Motor nameplate information • if the equipment was replaced as a direct result of recommendations provided by the PA | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 86
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any |  | EECP | 4 | This measure cannot be used in conjunction with the following measures: SWAP011 Vending and Beverage Merchandise Controller SWCR002 Low-Temperature Display Case Doors With No Anti-Sweat Heaters SWCR018 Reach-In Refrigerator or Freezer, Commercial SWCR019 Low-Temperature Coffin To Reach-In Display Case Conversion SWCR021 Medium or Low-Temperature Display Case With Doors SWCR020 Medium-Temperature Open Display Case Retrofit | Yes |  | Has this measure been combined with another refrigeration measure? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | QA Checklist | Check the enrollment package or installation report for any other refrigeration measures | This measure cannot be used in conjunction with the following measures: SWAP011 Vending and Beverage Merchandise Controller SWCR002 Low-Temperature Display Case Doors With No Anti-Sweat Heaters SWCR018 Reach-In Refrigerator or Freezer, Commercial SWCR019 Low-Temperature Coffin To Reach-In Display Case Conversion SWCR021 Medium or Low-Temperature Display Case With Doors SWCR020 Medium-Temperature Open Display Case Retrofit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 66
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any |  | EECP | 5 | This measure is applicable in conditioned spaces in any existing commercial building type of any vintage. | Yes |  | Is the building an existing commercial building? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | While on site, indicate whether or not the building is new (built within the last year) or existing | The building needs to be existing | QA Checklist | Use EECP to check for the service length of the site address | The site address should have at least one-year of continued service form SDG&E | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 48
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any |  | QA Checklist | 6 | The motor is installed as an evaporator fan motor in a refrigerated display case | Yes |  | Is the motor installed on a refrigerated display case? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | Observe the equipment where the motor was installed | The equipment was installed on a refrigerated display case | QA Checklist | Photographs of the motor and display case can be used to show what the motor was installed in | The motor must be installed in a refrigerated display case | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 54
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any |  | EECP | 7 | Program implementers are encouraged to collect data on motor products installed under the rebate program, such as the type of display case receiving a new motor, motor size, motor cost, and labor cost. | Yes | Fridge Type | Type of refrigerated display case the motor is being installed on | Drop Down List | Open Vertical;Vertical with Doors;Horizontal;Horizontal with Doors;Coffin;Island;Counter;Other; | [8 empty] | Inspections | Observe the case type where the motor is installed; There are several case types including Open Vertical; Vertical with Doors; Horizontal; Horizontal with Doors; Coffin; Island; Counter; Other; | The case type must match the type listed in EECP | QA Checklist | Use the installation report to identify the case type the motor was installed in | There are no validation criteria other than trying to match the type of case to what is listed in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 65
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any |  | QA Checklist | 8 | The installed motor is a permanent magnet electronically commutated motor (ECM) or permanent magnet synchronous AC (PMS) motor/fan. | Yes |  | Installed an electronically commutated motor (ECM) or permanent magnet synchronous (PMS) motor/fan? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice, installation report, or manufacturer spec sheet to validate the motor type is listed | The motor type listed in EECP should match what is listed in the invoice, installation report, or manufacturer spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 99
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any |  | EECP | 9 | The motor must be described as a low‐power or high efficiency model by the manufacturer | Yes | Motor Model | Does the manufacturer describe the motor as a low-power or high efficiency model? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted manufacturer spec sheet to validate if the motor is described as a low‐power or high efficiency model by the manufacturer | The motor must be described as a low‐power or high efficiency model by the manufacturer | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 81
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any |  | EECP | 10 | The new motor is the available product most closely matched to the original motor's speed and shaft output power (equivalent size) | Yes | Match Output power | Is the new motor closely matched to the original motor's speed and shaft output power? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-10 | Kenny Liljestrom |  | Add | 86
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any |  | EECP | 11 | Program implementers are encouraged to collect data on motor products installed under the rebate program, such as the type of display case receiving a new motor, motor size, motor cost, and labor cost. | Yes | Motor Size | Replacement motor size (W) | Numeric Value | [9 empty] | QA Checklist | Use the submitted manufacturer spec sheet to validate the motor power (W) | The value in EECP should match what is listed in the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 26
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any |  | EECP | 12 | Due to limited quantitative results in studies pertaining to refrigerated display cases on the market spread of motor efficiency within rather than across motor types (and motor size classes), program implementers are also encouraged to collect data on motor type and motor efficiency ratings that could be used in future programs to specify a high‐efficiency level for each motor type. | Yes | Motor Efficiency | Replacement motor efficiency (%) | Numeric Value | [9 empty] | QA Checklist | Use the submitted manufacturer spec sheet to validate the motor efficiency (%) | The value in EECP should match what is listed in the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 32
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any |  | EECP | 13 | Program implementers are encouraged to collect data on motor products installed under the rebate program, such as the type of display case receiving a new motor, motor size, motor cost, and labor cost. | Yes | Material Cost | Material cost for replacement motor | Numeric Value | [9 empty] | QA Checklist | Use the submitted invoice to identify the material cost for the motor | The value in EECP should match what is listed in the invoice | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 35
0 | SWCR003 | 1 | ECM Retrofit for a Refrigerated Display Case | Any | Any | Any |  | EECP | 14 | Program implementers are encouraged to collect data on motor products installed under the rebate program, such as the type of display case receiving a new motor, motor size, motor cost, and labor cost. | Yes | Labor Cost | Labor cost for replacement motor | Numeric Value | [9 empty] | QA Checklist | Use the submitted invoice to identify the labor cost for the motor | The value in EECP should match what is listed in the invoice | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 32
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 12
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 5
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any |  | EECP | 3 | Preponderance of evidence (POE) must be documented including: Customer/site information, specifications of existing equipment, proof the existing fan motor is still operating as intended, existing fan motor nameplate data with manufacturer date to confirm RUL, Replacement Motor nameplate information, if the equipment was replaced as a direct result of recommendations provided by the PA. | Yes | POE Docs | Has all the preponderance of evidence required by the workpaper been uploaded in EECP? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Check EECP for any POE related documents | Preponderance of evidence (POE) must be documented including: • Customer/site information, specifications of existing equipment • proof the existing fan motor is still operating as intended • existing fan motor nameplate data with manufacturer date to confirm RUL • Replacement Motor nameplate information, if the equipment was replaced as a direct result of recommendations provided by the PA | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 86
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any |  | EECP | 4 | Pre-inspection of existing equipment is required. | Yes | Site Pre-Inspection | Has a site Pre-Inspection been completed and documentation uploaded in EECP? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | Check EECP documents for any pre-inspection reports | There must be a pre-inspection for this measure to qualify | QA Checklist | Check EECP documents for any pre-inspection reports | There must be a pre-inspection for this measure to qualify |  | 2021-06-10 | Kenny Liljestrom |  | Add | 76
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any |  | EECP | 5 | The existing motor system must be fully functional with no signs of replacement in the 12 months following the project application date. | Yes |  | Existing motor was fully functional with no sign of replacement in 12 months from project app. date? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-04-12 | Kenny Liljestrom |  | Add | 100
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any |  | EECP | 7 | This measure is applicable in any existing commercial building type 2008 and older. This is based on the assumption that walk-in equipment is at least as new as the building. | Yes | Date Installed | When was the walk-in installed in the building? | Date | [8 empty] | Must be before 1/1/2009 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Property validation needs to be configured | 2021-08-06 | Kenny Liljestrom |  | Add | 47
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any |  | QA Checklist | 8 | This measure cannot be used in conjunction with the evaporative fan controller for walk-in coolers and freezers. | Yes |  | Measure combined with evaporative fan controller for walk-in coolers and/or freezers? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | QA Checklist | Using the measure report and EECP double dip, check previously installed measures at the location | The measure listing should not include evaporative fan controllers for the walk-in cooler or freezer | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-04-12 | Kenny Liljestrom | System of record updated from EECP to QA Checklist per request of Programs team who indicated the property could be cheked via double-dip report | Add | 85
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any |  | EECP | 9 | The measure excludes motors greater than ½ horsepower. | Yes | Motor Size | Replacement motor size (W) | Numeric Value | [8 empty] | Must be <= 373 | QA Checklist | Use the installation report or manufacturer spec sheet to validate the power (W) of the replacement motor is listed | The Power (W) listed in EECP should match the manufacturer spec sheet and be <= 373 W | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property validation needs to be configured | 2021-06-10 | Kenny Liljestrom |  | Add | 26
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any |  | EECP | 10 | The highest quality data collection would include associated motor sizes (nominal W) and a table of material and labor costs for each size of motor being installed. | Yes | CFM | Fan flow rate (CFM) | Numeric Value | [9 empty] | QA Checklist | Use the installation report or manufacturer spec sheet to validate the flow rate (cfm) of the replacement motor is listed | The Flow Rate (cfm) listed in EECP should match the manufacturer spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 19
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any |  | EECP | 11 | To improve quality of cost-effectiveness calculations, programs implementing this measure should collect data on actual costs for materials and labor. The highest quality data collection would include associated motor sizes (nominal W) and a table of material and labor costs for each size of motor being installed. | Yes | Material Cost | Material cost for replacement motor | Numeric Value | [9 empty] | QA Checklist | Use the submitted invoice to verify the material cost of the equipment | The cost listed in EECP should match the submitted invoice | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 35
1 | SWCR004 | 1 | ECM Retrofit for a Walk-in Cooler or Freezer | Any | Any | Any |  | EECP | 12 | To improve quality of cost-effectiveness calculations, programs implementing this measure should collect data on actual costs for materials and labor. The highest quality data collection would include associated motor sizes (nominal W) and a table of material and labor costs for each size of motor being installed. | Yes | Labor Cost | Labor cost for replacement motor | Numeric Value | [9 empty] | QA Checklist | Use the submitted invoice to verify the labor cost of the equipment | The cost listed in EECP should match the submitted invoice | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 32
0 | SWCR005 | 1 | Auto Closer For Refrigerated Storage Door | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | If accessible, photograph the controller nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-12 | Kenny Liljestrom |  | Add | 12
0 | SWCR005 | 1 | Auto Closer For Refrigerated Storage Door | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | If accessible, photograph the controller nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-12 | Kenny Liljestrom |  | Add | 5
0 | SWCR005 | 1 | Auto Closer For Refrigerated Storage Door | A | Any | Any |  | EECP | 3 | The automatic closer must be installed on a walk-in cooler or freezer that was manufactured before January 1, 2009. | Yes | Date of Manufacture | Manufacturer date of walk-in cooler? | Date | [8 empty] | Must be before 1/1/2009 | QA Checklist | The installation report should list the manufacture date of the Walk-In Cooler | The walk-in must be installed prior to 1/1/2009 to be eligible | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-12 | Kenny Liljestrom |  | Add | 36
0 | SWCR005 | 1 | Auto Closer For Refrigerated Storage Door | B | Any | Any |  | EECP | 4 | The automatic closer must be installed on a walk-in cooler or freezer that was manufactured before January 1, 2009. | Yes | Date of Manufacture | Manufacturer date of walk-in freezer? | Date | [8 empty] | Must be before 1/1/2009 | QA Checklist | The installation report should list the manufacture date of the Walk-In Freezer | The walk-in must be installed prior to 1/1/2009 to be eligible | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-12 | Kenny Liljestrom |  | Add | 37
0 | SWCR005 | 1 | Auto Closer For Refrigerated Storage Door | Any | Any | Any |  | EECP | 5 | The measure case is specified as the installation of an automatic door closer on a walk-in cooler or a walk-in freezer door that was not previously equipped with one. | Yes | Existing Auto Close | Did the walk-in cooler or freezer have an existing automatic closer installed? | Drop Down List | Yes;No | [7 empty] | Must be 'No'' | QA Checklist | The installation report should indicate whether or not the walk-in had any existing controls for the door closer; photographs of existing conditions can also verify the existence of any controls | There should not be any previous controls installed on the walk-in door | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWCR005 | 1 | Auto Closer For Refrigerated Storage Door | Any | Any | Any |  | EECP | 6 | The automatic door closer must be installed on the main insulated opaque door(s) of an existing walk-in cooler or freezer. | Yes | Location of Install | Was the automatic door closer installed on the main insulated opaque door(s) of an existing walk-in cooler or freezer? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Locate the main entry door for the walk-in | The door must be opaque (not glass or see through) and act as the main entry door for the walk-in cooler or freezer | QA Checklist | Photographs of the proposed conditions showing the controller installed on a main entry door (large opaque door, not see through, used to access the walk-in) | The photographs should show the doors as being opaque and in a location that would indicate it is the main entry door for the walk-in |  | 2021-08-12 | Kenny Liljestrom |  | Add | 118
0 | SWCR005 | 1 | Auto Closer For Refrigerated Storage Door | Any | Any | Any |  | EECP | 7 | The automatic door closer must firmly close the door when it is within one inch of full closure. | Yes | Firm Close | Does the automatic door closer firmly close the door when it is within one inch of full closure? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Open the door to the walk-in to test the functionality of the auto closer | When the door is closing observe the auto closure and note if the door shuts firmly when closed to about 1-inch of full closure | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-12 | Kenny Liljestrom |  | Add | 96
1 | SWCR005 | 2 | Auto Closer For Refrigerated Storage Door | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | If accessible, photograph the controller nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-11 | Kenny Liljestrom |  |  | 12
1 | SWCR005 | 2 | Auto Closer For Refrigerated Storage Door | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | If accessible, photograph the controller nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-11 | Kenny Liljestrom |  |  | 5
1 | SWCR005 | 2 | Auto Closer For Refrigerated Storage Door | A | Any | Any |  | EECP | 3 | The automatic closer must be installed on a walk-in cooler or freezer that was manufactured before January 1, 2009. | Yes | Date of Manufacture | Manufacturer date of walk-in cooler? | Date | [8 empty] | Must be before 1/1/2009 | QA Checklist | The installation report should list the manufacture date of the Walk-In Cooler | The walk-in must be installed prior to 1/1/2009 to be eligible | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-11 | Kenny Liljestrom |  |  | 36
1 | SWCR005 | 2 | Auto Closer For Refrigerated Storage Door | B | Any | Any |  | EECP | 4 | The automatic closer must be installed on a walk-in cooler or freezer that was manufactured before January 1, 2009. | Yes | Date of Manufacture | Manufacturer date of walk-in freezer? | Date | [8 empty] | Must be before 1/1/2009 | QA Checklist | The installation report should list the manufacture date of the Walk-In Freezer | The walk-in must be installed prior to 1/1/2009 to be eligible | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-11 | Kenny Liljestrom |  |  | 37
1 | SWCR005 | 2 | Auto Closer For Refrigerated Storage Door | Any | Any | Any |  | EECP | 5 | The measure case is specified as the installation of an automatic door closer on a walk-in cooler or a walk-in freezer door that was not previously equipped with one. | Yes | Existing Auto Close | Did the walk-in cooler or freezer have an existing automatic closer installed? | Drop Down List | Yes;No | [7 empty] | Must be 'No'' | QA Checklist | The installation report should indicate whether or not the walk-in had any existing controls for the door closer; photographs of existing conditions can also verify the existence of any controls | There should not be any previous controls installed on the walk-in door | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-11 | Kenny Liljestrom |  |  | 78
1 | SWCR005 | 2 | Auto Closer For Refrigerated Storage Door | Any | Any | Any |  | EECP | 6 | The automatic door closer must be installed on the main insulated opaque door(s) of an existing walk-in cooler or freezer. | Yes | Location of Install | Was the automatic door closer installed on the main insulated opaque door(s) of an existing walk-in cooler or freezer? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Locate the main entry door for the walk-in | The door must be opaque (not glass or see through) and act as the main entry door for the walk-in cooler or freezer | QA Checklist | Photographs of the proposed conditions showing the controller installed on a main entry door (large opaque door, not see through, used to access the walk-in) | The photographs should show the doors as being opaque and in a location that would indicate it is the main entry door for the walk-in |  | 2021-11-11 | Kenny Liljestrom |  |  | 118
1 | SWCR005 | 2 | Auto Closer For Refrigerated Storage Door | Any | Any | Any |  | EECP | 7 | The automatic door closer must firmly close the door when it is within one inch of full closure. | Yes | Firm Close | Does the automatic door closer firmly close the door when it is within one inch of full closure? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Open the door to the walk-in to test the functionality of the auto closer | When the door is closing observe the auto closure and note if the door shuts firmly when closed to about 1-inch of full closure | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-11 | Kenny Liljestrom |  |  | 96
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 12
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 5
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 3 | - | Yes | Model Number | Model Number | Text Box | [9 empty] | - | - | - | - | - | - | request to retire property | 2021-06-10 | Kenny Liljestrom |  | Add | 12
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 3 | This measure is applicable to any existing non-residential building type in commercial sector, and the vintage categories listed below: Prior to 1978 (represented by typical year “1975”) 1978 through 1992 (“1985”) 1993 through 2001 (“1996”) 2002 through 2005 (“2003”) 2006 through 2009 (“2007”) 2010 through 2013 (“2011”) In addition, the following installations are ineligible: New construction installations | Yes | Building vintage | Select the most appropriate building vintage | Drop Down List | Prior to 1978;1978 - 1992;1993 - 2001;2002 - 2005;2006 - 2009;2010 - 2013;2014 - Present; | [7 empty] | Must not be '2014 - Present' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload Can be configured at the enrollment level | 2021-08-06 | Kenny Liljestrom |  | Add | 44
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 4 | - | Yes | Building vintage | Building Vintage | Text Box | [9 empty] | - | - | - | - | - | - | Legacy property should be removed, replaced by above property | 2021-06-10 | Kenny Liljestrom |  | Add | 16
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 4 | This measure is applicable to any existing non-residential building type in commercial sector, and the vintage categories listed below: Prior to 1978 (represented by typical year “1975”) 1978 through 1992 (“1985”) 1993 through 2001 (“1996”) 2002 through 2005 (“2003”) 2006 through 2009 (“2007”) 2010 through 2013 (“2011”) The program should collect and verify the vintage of the building and the refrigeration multiplex system. The offerings are ineligible for multiplex systems majorly upgraded or installed after July 1, 2014 since the Title-24 code mandates the floating controls since July 1, 2014. | Yes | Multiplex System Vintage | Select the most appropriate Multiplex compressor system vintage | Drop Down List | Prior to 1978;1978 - 1992;1993 - 2001;2002 - 2005;2006 - 2009;2010 - 2013;2014 - Present; | [7 empty] | Must not be '2014 - Present' | Inspections | Photograph the nameplate of the refrigeration system; the nameplate may be difficult to locate on the multiplex systems because most are custom made, start by looking at the compressor then the entire system to try and locate a nameplate; you will want to capture the serial number or date of manufacture | The value listed in EECP should match and be identifiable on the equipment nameplate; you may need to use a serial number lookup table online or pass the information to the processing team for them to review and approve this measure property; The equipment must not have been constructed between 2014 and the present year | QA Checklist | Using photographs of the multiplex nameplate, try to identify the equipment age via the serial number or date of manufacture (if listed) | The equipment must not have been constructed between 2014 and the present year |  | 2021-06-10 | Kenny Liljestrom |  | Add | 63
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 5 | - | Yes | Refrigeration multiplex system | Refrigeration Multiplex System | Text Box | [9 empty] | - | - | - | - | - | - | Legacy property should be removed, replaced by 'Multiplex System Vintage' | 2021-06-10 | Kenny Liljestrom |  | Add | 30
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | QA Checklist | 5 | Products cannot be used in conjunction with measures that already incorporate floating head pressure controls. | Yes |  | Measure installed in conjunction with floating head pressure controls? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | QA Checklist | Use the submitted installation report or EECP Double Dip to check for measures installed at the site | This measure cannot be used in conjunction with floating head pressure controls | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 70
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | QA Checklist | 6 | In addition, the following installations are ineligible: Projects that only reprogram a controller; new hardware must be installed. | Yes |  | Is new equipment/hardware being installed (i.e. not reprogramming an existing controller)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to check if the equipment being installed is brand new | The equipment needs to be new (not used or rebuilt) | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 90
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 7 | The controls only apply to refrigeration systems having multiplex compressor systems with existing control of the SCT at a fixed setpoint. The controls are added to float head pressure down to a lower pressure when conditions permit (i.e., changes control from fixed setpoint to floating setpoint). | Yes | Setpoint Controls | Does the existing refrigeration system have a multiplex compressor system with saturated condensing temperature (SCT) controls at a fixed setpoint? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the installation report to check for a demonstration or proof the existing system uses a fixed setpoint to control the condensing temperature | The existing system must operate with fixed saturation setpoint controls | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Should be used to replace 'Refrigeration multiplex system' | 2021-06-10 | Kenny Liljestrom |  | Add | 147
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 8 | The new SCT setpoint must follow the ambient temperature by controlling condenser fans with variable-speed drives or by staging condenser fans. | Yes | Setpoint Adjust | Does the new saturated condensing temperature (SCT) setpoint adjust based on the ambient temperature by controlling condenser fans with variable-speed drives or by staging condenser fans? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Review the installation report or manufacturer spec sheet to check for how the SCT is controlled | The installation report or manufacturer spec sheet must indicate the new SCT setpoint follows the ambient temperature by controlling condenser fans with variable-speed drives or by staging condenser fans | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 187
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 9 | In addition, the following installations are ineligible: Any improvements that will increase system energy use. | Yes |  | Have any improvements been made that would increase system energy use? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 70
0 | SWCR007 | 1 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 10 | Additionally, the calculation of the design cooling load (tons) is to be based on connected display cases, walk-in coolers and freezers, cooled storage, and prep areas only. Sub-cooler loads and air conditioning loads are ineligible for consideration. | Yes | Design tons | Design cooling load for connected display cases, walk-in coolers and freezers, cooled storage, and prep areas only (sub-coolers and air conditioning loads ineligible) (tons) | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-10 | Kenny Liljestrom |  | Add | 173
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Kenny Liljestrom |  |  | 12
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Kenny Liljestrom |  |  | 5
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 3 | This measure is applicable to any existing non-residential building type in commercial sector, and the vintage categories listed below: Prior to 1978 (represented by typical year “1975”) 1978 through 1992 (“1985”) 1993 through 2001 (“1996”) 2002 through 2005 (“2003”) 2006 through 2009 (“2007”) 2010 through 2013 (“2011”) In addition, the following installations are ineligible: New construction installations | No |  | Select the most appropriate building vintage | Drop Down List | Prior to 1978;1978 - 1992;1993 - 2001;2002 - 2005;2006 - 2009;2010 - 2013;2014 - Present; | [7 empty] | Must not be '2014 - Present' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-01-07 | Kenny Liljestrom | Property removed, new construction installations not eligible to be configured at enrollment level |  | 44
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 3 | This measure is applicable to any existing non-residential building type in commercial sector, and the vintage categories listed below: Prior to 1978 (represented by typical year “1975”) 1978 through 1992 (“1985”) 1993 through 2001 (“1996”) 2002 through 2005 (“2003”) 2006 through 2009 (“2007”) 2010 through 2013 (“2011”) In addition, the following installations are ineligible: New construction installations | Yes |  | Building vintage | None | [8 empty] | Construction year must be < current year (new construction not eligible) | - | - | - | - | - | - | This property to be configured at the enrollment level | 2022-01-07 | Kenny Liljestrom |  |  | 16
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 4 | This measure is applicable to any existing non-residential building type in commercial sector, and the vintage categories listed below: Prior to 1978 (represented by typical year “1975”) 1978 through 1992 (“1985”) 1993 through 2001 (“1996”) 2002 through 2005 (“2003”) 2006 through 2009 (“2007”) 2010 through 2013 (“2011”) The program should collect and verify the vintage of the building and the refrigeration multiplex system. The offerings are ineligible for multiplex systems majorly upgraded or installed after July 1, 2014 since the Title-24 code mandates the floating controls since July 1, 2014. | Yes | Multiplex System Vintage | Select the most appropriate Multiplex compressor system vintage | Drop Down List | Prior to 1978;1978 - 1992;1993 - 2001;2002 - 2005;2006 - 2009;2010 - 2013;2014 - Present; | [7 empty] | Must not be '2014 - Present' | Inspections | Photograph the nameplate of the refrigeration system; the nameplate may be difficult to locate on the multiplex systems because most are custom made, start by looking at the compressor then the entire system to try and locate a nameplate; you will want to capture the serial number or date of manufacture | The value listed in EECP should match and be identifiable on the equipment nameplate; you may need to use a serial number lookup table online or pass the information to the processing team for them to review and approve this measure property; The equipment must not have been constructed between 2014 and the present year | QA Checklist | Using photographs of the multiplex nameplate, try to identify the equipment age via the serial number or date of manufacture (if listed) | The equipment must not have been constructed between 2014 and the present year |  | 8/19/2021 | Kenny Liljestrom |  |  | 63
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | QA Checklist | 5 | Products cannot be used in conjunction with measures that already incorporate floating head pressure controls. | Yes |  | Measure installed in conjunction with floating head pressure controls? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | QA Checklist | Use the submitted installation report or EECP Double Dip to check for measures installed at the site | This measure cannot be counted towards other measures like installing a new chiller at the site; check the EECP double dip report to check for claims of a new chiller being installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 8/19/2021 | Kenny Liljestrom |  |  | 70
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 6 | In addition, the following installations are ineligible: Projects that only reprogram a controller; new hardware must be installed. | Yes |  | Is new equipment/hardware being installed (i.e. not reprogramming an existing controller)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to check if the equipment being installed is brand new | The equipment needs to be new (not used or rebuilt) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 8/19/2021 | Kenny Liljestrom |  |  | 90
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 7 | The controls only apply to refrigeration systems having multiplex compressor systems with existing control of the SCT at a fixed setpoint. The controls are added to float head pressure down to a lower pressure when conditions permit (i.e., changes control from fixed setpoint to floating setpoint). | Yes | Setpoint Controls | Does the existing refrigeration system have a multiplex compressor system with saturated condensing temperature (SCT) controls at a fixed setpoint? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the installation report to check for a demonstration or proof the existing system uses a fixed setpoint to control the condensing temperature | The existing system must operate with fixed saturation setpoint controls | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Kenny Liljestrom |  |  | 147
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 8 | The new SCT setpoint must follow the ambient temperature by controlling condenser fans with variable-speed drives or by staging condenser fans. | Yes | Setpoint Adjust | Does the new saturated condensing temperature (SCT) setpoint adjust based on the ambient temperature by controlling condenser fans with variable-speed drives or by staging condenser fans? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Review the installation report or manufacturer spec sheet to check for how the SCT is controlled | The installation report or manufacturer spec sheet must indicate the new SCT setpoint follows the ambient temperature by controlling condenser fans with variable-speed drives or by staging condenser fans | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Kenny Liljestrom |  |  | 187
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | - | 9 | In addition, the following installations are ineligible: Any improvements that will increase system energy use. | No |  | Have any improvements been made that would increase system energy use? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-01-07 | Kenny Liljestrom | Worked with Program Ops to justify removal of property. Since the multiplex system vintage is being captured, capactiy expansion will result in disqualification and added energy use in unlikely. |  | 70
1 | SWCR007 | 2 | Floating Head Pressure Controls, Multiplex | Any | Any | Any |  | EECP | 10 | Additionally, the calculation of the design cooling load (tons) is to be based on connected display cases, walk-in coolers and freezers, cooled storage, and prep areas only. Sub-cooler loads and air conditioning loads are ineligible for consideration. | Yes | Design tons | Design cooling load for connected display cases, walk-in coolers and freezers, cooled storage, and prep areas only (sub-coolers and air conditioning loads ineligible) (tons) | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 8/19/2021 | Kenny Liljestrom |  |  | 173
0 | SWCR010 | 1 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 12
0 | SWCR010 | 1 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 5
0 | SWCR010 | 1 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any |  | EECP | 3 | Measure Description | Yes | Insulation on Bare Suction Pipes | Insulation is being installed on bare suction pipes for medium temperature, walk-in coolers | Drop Down List | [8 empty] | Must be Yes | - | - | - | - | - | - | Request to remove property, in measure description | 2021-08-10 | Kenny Liljestrom |  | Add | 91
0 | SWCR010 | 1 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any |  | EECP | 4 | The eligibility requirements are as follows: • The refrigeration suction pipe on existing equipment must be no more than 1-5/8 inches in diameter. • This measure is applicable to bare suction pipes insulated with closed-cell nitrite rubber or equivalent with at least ¾-inch for medium-temperature and 1-inch for low-temperature systems. • Insulation R-values must be greater than or equal to R-3.2 for medium-temperature cooler pipes. • Insulation R-values must be greater than or equal to R-4.3 low-temperature freezer pipes. | Yes | Size | Refrigeration suction pipe diameter on existing equipment in inches | Numeric Value | [8 empty] | Must be <= 1-5/8 inches | QA Checklist | Use the manufacturer specification sheet or installation report to determine the thickness of the insulation | The insulation thickness should be greater than 1-5/8" and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 67
0 | SWCR010 | 1 | Bare Suction Pipe Insulation, Commercial | A | Any | Any |  | EECP | 5 | The eligibility requirements are as follows: • The refrigeration suction pipe on existing equipment must be no more than 1-5/8 inches in diameter. • This measure is applicable to bare suction pipes insulated with closed-cell nitrite rubber or equivalent with at least ¾-inch for medium-temperature and 1-inch for low-temperature systems. • Insulation R-values must be greater than or equal to R-3.2 for medium-temperature cooler pipes. • Insulation R-values must be greater than or equal to R-4.3 low-temperature freezer pipes. | Yes | R-value Installed Greater | Is the insulation R-values of the installed insulation greater than or equal to R-3.2? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Use the manufacturer specification sheet or installation report to determine the insulation R-Value | The insulation R-Value should be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 86
0 | SWCR010 | 1 | Bare Suction Pipe Insulation, Commercial | B | Any | Any |  | EECP | 6 | The eligibility requirements are as follows: • The refrigeration suction pipe on existing equipment must be no more than 1-5/8 inches in diameter. • This measure is applicable to bare suction pipes insulated with closed-cell nitrite rubber or equivalent with at least ¾-inch for medium-temperature and 1-inch for low-temperature systems. • Insulation R-values must be greater than or equal to R-3.2 for medium-temperature cooler pipes. • Insulation R-values must be greater than or equal to R-4.3 low-temperature freezer pipes. | Yes | R-value Installed Greater | Is the insulation R-values of the installed insulation greater than or equal to R-4.3? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Use the manufacturer specification sheet or installation report to determine the insulation R-Value | The insulation R-Value should be >= 4.3 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 86
1 | SWCR010 | 2 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 12
1 | SWCR010 | 2 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 5
1 | SWCR010 | 2 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any |  | EECP | 3 | Measure Description | No | Insulation on Bare Suction Pipes | Insulation is being installed on bare suction pipes for medium temperature, walk-in coolers | Drop Down List | [8 empty] | Must be Yes | - | - | - | - | - | - | Request to remove property, in measure description | 2021-08-10 | Kenny Liljestrom |  | Add | 91
1 | SWCR010 | 2 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any |  | EECP | 3 | Measure Description | No | PreExisting Bare Suction Pipe | Is the pre-existing condition bare suction pipe on a low-temperature, walk-in freezer? | Drop Down List | [8 empty] | Must be Yes | - | - | - | - | - | - | Request to remove property, in measure description | 2021-08-10 | Kenny Liljestrom |  |  | 86
1 | SWCR010 | 2 | Bare Suction Pipe Insulation, Commercial | Any | Any | Any |  | EECP | 4 | The eligibility requirements are as follows: • The refrigeration suction pipe on existing equipment must be no more than 1-5/8 inches in diameter. • This measure is applicable to bare suction pipes insulated with closed-cell nitrite rubber or equivalent with at least ¾-inch for medium-temperature and 1-inch for low-temperature systems. • Insulation R-values must be greater than or equal to R-3.2 for medium-temperature cooler pipes. • Insulation R-values must be greater than or equal to R-4.3 low-temperature freezer pipes. | Yes | Size | Refrigeration suction pipe diameter on existing equipment in inches | Numeric Value | [8 empty] | Must be <= 1-5/8 inches | QA Checklist | Use the manufacturer specification sheet or installation report to determine the thickness of the insulation | The insulation thickness should be greater than 1-5/8" and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 67
1 | SWCR010 | 2 | Bare Suction Pipe Insulation, Commercial | A | Any | Any |  | EECP | 5 | The eligibility requirements are as follows: • The refrigeration suction pipe on existing equipment must be no more than 1-5/8 inches in diameter. • This measure is applicable to bare suction pipes insulated with closed-cell nitrite rubber or equivalent with at least ¾-inch for medium-temperature and 1-inch for low-temperature systems. • Insulation R-values must be greater than or equal to R-3.2 for medium-temperature cooler pipes. • Insulation R-values must be greater than or equal to R-4.3 low-temperature freezer pipes. | Yes | R-value Installed Greater | Is the insulation R-values of the installed insulation greater than or equal to R-3.2? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Use the manufacturer specification sheet or installation report to determine the insulation R-Value | The insulation R-Value should be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 86
1 | SWCR010 | 2 | Bare Suction Pipe Insulation, Commercial | B | Any | Any |  | EECP | 6 | The eligibility requirements are as follows: • The refrigeration suction pipe on existing equipment must be no more than 1-5/8 inches in diameter. • This measure is applicable to bare suction pipes insulated with closed-cell nitrite rubber or equivalent with at least ¾-inch for medium-temperature and 1-inch for low-temperature systems. • Insulation R-values must be greater than or equal to R-3.2 for medium-temperature cooler pipes. • Insulation R-values must be greater than or equal to R-4.3 low-temperature freezer pipes. | Yes | R-value Installed Greater | Is the insulation R-values of the installed insulation greater than or equal to R-4.3? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Use the manufacturer specification sheet or installation report to determine the insulation R-Value | The insulation R-Value should be >= 4.3 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 86
0 | SWCR015 | 1 | Medium-Temperature Case Doors | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 12
0 | SWCR015 | 1 | Medium-Temperature Case Doors | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 5
0 | SWCR015 | 1 | Medium-Temperature Case Doors | Any | Any | Any |  | EECP | 3 | The retrofit of glass doors, or glass doors with LED lights, for a medium-temperature, open-vertical, refrigerated display case must be added to an existing open-vertical, medium temp display case. The complete removal of the existing display case and replacing it with a new case with glass doors is not eligible | Yes |  | Are the glass doors being installed on an existing vertical display case? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | Photograph and observe the display case and determine the case type (vertical, horizontal, coffin, etc.) | To qualify, the display case with the retrofitted doors must be a vertical display case | QA Checklist | Check EECP for photographs of the display cases; or check the invoice and determine if the entire case was replaced | The photograph should show glass doors on the display case; or the invoice should only show costs for the doors and hardware, not an entire case replacement | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 73
0 | SWCR015 | 1 | Medium-Temperature Case Doors | Any | Any | Any |  | QA Checklist | 4 | In addition to retrofitting the doors and door frames, the measure may require changes to the refrigeration system serving the affected display case(s). These changes may include but are not limited to: replacing the expansion valve and/or evaporator pressure regulating valve, adjusting the evaporator temperature/pressure set point, resizing refrigeration piping, replacing the flood back valve on the condenser, resizing the coil/piping on applicable heat reclaim systems, and replacing or removing compressors. These potential changes stem from the significant reduction in the overall refrigeration load. Due to the complexity in determining which system alterations will be required at a site to maintain optimum system performance, a refrigeration contractor with design experience should be consulted before proceeding with the retrofit. | Yes |  | Was a design consultant used for major refrigeration system upgrades as a result of this measure? | Drop Down List | Yes;No;N/A; | [7 empty] | Must be 'Yes' or 'N/A' | QA Checklist | Review submitted invoice to determine if the Medium Case doors are being purchased with a new case | The doors must be listed on the invoice not in conjunction with a new/replacement case; The tmeasure requires the doors to be a standalone measure not a case replacement | - | - | - |  | 2022-04-12 | Kenny Liljestrom | System of record updated from EECP to QA Checklist per request of Programs team who indicated the property could be cheked via invoice. | Add | 97
0 | SWCR015 | 1 | Medium-Temperature Case Doors | Any | Any | Any |  | EECP | 5 | Anti-sweat heat (ASH) may not be present in the glass doors or door mounting. (Two out of three manufacturers stated that their products did not contain ASH in the door or mullion. Thus, it was decided to specifically prohibit door and frame heat, as it does not appear necessary in medium-temperature applications.) | No | Doors Anti Sweat Heat Controls | Do the retrofit doors have ASH controls installed? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | QA Checklist | Use the submitted manufacturer spec sheet to determine whether the retrofit doors have Anti-Sweat Heater (ASH) controls installed | The retrofit doors must NOT have ASH controls already installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-04-12 | Kenny Liljestrom | Measure property removed, the measure package does not say this is an absolute requirement, it just suggests a design consultant be used. Worked with programs team to remove property. | Add | 50
0 | SWCR015 | 1 | Medium-Temperature Case Doors | B | Any | Any |  | EECP | 6 | Total lighting power in the measure case may not exceed total lighting power in the base case (Several manufacturers interviewed stated that most retrofits include a switch to more efficient LED case lighting, but not an overall increase in lighting power density.) | Yes | Power Density | Has the lighting power density increased with a replacement or retrofit of the LED lighting systems in the display case? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-10 | Kenny Liljestrom |  | Add | 120
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 12
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 5
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any |  | QA Checklist | 3 | Eligible Building Types This measure is applicable for the following existing building types: Education – University, Health/Medical – Hospital, Manufacturing – Biotech, and Manufacturing – Pharmaceuticals. | Yes | Building Type | Building Type | Drop Down List | Education – University;Health/Medical – Hospital;Manufacturing – Biotech;Manufacturing – Pharmaceuticals;Other; | [7 empty] | Must not be 'Other' | QA Checklist | Verify the building type is Education – University; Health/Medical – Hospital; Manufacturing – Biotech; or Manufacturing – Pharmaceuticals | The building type must be Education – University; Health/Medical – Hospital; Manufacturing – Biotech; or Manufacturing – Pharmaceuticals | Inspections | During inspection verify building type | The building type must be Education – University; Health/Medical – Hospital; Manufacturing – Biotech; or Manufacturing – Pharmaceuticals |  | 8/19/2021 | Keith Valenzuela |  | Add | 13
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any |  | QA Checklist | 4 | Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | Freezer Type | Freezer Type | Drop Down List | Upright;Coffin;Other; | [7 empty] | Must be 'Upright' | QA Checklist | Use the make and model number listed on the invoice/EECP and verify freezer type. | The freezer type must be "Upright" | Inspections | During inspection verify freezer type | The freezer type must be "Upright" |  | 8/19/2021 | Keith Valenzuela |  | Add | 12
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any |  | EECP | 5 | Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | Setpoint storage temperature range | Is the setpoint storage temperature range between -70 °C and -80 °C (-94 °F and -112 °F)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | During inspection verify freezer temperature | Freezer temperature must be between -70 °C and -80 °C (-94 °F and -112 °F)? | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 89
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any |  | QA Checklist | 6 | Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | ENERGY STAR Qualified? | Does the freezer have an ENERGY STAR certification? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the make and model number listed on the invoice/EECP and cross check the EnergyStar database to determine if the product is listed as EnergyStar qualified | The listed make and model in EECP should be included in the EnergyStar database | - | None | None |  | 8/19/2021 | Keith Valenzuela |  | Add | 51
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any |  | QA Checklist | 7 | Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | Daily Energy Use | Maximum daily energy consumption(MDEC) (kWh/day/ft3) | Numeric Value | [8 empty] | If "Does the freezer have an ENERGY STAR verification?" is 'No' then <= 0.55 | QA Checklist | Use the make and model number listed on the invoice/EECP and verify freezer energy use (kWh/day/ft3) | Freezer energy use must be <= 0.55 kWh/day/ft3 | - | None | None |  | 8/19/2021 | Keith Valenzuela |  | Add | 52
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | A | Any | Any |  | EECP | 8 | Refrig-Freezer-High Efficiency Ultra-Low Temperature (ULT, -80 °C) Freezers, 15 to <24 ft3 | Yes | Freezer Volume (ft^3) | Volume of freezer in cubic feet? | Numeric Value | [8 empty] | >= 15 and < 24 | QA Checklist | Use the make and model number listed on the invoice/EECP and verify freezer volume. | Freezer volume must be >= 15 cubic feet and < 24 cubic feet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 32
1 | SWCR017 | 1 | High Efficiency Ultra-Low Temperature Freezers | B | Any | Any |  | EECP | 9 | Refrig-Freezer-High Efficiency Ultra-Low Temperature (ULT, -80 °C) Freezers, 24 to 29 ft3 | Yes | Freezer Volume (ft^3) | Volume of freezer in cubic feet? | Numeric value | [8 empty] | 24 ≤ and ≤ 29 | QA Checklist | Use the make and model number listed on the invoice/EECP and verify freezer volume. | Freezer volume must be 24 cubic feet ≤ and ≤ 29 cubic feet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 32
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 12
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 5
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any |  | QA Checklist | 3 | Eligible Building Types This measure is applicable for the following existing building types: Education – University, Health/Medical – Hospital, Manufacturing – Biotech, and Manufacturing – Pharmaceuticals. | Yes | Building Type | Building Type | Drop Down List | Education – University;Health/Medical – Hospital;Manufacturing – Biotech;Manufacturing – Pharmaceuticals;Other; | [7 empty] | Must not be 'Other' | QA Checklist | Verify the building type is Education – University; Health/Medical – Hospital; Manufacturing – Biotech; or Manufacturing – Pharmaceuticals | The building type must be Education – University; Health/Medical – Hospital; Manufacturing – Biotech; or Manufacturing – Pharmaceuticals | Inspections | During inspection verify building type | The building type must be Education – University; Health/Medical – Hospital; Manufacturing – Biotech; or Manufacturing – Pharmaceuticals |  | 8/19/2021 | Keith Valenzuela |  | Add | 13
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any |  | QA Checklist | 4 | Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | Freezer Type | Freezer Type | Drop Down List | Upright;Coffin;Other; | [7 empty] | Must be 'Upright' | QA Checklist | Use the make and model number listed on the invoice/EECP and verify freezer type. | The freezer type must be "Upright" | Inspections | During inspection verify freezer type | The freezer type must be "Upright" |  | 8/19/2021 | Keith Valenzuela |  | Add | 12
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any |  | EECP | 5 | Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | Setpoint storage temperature range | Is the setpoint storage temperature range between -70 °C and -80 °C (-94 °F and -112 °F)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | During inspection verify freezer temperature | Freezer temperature must be between -70 °C and -80 °C (-94 °F and -112 °F)? | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 89
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any |  | QA Checklist | 6 | Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | ENERGY STAR Qualified? | Does the freezer have an ENERGY STAR certification? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the make and model number listed on the invoice/EECP and cross check the EnergyStar database to determine if the product is listed as EnergyStar qualified | The listed make and model in EECP should be included in the EnergyStar database | - | None | None |  | 8/19/2021 | Keith Valenzuela |  | Add | 51
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | Any | Any | Any |  | QA Checklist | 7 | Eligible Products A qualifying ultra-low-temperature (ULT) freezer must meet the following criteria: • Upright ULT freezer designed for laboratory application that will maintain a setpoint storage temperature between -70 °C and -80 °C (-94 °F and -112 °F) • ENERGY STAR® certification, or the maximum daily energy consumption (MDEC) of an ULT freezer at -75 °C (-103 °F) is 0.55 kWh/day/ft3 • 15 ft3 < Volume = 29 ft3 | Yes | Daily Energy Use | Maximum daily energy consumption(MDEC) (kWh/day/ft3) | Numeric Value | [8 empty] | If "Does the freezer have an ENERGY STAR verification?" is 'No' then <= 0.55 | QA Checklist | Use the make and model number listed on the invoice/EECP and verify freezer energy use (kWh/day/ft3) | Freezer energy use must be <= 0.55 kWh/day/ft3 | - | None | None |  | 8/19/2021 | Keith Valenzuela |  | Add | 52
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | A | Any | Any |  | EECP | 8 | Refrig-Freezer-High Efficiency Ultra-Low Temperature (ULT, -80 °C) Freezers, 15 to <24 ft3 | Yes | Freezer Volume (ft^3) | Volume of freezer in cubic feet? | Numeric Value | [8 empty] | >= 15 and < 24 | QA Checklist | Use the make and model number listed on the invoice/EECP and verify freezer volume. | Freezer volume must be >= 15 cubic feet and < 24 cubic feet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 32
0 | SWCR017 | 2 | High Efficiency Ultra-Low Temperature Freezers | B | Any | Any |  | EECP | 9 | Refrig-Freezer-High Efficiency Ultra-Low Temperature (ULT, -80 °C) Freezers, 24 to 29 ft3 | Yes | Freezer Volume (ft^3) | Volume of freezer in cubic feet? | Numeric value | [8 empty] | 24 ≤ and ≤ 29 | QA Checklist | Use the make and model number listed on the invoice/EECP and verify freezer volume. | Freezer volume must be 24 cubic feet ≤ and ≤ 29 cubic feet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 8/19/2021 | Keith Valenzuela |  | Add | 32
1 | SWCR018 | 2 | Reach-In Refrigerator or Freezer, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-09 | Kenny Liljestrom |  | Add | 12
1 | SWCR018 | 2 | Reach-In Refrigerator or Freezer, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-09 | Kenny Liljestrom |  | Add | 5
1 | SWCR018 | 2 | Reach-In Refrigerator or Freezer, Commercial | Any | Any | Any |  | EECP | 3 | No requirement listed | Yes |  | New Equipment | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Collect the equipment invoice for the product | The invoice should list the equipment as new (i.e. not used, rebuilt. or leased) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 13
1 | SWCR018 | 2 | Reach-In Refrigerator or Freezer, Commercial | Any | Any | Any |  | EECP | 4 | Eligible products include ENERGY STAR®-qualified commercial reach-in refrigerators and freezers that replace a standard efficiency unit of the same configuration and capacity. | Yes | Energy Star Qualified | ENERGY STAR Qualified? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the make and model number listed on the invoice/EECP and cross check the EnergyStar database to determine if the product is listed as EnergyStar qualified | The listed make and model in EECP should be included in the EnergyStar database | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-09 | Kenny Liljestrom |  | Add | 22
1 | SWCR018 | 2 | Reach-In Refrigerator or Freezer, Commercial | Any | Any | Any |  | EECP | 5 | Good to have | Yes |  | Volume of reach-in unit (ft3) | Numeric Value | [9 empty] | QA Checklist | Use the EnergyStar database to capture the volume of the specified equipment | The EnergyStar database value for the volume should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 29
1 | SWCR018 | 2 | Reach-In Refrigerator or Freezer, Commercial | Any | Any | Any |  | EECP | 6 | Units with remote refrigeration systems do not qualify and used or rebuilt equipment is not eligible. | Yes | Remote Refrigeration System | Does the installed unit have a remote refrigeration system? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-09 | Kenny Liljestrom |  | Add | 59
1 | SWCR018 | 2 | Reach-In Refrigerator or Freezer, Commercial | Any | Any | Any |  | EECP | 7 | Eligible products include ENERGY STAR®-qualified commercial reach-in refrigerators and freezers that replace a standard efficiency unit of the same configuration and capacity. | Yes | New Same as Existing | Is the existing unit a standard efficiency unit of the same configuration and capacity? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-09 | Kenny Liljestrom |  | Add | 87
0 | SWCR019 | 1 | Low-Temperature Coffin to Reach-in Display Case Conversion | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 12
0 | SWCR019 | 1 | Low-Temperature Coffin to Reach-in Display Case Conversion | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 5
0 | SWCR019 | 1 | Low-Temperature Coffin to Reach-in Display Case Conversion | Any | Any | Any |  | EECP | 3 | Equipment must be new | Yes | New Equipment | New Equipment | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 13
0 | SWCR019 | 1 | Low-Temperature Coffin to Reach-in Display Case Conversion | Any | Any | Any |  | EECP | 4 | All coffin replacements with a reach-in display case must meet the specifications in the Measure Case Description. The measure is applicable to replace any existing coffin that is less than or equal to code: • If the display width is less than or equal to 3 feet, the coffin must be replaced by a reach-in case that is ⅟4 of the total length of the coffins or less. • If the display width is greater than 3 feet, the coffin must be replaced by a reach-in case that is ⅓ of the total length of the coffin or less. | Yes | Existing Unit Width | Is the existing unit a low temp coffin with a display width greater than 3 feet? | Drop Down List | Yes;No | [7 empty] | Must be Yes | Inspections | Check the length of the newly installed case, you can do this by estimating, no need for actual measurements | The case needs to be greater than 3-feet in length | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-10 | Kenny Liljestrom |  | Add | 80
0 | SWCR019 | 1 | Low-Temperature Coffin to Reach-in Display Case Conversion | Any | Any | Any |  | EECP | 5 | All coffin replacements with a reach-in display case must meet the specifications in the Measure Case Description. The measure is applicable to replace any existing coffin that is less than or equal to code: • If the display width is less than or equal to 3 feet, the coffin must be replaced by a reach-in case that is ⅟4 of the total length of the coffins or less. • If the display width is greater than 3 feet, the coffin must be replaced by a reach-in case that is ⅓ of the total length of the coffin or less. | Yes | Existing Unit Length | Is the installed unit a reach-in case that is "1/4" of the total length of the coffin or less? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-10 | Kenny Liljestrom |  | Add | 94
0 | SWCR019 | 1 | Low-Temperature Coffin to Reach-in Display Case Conversion | Any | Any | Any |  | EECP | 6 | The replacement case must include triple-pane doors with low or no anti-sweat heat or anti-sweat-heat controls. | Yes | Doors Anti Sweat Heat Controls | Does the installed case include triple-pane doors with low or no anti-sweat heat or anti-sweat-heat controls? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-10 | Kenny Liljestrom |  | Add | 109
1 | SWCR020 | 1 | Medium-Temperature Open Display Case Retrofit | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 12
1 | SWCR020 | 1 | Medium-Temperature Open Display Case Retrofit | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-04 | Kenny Liljestrom |  | Add | 5
1 | SWCR020 | 1 | Medium-Temperature Open Display Case Retrofit | Any | Any | Any |  | EECP | 3 | - | Yes | New Equipment | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property can be removed | 2021-08-04 | Kenny Liljestrom |  | Add | 43
1 | SWCR020 | 1 | Medium-Temperature Open Display Case Retrofit | Any | Any | Any |  | EECP | 4 | The medium-temperature display case must meet or exceed specifications and efficiency requirements in the Measure Case Description and Code Requirements through the use of a high efficiency evaporator coil. | Yes | Evaporator Coil | Was a medium-temperature, open, vertical refrigerated display case with a high efficiency evaporator coil installed? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-08-04 | Kenny Liljestrom |  | Add | 116
1 | SWCR020 | 1 | Medium-Temperature Open Display Case Retrofit | Any | Any | Any |  | EECP | 5 | The new display case must replace an existing medium-temperature, open, vertical refrigerated display case of the same style | Yes | New Same as Existing | Was the installed unit the same style as the existing case? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-08-04 | Kenny Liljestrom |  | Add | 60
1 | SWCR020 | 1 | Medium-Temperature Open Display Case Retrofit | Any | Any | Any |  | EECP | 6 | The manufacturer spec sheet for the new display case must be submitted to the Program for review to confirm eligibility. | Yes | Manufacturer Cut Sheet Submitted | Manufacturer specification sheet submitted with the application? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | Review the EECP documentation and look for the manufacturer spec sheet | A spec sheet must be submitted for this measure to qualify | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-04 | Kenny Liljestrom |  | Add | 64
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-09 | Kenny Liljestrom |  | Add | 12
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-09 | Kenny Liljestrom |  | Add | 5
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any |  | EECP | 3 | This measure is applicable for supermarkets and grocery stores with stand-alone and/or multiplex compressor racks that provide refrigeration to remote display cases and walk-in coolers/freezers. This measure is applicable to supermarkets and grocery stores with both medium-temperature and low-temperature open multi-deck refrigeration cases. Must replace an existing, open, multi-deck display case with a new reach-in unit with doors, electronically commutated motor (ECM) evaporator fan(s), and LED lighting. | Yes | Display Case Replace | Is an existing, open, multi-deck display case being replaced with a new reach-in unit with doors, electronically commutated motor (ECM) evaporator fan(s), and LED lighting? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | Use the submitted manufacturer spec sheet to validate the display case specifications | the case must consist of: Reach-In type with doors, electronically commutated motor (ECM) evaporator fan(s), and LED lighting | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-09 | Kenny Liljestrom |  | Add | 172
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any |  | EECP | 4 | Refurbished cases are not eligible unless compliant with the 2012 Federal Efficiency Standards (see Code Requirements). | Yes |  | New Equipment | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | Collect the equipment invoice for the product | The invoice should list the equipment as new (i.e. not used, rebuilt. or leased) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 13
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | A | Any | Any |  | EECP | 5 | Medium-temperature cases must have no heat in the door. Heat is allowed in the frames of medium temperature cases. | Yes |  | Do the medium-temp cases have heat in the door (answer No if there is only heat in the door frame)? | Drop Down List | Yes;No; | [7 empty] | Must be No | QA Checklist | Use the submitted manufacturer spec sheet to validate if the display case already has heaters or Anti-Sweat Heaters (ASH) controls installed | The display case must NOT have ASH controls installed; heaters in the frame of the case are ok | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 99
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | B | Any | Any |  | EECP | 6 | Low-temperature case door and frame heaters combined may not consume more than 50 W/ft of case length. | Yes | Doorframe Measurement | Do the low-temperature case door and frame heaters combined consume more than 50 W/ft of case length? | Drop Down List | Yes;No; | [7 empty] | Must be No | QA Checklist | Use the submitted manufacturer spec sheet to validate the energy consumed per linear foot of the case | The energy per linear foot of the display case must be <= 50 W/ft; to calculate this value, take the input energy or total power (W) and divide by the length of the case (ft), this value should be <= 50 W/ft | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-09 | Kenny Liljestrom |  | Add | 101
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any |  | EECP | 7 | The new case length must be less than or equal to the original case length. | Yes | New Case Length | Is the new case length less than or equal to the original case length? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-09 | Kenny Liljestrom |  | Add | 70
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any |  | EECP | 8 | This measure is only for display cases served by a remote refrigeration system. | Yes | Remote Refrigeration System | Are the display cases served by a remote refrigeration system? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-09 | Kenny Liljestrom |  | Add | 62
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any |  | EECP | 9 | Specialty deli cases, custom coolers/freezers, and walk-in boxes with reach-in doors are not eligible. | Yes | Category | Are the display cases any of the following: specialty deli cases, custom coolers/freezers, and walk-in boxes with reach-in doors? | Drop Down List | Yes;No; | [7 empty] | Must be No | QA Checklist | Using the submitted manufacturer spec sheet, check the case type (vertical, horizontal, deli coffin, etc.) | The case type must not be any of the following case types: specialty deli cases, custom coolers/freezers, and walk-in boxes with reach-in doors | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-09 | Kenny Liljestrom |  | Add | 129
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any |  | EECP | 10 | Display case replacements that are part of large-scale store remodels and any new construction projects should be revised to be custom measures. Large-scale remodels are defined as any project involving 50% of the linear feet of refrigerated casework or 32 linear feet of casework replacements, whichever is less. | Yes | Large Scale Remodel | Large-scale remodels are defined as any project involving 50% of the linear feet of refrigerated casework or 32 linear feet of casework replacements, whichever is less. Are the display case replacements part of large-scale store remodels? | Drop Down List | Yes;No; | [7 empty] | Must be No | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-09 | Kenny Liljestrom |  | Add | 238
0 | SWCR021 | 1 | Medium or Low-Temperature Display Case With Doors | Any | Any | Any |  | EECP | 11 | Salvage, disposal or photographic records of replaced equipment should be part of program application requirements when early replacement or open-to-closed case conversion savings are being utilized to ensure the correct baseline is assumed for these measures. | Yes |  | If customer chose Accelerated Replacement, have written/photographic records disposal been provided? | Drop Down List | Yes;No;N/A; | [7 empty] | Must be Yes or N/A | QA Checklist | Review the EECP submitted files and check for photographic evidence or records indicating the disposal of the existing cases | The display cases need to be properly disposed of with photographic or documented evidence | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 100
1 | SWFS001 | 2 | Convection Oven, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-07 | Kenny Liljestrom |  | Add | 12
1 | SWFS001 | 2 | Convection Oven, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-07 | Kenny Liljestrom |  | Add | 5
1 | SWFS001 | 2 | Convection Oven, Commercial | Any | Any | Any |  | EECP | 3 | All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. * Half-size gas convection ovens are excluded from ENERGY STAR. | Yes | Energy Star Qualified | ENERGY STAR Qualified? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | Use the make and model number listed on the invoice/EECP and cross check the EnergyStar database to determine if the product is listed as EnergyStar qualified | The listed make and model in EECP should be included in the EnergyStar database | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Needs to be updated to a per measure basis. The requirement says it can be CEC certified as well. | 2021-06-10 | Kenny Liljestrom |  | Add | 22
1 | SWFS001 | 2 | Convection Oven, Commercial | Any | Any | Any |  | EECP | 3 | Used or rebuilt equipment is not eligible. Half-size gas convection is not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 43
1 | SWFS001 | 2 | Convection Oven, Commercial | A | Any | Any |  | EECP | 4 | All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. * Half-size gas convection ovens are excluded from ENERGY STAR. | Yes |  | Product qualification method? | Drop Down List | CEC ;EnergyStar;Other; | [7 empty] | Must not be Other | QA Checklist | Use the make and model number listed on the invoice/EECP and cross check the EnergyStar database to determine if the product is listed as EnergyStar qualified | The listed make and model in EECP should be included in the EnergyStar database | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Use to replace 'Energy Star Qualified' | 2021-06-07 | Kenny Liljestrom |  | Add | 29
1 | SWFS001 | 2 | Convection Oven, Commercial | B | Any | Any |  | EECP | 5 | Measure Description | Yes | Size | Oven Size | Drop Down List | Full;Half | [7 empty] | Must be 'Full' | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the equipment is size (half or full size) | The equipment should be listed as being a full-size | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property needs to be reconfigured in EECP. It is currently configured as 'Half' | 2021-06-10 | Kenny Liljestrom |  | Add | 9
1 | SWFS001 | 2 | Convection Oven, Commercial | A | Any | Any |  | EECP | 5 | Measure Description | Yes |  | Oven Size | Drop Down List | Full;Half | [7 empty] | Must be 'Half' | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the equipment is size (half or full size) | The equipment should be listed as being a half-size | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 9
1 | SWFS001 | 2 | Convection Oven, Commercial | C | Any | Any |  | EECP | 5 | Measure Description | Yes |  | Oven Size | Drop Down List | Full;Half | [7 empty] | Must be 'Half' | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the equipment is size (half or full size) | The equipment should be listed as being a half-size | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 9
1 | SWFS001 | 2 | Convection Oven, Commercial | D | Any | Any |  | EECP | 5 | Measure Description | Yes |  | Oven Size | Drop Down List | Full;Half | [7 empty] | Must be 'Full' | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the equipment is size (half or full size) | The equipment should be listed as being a full-size | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 9
1 | SWFS001 | 2 | Convection Oven, Commercial | A | Any | Any |  | EECP | 6 | Energy Efficiency Requirements of Commercial Convection Ovens Table | Yes |  | Min Cooking Efficiency (%) | Numeric Value | [8 empty] | If Energy Star Qualified = 'EnergyStar' must be >=71% | QA Checklist | If the product is not listed as being EnergyStar qualified, use the submitted installation report or manufacturer spec sheet to validate the equipment minimum cooking efficiency (%) | The cooking efficiency needs to be >= 71% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 27
1 | SWFS001 | 2 | Convection Oven, Commercial | A | Any | Any |  | EECP | 7 | All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. | Yes |  | Max Idle Energy Rate (kW) | Numeric Value | [8 empty] | If 'Energy Star Qualified" is 'No' then make active Must be <= 1.0 | QA Checklist | If the product is not listed as being EnergyStar qualified, use the submitted installation report or manufacturer spec sheet to validate the equipment Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 1.0 kW | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 25
1 | SWFS001 | 2 | Convection Oven, Commercial | B | Any | Any |  | EECP | 8 | Energy Efficiency Requirements of Commercial Convection Ovens Table | Yes | EFFICIENCY | Min Cooking Efficiency (%) | Numeric Value | [8 empty] | If Energy Star Qualified = 'EnergyStar' Must be >=71% | QA Checklist | If the product is not listed as being EnergyStar qualified, use the submitted installation report or manufacturer spec sheet to validate the equipment minimum cooking efficiency (%) | The cooking efficiency needs to be >= 71% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 27
1 | SWFS001 | 2 | Convection Oven, Commercial | B | Any | Any |  | EECP | 10 | All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [8 empty] | If 'Energy Star Qualified" is 'No' then make active Must be <= 1.6 | QA Checklist | If the product is not listed as being EnergyStar qualified, use the submitted installation report or manufacturer spec sheet to validate the equipment Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 1.6 kW | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-10 | Kenny Liljestrom |  | Add | 25
1 | SWFS001 | 2 | Convection Oven, Commercial | D | Any | Any |  | EECP | 16 | All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. | Yes |  | Min. Cooking Energy Efficiency (%) | Numeric Value | [8 empty] | If 'Energy Star Qualified" is 'No' then make active Must be >= 46% | QA Checklist | If the product is not listed as being EnergyStar qualified, use the submitted installation report or manufacturer spec sheet to validate the equipment minimum cooking efficiency (%) | The cooking efficiency needs to be >= 46% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 34
1 | SWFS001 | 2 | Convection Oven, Commercial | D | Any | Any |  | EECP | 17 | Energy Efficiency Requirements of Commercial Convection Ovens Table | Yes |  | Idle Energy Rate (Btu/Hr) | Numeric Value | [8 empty] | If Energy Star Qualified = 'EnergyStar' Must be <= 12000 | QA Checklist | If the product is not listed as being EnergyStar qualified, use the submitted installation report or manufacturer spec sheet to validate the equipment Idle Energy Rate (Btu/hr) | The idle energy rate must be <= 12,000 Btu/hr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 25
1 | SWFS001 | 2 | Convection Oven, Commercial | B | Any | Any |  | EECP | 18 | All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. * Half-size gas convection ovens are excluded from ENERGY STAR. | Yes |  | Product qualification method? | Drop Down List | CEC ;EnergyStar;Other; | [7 empty] | Must not be Other | QA Checklist | Use the make and model number listed on the invoice/EECP and cross check the EnergyStar database to determine if the product is listed as EnergyStar qualified | The listed make and model in EECP should be included in the EnergyStar database | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Use to replace 'Energy Star Qualified' | 2021-06-07 | Kenny Liljestrom |  | Add | 29
1 | SWFS001 | 2 | Convection Oven, Commercial | C | Any | Any |  | EECP | 19 | All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. * Half-size gas convection ovens are excluded from ENERGY STAR. | Yes |  | Product qualification method? | Drop Down List | CEC ;EnergyStar;Other; | [7 empty] | Must be 'CEC' | QA Checklist | Use the make and model number listed on the invoice/EECP and cross check the EnergyStar database to determine if the product is listed as EnergyStar qualified | The listed make and model in EECP should be included in the EnergyStar database | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Use to replace 'Energy Star Qualified' | 2021-06-07 | Kenny Liljestrom |  | Add | 29
1 | SWFS001 | 2 | Convection Oven, Commercial | D | Any | Any |  | EECP | 20 | All qualifying convection oven models must be approved and listed in the California Energy Commission (CEC) certified appliance database or must meet the ENERGY STAR Version 2.2 eligibility criteria. * Half-size gas convection ovens are excluded from ENERGY STAR. | Yes |  | Product qualification method? | Drop Down List | CEC ;EnergyStar;Other; | [7 empty] | Must not be Other | QA Checklist | Use the make and model number listed on the invoice/EECP and cross check the EnergyStar database to determine if the product is listed as EnergyStar qualified | The listed make and model in EECP should be included in the EnergyStar database | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Use to replace 'Energy Star Qualified' | 2021-06-07 | Kenny Liljestrom |  | Add | 29
0 | SWFS002 | 1 | Door-Type Dishwasher, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-11 | Kenny Liljestrom |  | Add | 12
0 | SWFS002 | 1 | Door-Type Dishwasher, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-11 | Kenny Liljestrom |  | Add | 5
0 | SWFS002 | 1 | Door-Type Dishwasher, Commercial | Any | Any | Any |  | EECP | 3 | Used or rebuilt equipment and other dishwasher types (conveyor, under-counter, flight-type) are not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 43
0 | SWFS002 | 1 | Door-Type Dishwasher, Commercial | A | Any | Any |  | EECP | 4 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Water Consumption | Water consumption of dishwasher in gallons per rack | Numeric Value | [8 empty] | Must be <=0.76 | QA Checklist | Using the submitted manufacturer spec sheet validate the water consumption per pack (gallons/rack) | The water consumption must be <= 0.76 gallons/rack | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 51
0 | SWFS002 | 1 | Door-Type Dishwasher, Commercial | B | Any | Any |  | EECP | 5 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Water Consumption | Water consumption of dishwasher in gallons per rack | Numeric Value | [8 empty] | Must be <=1.0 | QA Checklist | Using the submitted manufacturer spec sheet validate the water consumption per pack (gallons/rack) | The water consumption must be <= 1.0 gallons/rack | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 51
0 | SWFS002 | 1 | Door-Type Dishwasher, Commercial | A | Any | Any |  | EECP | 6 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <=0.70 | QA Checklist | Using the submitted manufacturer spec sheet validate the Idle Energy Rate (kW) | The Idle Energy Rate must be <= 0.70 kW | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 21
0 | SWFS002 | 1 | Door-Type Dishwasher, Commercial | B | Any | Any |  | EECP | 7 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <=0.60 | QA Checklist | Using the submitted manufacturer spec sheet validate the Idle Energy Rate (kW) | The Idle Energy Rate must be <= 0.60 kW | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 21
0 | SWFS002 | 1 | Door-Type Dishwasher, Commercial | Any | Any | Any |  | EECP | 8 | Used or rebuilt equipment and other dishwasher types (conveyor, under-counter, flight-type) are not eligible. | Yes |  | Dishwasher Type | Drop Down List | Door Dishwasher;Conveyor Dishwasher;Under-Counter Dishwasher;Flight Dishwasher; | [7 empty] | Must be 'Door Dishwasher' | QA Checklist | Using the submitted manufacturer spec sheet validate the equipment type | The dishwasher must be listed as being a Door Dishwasher type (not Conveyor Dishwasher, Under-Counter Dishwasher, or Flight Dishwasher) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 15
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 12
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 5
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | Any | Any | Any |  | QA Checklist | 3 | Used or rebuilt equipment and other dishwasher types (conveyor, under-counter, flight-type) are not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property pending MGMT approval | 2021-09-09 | Kenny Liljestrom |  | Add | 43
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | A | Any | Any |  | EECP | 4 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Water Consumption | Water consumption of dishwasher in gallons per rack | Numeric Value | [8 empty] | Must be <=0.76 | QA Checklist | Using the submitted manufacturer spec sheet validate the water consumption per pack (gallons/rack) | The water consumption must be <= 0.76 gallons/rack | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property pending MGMT approval | 2021-09-09 | Kenny Liljestrom |  | Add | 51
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | B | Any | Any |  | EECP | 5 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Water Consumption | Water consumption of dishwasher in gallons per rack | Numeric Value | [8 empty] | Must be <=1.0 | QA Checklist | Using the submitted manufacturer spec sheet validate the water consumption per pack (gallons/rack) | The water consumption must be <= 1.0 gallons/rack | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 51
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | A | Any | Any |  | EECP | 6 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes |  | Max washing energy (kWh/rack) | Numeric Value | [8 empty] | Must be <= 0.35 | QA Checklist | Using the submitted manufacturer spec sheet validate the water consumption per pack (gallons/rack) | The water consumption must be <= 0.76 gallons/rack | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-09-09 | Kenny Liljestrom |  | Add | 29
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | B | Any | Any |  | EECP | 7 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes |  | Max washing energy (kWh/rack) | Numeric Value | [8 empty] | Must be <= 0.15 | QA Checklist | Using the submitted manufacturer spec sheet validate the water consumption per pack (gallons/rack) | The water consumption must be <= 1.0 gallons/rack | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-09-09 | Kenny Liljestrom |  | Add | 29
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | A | Any | Any |  | EECP | 8 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <=0.55 | QA Checklist | Using the submitted manufacturer spec sheet validate the Idle Energy Rate (kW) | The Idle Energy Rate must be <= 0.55 kW | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Validation rule updated for measure package revision | 2021-09-09 | Kenny Liljestrom |  | Add | 21
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | B | Any | Any |  | EECP | 9 | This measure includes new commercial low- and high-temperature door-type dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <=0.30 | QA Checklist | Using the submitted manufacturer spec sheet validate the Idle Energy Rate (kW) | The Idle Energy Rate must be <= 0.30 kW | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Validation rule updated for measure package revision | 2021-09-09 | Kenny Liljestrom |  | Add | 21
1 | SWFS002 | 2 | Door-Type Dishwasher, Commercial | Any | Any | Any |  | QA Checklist | 10 | Used or rebuilt equipment and other dishwasher types (conveyor, under-counter, flight-type) are not eligible. | Yes |  | Dishwasher Type | Drop Down List | Door Dishwasher;Conveyor Dishwasher;Under-Counter Dishwasher;Flight Dishwasher; | [7 empty] | Must be 'Door Dishwasher' | QA Checklist | Using the submitted manufacturer spec sheet validate the equipment type | The dishwasher must be listed as being a Door Dishwasher type (not Conveyor Dishwasher, Under-Counter Dishwasher, or Flight Dishwasher) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property pending MGMT approval | 2021-09-09 | Kenny Liljestrom |  | Add | 15
0 | SWFS003 | 1 | Combination Oven, Commercial | Any | Any | Any |  | EECP | 1 | Manufacturer | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-07 | Kenny Liljestrom |  | Add | 12
0 | SWFS003 | 1 | Combination Oven, Commercial | Any | Any | Any |  | EECP | 2 | Model | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-07 | Kenny Liljestrom |  | Add | 5
0 | SWFS003 | 1 | Combination Oven, Commercial | Any | Any | Any |  | EECP | 3 | Used or rebuilt equipment is not eligible. | Yes |  | New Equipment | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Collect the equipment invoice for the product | The invoice should list the equipment as new (i.e. not used, rebuilt. or leased) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 13
0 | SWFS003 | 1 | Combination Oven, Commercial | A | Any | Any |  | EECP | 4 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Production Capacity | Oven Production Capacity (lbs/hr) | Numeric Value | [8 empty] | Must be >= 100 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Production Capacity (lbs/hr) | The Oven Production Capacity (lbs/hr) Must be >= 100 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | A | Any | Any |  | EECP | 5 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Preheat Energy (watts) | Numeric Value | [8 empty] | Must be <= 1500 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Preheat Energy (watts) | The Preheat Energy (watts) Must be <= 1500 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 22
0 | SWFS003 | 1 | Combination Oven, Commercial | A | Any | Any |  | EECP | 6 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Idle Energy Rate | Oven Mode Idle Energy Rate (watts) | Numeric Value | [8 empty] | Must be <= 2000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Idle Energy Rate (watts) | The Oven Mode Idle Energy Rate (watts) Must be <= 2000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | A | Any | Any |  | EECP | 7 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Efficiency | Oven Mode Cooking Efficiency (%) | Numeric Value | [8 empty] | Must be >= 70% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Cooking Efficiency (%) | The Oven Mode Cooking Efficiency (%) Must be >= 70% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 32
0 | SWFS003 | 1 | Combination Oven, Commercial | A | Any | Any |  | EECP | 8 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Production Capacity | Steam Production Capacity (lbs/hr) | Numeric Value | [8 empty] | Must be >= 120 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Production Capacity (lbs/hr) | The Steam Production Capacity (lbs/hr) Must be >= 120 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | A | Any | Any |  | EECP | 9 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Idle Energy Rate | Steam Mode Idle Energy Rate (watts) | Numeric Value | [8 empty] | Must be <= 5000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Idle Energy Rate (watts) | The Steam Mode Idle Energy Rate (watts) Must be <= 5000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 35
0 | SWFS003 | 1 | Combination Oven, Commercial | A | Any | Any |  | EECP | 10 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Efficiency | Steam Mode Cooking Efficiency (%) | Numeric Value | [8 empty] | Must be >= 50% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Cooking Efficiency (%) | The Steam Mode Cooking Efficiency (%) Must be >= 50% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | A | Any | Any |  | EECP | 11 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Water Consumption Rate (gal/hr) | Numeric Value | [8 empty] | Must be <= 20 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Water Consumption Rate (gal/hr) | The Water Consumption Rate (gal/hr) Must be <= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 31
0 | SWFS003 | 1 | Combination Oven, Commercial | B | Any | Any |  | EECP | 12 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Production Capacity | Oven Production Capacity (lbs/hr) | Numeric Value | [8 empty] | Must be >= 125 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Production Capacity (lbs/hr) | The Oven Production Capacity (lbs/hr) Must be >= 125 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | B | Any | Any |  | EECP | 13 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Preheat Energy (watts) | Numeric Value | [8 empty] | Must be <= 2000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Preheat Energy (watts) | The Preheat Energy (watts) Must be <= 2000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 22
0 | SWFS003 | 1 | Combination Oven, Commercial | B | Any | Any |  | EECP | 14 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Idle Energy Rate | Oven Mode Idle Energy Rate (watts) | Numeric Value | [8 empty] | Must be <= 2500 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Idle Energy Rate (watts) | The Oven Mode Idle Energy Rate (watts) Must be <= 2500 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | B | Any | Any |  | EECP | 15 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Efficiency | Oven Mode Cooking Efficiency (%) | Numeric Value | [8 empty] | Must be >= 70% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Cooking Efficiency (%) | The Oven Mode Cooking Efficiency (%) Must be >= 70% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Configured as 71%, needs to be updated to 70% | 2021-06-07 | Kenny Liljestrom |  | Add | 32
0 | SWFS003 | 1 | Combination Oven, Commercial | B | Any | Any |  | EECP | 16 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Production Capacity | Steam Production Capacity (lbs/hr) | Numeric Value | [8 empty] | Must be >= 200 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Production Capacity (lbs/hr) | The Steam Production Capacity (lbs/hr) Must be >= 200 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | B | Any | Any |  | EECP | 17 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Idle Energy Rate | Steam Mode Idle Energy Rate (watts) | Numeric Value | [8 empty] | Must be <= 6000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Idle Energy Rate (watts) | The Steam Mode Idle Energy Rate (watts) Must be <= 6000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 35
0 | SWFS003 | 1 | Combination Oven, Commercial | B | Any | Any |  | EECP | 18 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Efficiency | Steam Mode Cooking Efficiency (%) | Numeric Value | [8 empty] | Must be >= 50% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Cooking Efficiency (%) | The Steam Mode Cooking Efficiency (%) Must be >= 50% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Configured as 51%, needs to be updated to 50% | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | B | Any | Any |  | EECP | 19 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Water Consumption Rate (gal/hr) | Numeric Value | [8 empty] | Must be <= 25 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Water Consumption Rate (gal/hr) | The Water Consumption Rate (gal/hr) Must be <= 25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 31
0 | SWFS003 | 1 | Combination Oven, Commercial | C | Any | Any |  | EECP | 20 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Production Capacity | Oven Production Capacity (lbs/hr) | Numeric Value | [8 empty] | Must be >= 325 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Production Capacity (lbs/hr) | The Oven Production Capacity (lbs/hr) Must be >= 325 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | C | Any | Any |  | EECP | 21 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Preheat Energy (watts) | Numeric Value | [8 empty] | Must be <= 3000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Preheat Energy (watts) | The Preheat Energy (watts) Must be <= 3000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 22
0 | SWFS003 | 1 | Combination Oven, Commercial | C | Any | Any |  | EECP | 22 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Idle Energy Rate | Oven Mode Idle Energy Rate (watts) | Numeric Value | [8 empty] | Must be <= 4000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Idle Energy Rate (watts) | The Oven Mode Idle Energy Rate (watts) Must be <= 4000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | C | Any | Any |  | EECP | 23 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Efficiency | Oven Mode Cooking Efficiency (%) | Numeric Value | [8 empty] | Must be >= 70% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Cooking Efficiency (%) | The Oven Mode Cooking Efficiency (%) Must be >= 70% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 32
0 | SWFS003 | 1 | Combination Oven, Commercial | C | Any | Any |  | EECP | 24 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Production Capacity | Steam Production Capacity (lbs/hr) | Numeric Value | [8 empty] | Must be >= 400 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Production Capacity (lbs/hr) | The Steam Production Capacity (lbs/hr) Must be >= 400 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | C | Any | Any |  | EECP | 25 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Idle Energy Rate | Steam Mode Idle Energy Rate (watts) | Numeric Value | [8 empty] | Must be <= 9000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Idle Energy Rate (watts) | The Steam Mode Idle Energy Rate (watts) Must be <= 9000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 35
0 | SWFS003 | 1 | Combination Oven, Commercial | C | Any | Any |  | EECP | 26 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Efficiency | Steam Mode Cooking Efficiency (%) | Numeric Value | [8 empty] | Must be >= 50% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Cooking Efficiency (%) | The Steam Mode Cooking Efficiency (%) Must be >= 50% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | C | Any | Any |  | EECP | 27 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Water Consumption Rate (gal/hr) | Numeric Value | [8 empty] | Must be <= 30 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Water Consumption Rate (gal/hr) | The Water Consumption Rate (gal/hr) Must be <= 30 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 31
0 | SWFS003 | 1 | Combination Oven, Commercial | D | Any | Any |  | EECP | 28 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Production Capacity | Oven Production Capacity (lbs/hr) | Numeric Value | [8 empty] | Must be >= 100 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Production Capacity (lbs/hr) | The Oven Production Capacity (lbs/hr) Must be >= 100 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | D | Any | Any |  | EECP | 29 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Preheat Energy (Btu/hr) | Numeric Value | [8 empty] | Must be <= 13000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Preheat Energy (Btu/hr) | The Preheat Energy (Btu/hr) Must be <= 13000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 23
0 | SWFS003 | 1 | Combination Oven, Commercial | D | Any | Any |  | EECP | 30 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Idle Energy Rate | Oven Mode Idle Energy Rate (Btu/hr) | Numeric Value | [8 empty] | Must be <= 8000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Idle Energy Rate (Btu/hr) | The Oven Mode Idle Energy Rate (Btu/hr) Must be <= 8000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 35
0 | SWFS003 | 1 | Combination Oven, Commercial | D | Any | Any |  | EECP | 31 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Efficiency | Oven Mode Cooking Efficiency (%) | Numeric Value | [8 empty] | Must be >= 44% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Cooking Efficiency (%) | The Oven Mode Cooking Efficiency (%) Must be >= 44% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 32
0 | SWFS003 | 1 | Combination Oven, Commercial | D | Any | Any |  | EECP | 32 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Production Capacity | Steam Production Capacity (lbs/hr) | Numeric Value | [8 empty] | Must be >= 120 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Production Capacity (lbs/hr) | The Steam Production Capacity (lbs/hr) Must be >= 120 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | D | Any | Any |  | EECP | 33 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Idle Energy Rate | Steam Mode Idle Energy Rate (Btu/hr) | Numeric Value | [8 empty] | Must be <= 15000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Idle Energy Rate (Btu/hr) | The Steam Mode Idle Energy Rate (Btu/hr) Must be <= 15000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 36
0 | SWFS003 | 1 | Combination Oven, Commercial | D | Any | Any |  | EECP | 34 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Efficiency | Steam Mode Cooking Efficiency (%) | Numeric Value | [8 empty] | Must be >= 38% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Cooking Efficiency (%) | The Steam Mode Cooking Efficiency (%) Must be >= 38% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | D | Any | Any |  | EECP | 35 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Water Consumption Rate (gal/hr) | Numeric Value | [8 empty] | Must be <= 18 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Water Consumption Rate (gal/hr) | The Water Consumption Rate (gal/hr) Must be <= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 31
0 | SWFS003 | 1 | Combination Oven, Commercial | E | Any | Any |  | EECP | 36 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Production Capacity | Oven Production Capacity (lbs/hr) | Numeric Value | [8 empty] | Must be >= 125 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Production Capacity (lbs/hr) | The Oven Production Capacity (lbs/hr) Must be >= 125 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | E | Any | Any |  | EECP | 37 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Preheat Energy (Btu/hr) | Numeric Value | [8 empty] | Must be <= 16000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Preheat Energy (Btu/hr) | The Preheat Energy (Btu/hr) Must be <= 16000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 23
0 | SWFS003 | 1 | Combination Oven, Commercial | E | Any | Any |  | EECP | 38 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Idle Energy Rate | Oven Mode Idle Energy Rate (Btu/hr) | Numeric Value | [8 empty] | Must be <= 10000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Idle Energy Rate (Btu/hr) | The Oven Mode Idle Energy Rate (Btu/hr) Must be <= 10000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 35
0 | SWFS003 | 1 | Combination Oven, Commercial | E | Any | Any |  | EECP | 39 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Efficiency | Oven Mode Cooking Efficiency (%) | Numeric Value | [8 empty] | Must be >= 44% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Cooking Efficiency (%) | The Oven Mode Cooking Efficiency (%) Must be >= 44% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 32
0 | SWFS003 | 1 | Combination Oven, Commercial | E | Any | Any |  | EECP | 40 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Production Capacity | Steam Production Capacity (lbs/hr) | Numeric Value | [8 empty] | Must be >= 200 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Production Capacity (lbs/hr) | The Steam Production Capacity (lbs/hr) Must be >= 200 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | E | Any | Any |  | EECP | 41 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Idle Energy Rate | Steam Mode Idle Energy Rate (Btu/hr) | Numeric Value | [8 empty] | Must be <= 18000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Idle Energy Rate (Btu/hr) | The Steam Mode Idle Energy Rate (Btu/hr) Must be <= 18000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 36
0 | SWFS003 | 1 | Combination Oven, Commercial | E | Any | Any |  | EECP | 42 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Efficiency | Steam Mode Cooking Efficiency (%) | Numeric Value | [8 empty] | Must be >= 38% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Cooking Efficiency (%) | The Steam Mode Cooking Efficiency (%) Must be >= 38% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | E | Any | Any |  | EECP | 43 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Water Consumption Rate (gal/hr) | Numeric Value | [8 empty] | Must be <= 30 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Water Consumption Rate (gal/hr) | The Water Consumption Rate (gal/hr) Must be <= 30 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 31
0 | SWFS003 | 1 | Combination Oven, Commercial | F | Any | Any |  | EECP | 44 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Production Capacity | Oven Production Capacity (lbs/hr) | Numeric Value | [8 empty] | Must be >= 325 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Production Capacity (lbs/hr) | The Oven Production Capacity (lbs/hr) Must be >= 325 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | F | Any | Any |  | EECP | 45 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Preheat Energy (Btu/hr) | Numeric Value | [8 empty] | Must be <= 24000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Preheat Energy (Btu/hr) | The Preheat Energy (Btu/hr) Must be <= 24000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 23
0 | SWFS003 | 1 | Combination Oven, Commercial | F | Any | Any |  | EECP | 46 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Idle Energy Rate | Oven Mode Idle Energy Rate (Btu/hr) | Numeric Value | [8 empty] | Must be <= 16000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Idle Energy Rate (Btu/hr) | The Oven Mode Idle Energy Rate (Btu/hr) Must be <= 16000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 35
0 | SWFS003 | 1 | Combination Oven, Commercial | F | Any | Any |  | EECP | 47 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Oven Efficiency | Oven Mode Cooking Efficiency (%) | Numeric Value | [8 empty] | Must be >= 44% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Oven Mode Cooking Efficiency (%) | The Oven Mode Cooking Efficiency (%) Must be >= 44% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 32
0 | SWFS003 | 1 | Combination Oven, Commercial | F | Any | Any |  | EECP | 48 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Production Capacity | Steam Production Capacity (lbs/hr) | Numeric Value | [8 empty] | Must be >= 400 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Production Capacity (lbs/hr) | The Steam Production Capacity (lbs/hr) Must be >= 400 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS003 | 1 | Combination Oven, Commercial | F | Any | Any |  | EECP | 49 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Idle Energy Rate | Steam Mode Idle Energy Rate (Btu/hr) | Numeric Value | [8 empty] | Must be <= 28000 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Idle Energy Rate (Btu/hr) | The Steam Mode Idle Energy Rate (Btu/hr) Must be <= 28000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 36
0 | SWFS003 | 1 | Combination Oven, Commercial | F | Any | Any |  | EECP | 50 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes | Steam Efficiency | Steam Mode Cooking Efficiency (%) | Numeric Value | [8 empty] | Must be >= 38% | QA Checklist | Using the submitted manufacturer spec sheet, validate the Steam Mode Cooking Efficiency (%) | The Steam Mode Cooking Efficiency (%) Must be >= 38% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS003 | 1 | Combination Oven, Commercial | F | Any | Any |  | EECP | 51 | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | Yes |  | Water Consumption Rate (gal/hr) | Numeric Value | [8 empty] | Must be <= 60 | QA Checklist | Using the submitted manufacturer spec sheet, validate the Water Consumption Rate (gal/hr) | The Water Consumption Rate (gal/hr) Must be <= 60 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 31
1 | SWFS004 | 1 | Griddle, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-11 | Kenny Liljestrom |  | Add | 12
1 | SWFS004 | 1 | Griddle, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-11 | Kenny Liljestrom |  | Add | 5
1 | SWFS004 | 1 | Griddle, Commercial | Any | Any | Any |  | EECP | 3 | Double-sided griddles and used or rebuilt equipment are not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
1 | SWFS004 | 1 | Griddle, Commercial | Any | Any | Any |  | EECP | 4 | Double-sided griddles and used or rebuilt equipment are not eligible. | Yes |  | Is the griddle double-sided? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | QA Checklist | Cross check make and model number with EnergyStar database or specification sheet | The unit must not be listed as being 'Double Sided' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 28
1 | SWFS004 | 1 | Griddle, Commercial | Any | Any | Any |  | EECP | 5 | This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | Energy Star Qualified | ENERGY STAR Qualified? | Drop Down List | Yes;No | [8 empty] | QA Checklist | Use the EnergyStar database and compare the listed make and model in EECP to the list | The database needs to have the make and model listed in EECP as being EnergyStar qualified; if not, criteria below must be met | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 22
1 | SWFS004 | 1 | Griddle, Commercial | A | Any | Any |  | EECP | 6 | This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | Size | Production Capacity (lb/hr) | Numeric Value | [8 empty] | If 'Energy Star Qualified' is 'No' then Must be >=49 | QA Checklist | Use the manufacturer specification sheet to capture the production capacity of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be >= 49 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 27
1 | SWFS004 | 1 | Griddle, Commercial | A | Any | Any |  | EECP | 7 | This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (W/ft2/hr) | Numeric Value | [8 empty] | If 'Energy Star Qualified' is 'No' then Must be <= 293 | QA Checklist | Use the manufacturer specification sheet to capture the maximum idle energy rate (W/ft2-hr) of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be <= 293 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 31
1 | SWFS004 | 1 | Griddle, Commercial | A | Any | Any |  | EECP | 8 | This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | EFFICIENCY | Min. Cooking Energy Efficiency (%) | Numeric Value | [8 empty] | If 'Energy Star Qualified' is 'No' then Must be >= 75% | QA Checklist | Use the manufacturer specification sheet to capture the minimum cooking efficiency (%) of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be >= 75% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 34
1 | SWFS004 | 1 | Griddle, Commercial | B | Any | Any |  | EECP | 9 | This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | Size | Production Capacity (lb/hr) | Numeric Value | [8 empty] | If 'Energy Star Qualified' is 'No' then Must be >=49.2 | QA Checklist | Use the manufacturer specification sheet to capture the production capacity (lb/hr) of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be >= 49.2 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 27
1 | SWFS004 | 1 | Griddle, Commercial | B | Any | Any |  | EECP | 10 | This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (Btu/hr) | Numeric Value | [8 empty] | If 'Energy Star Qualified' is 'No' then Must be <= 2068 | QA Checklist | Use the manufacturer specification sheet to capture the maximum idle energy rate (Btu/hr) of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be <= 2068 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 29
1 | SWFS004 | 1 | Griddle, Commercial | B | Any | Any |  | EECP | 11 | This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | Yes | EFFICIENCY | Min. Cooking Energy Efficiency (%) | Numeric Value | [8 empty] | If 'Energy Star Qualified' is 'No' then Must be >= 46% | QA Checklist | Use the manufacturer specification sheet to capture the minimum cooking efficiency (%) of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be >= 46% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-11 | Kenny Liljestrom |  | Add | 34
0 | SWFS005 | 2 | Steamer, Commercial | Any | Any | Any |  | EECP | 1 | Manufacturer | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-07 | Kenny Liljestrom |  | Add | 12
0 | SWFS005 | 2 | Steamer, Commercial | Any | Any | Any |  | EECP | 2 | Model | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-07 | Kenny Liljestrom |  | Add | 5
0 | SWFS005 | 2 | Steamer, Commercial | Any | Any | Any |  | EECP | 3 | Measure Description | Yes |  | Is Equipment Gas or Electric? | Drop Down List | Gas;Electric; | [8 empty] | - | - | - | - | - | - | Not configured in original upload | 2021-06-07 | Kenny Liljestrom | Removed, measure description clarifies what is being installed | Add | 30
0 | SWFS005 | 2 | Steamer, Commercial | Any | Any | Any |  | EECP | 4 | Used or rebuilt equipment is not eligible. | Yes |  | New Equipment | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Collect the equipment invoice for the product | The invoice should list the equipment as new (i.e. not used, rebuilt. or leased) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 13
0 | SWFS005 | 2 | Steamer, Commercial | Any | Any | Any |  | EECP | 5 | New commercial steam cookers must meet the ENERGY STAR Program Requirements for Commercial Steam Cookers, Version 1.2 or the specification in the Measure Case Description. | Yes | Energy Star Qualified | ENERGY STAR Qualified | Drop Down List | Yes;No; | [8 empty] | QA Checklist | Use the EnergyStar database and compare the listed make and model in EECP to the list | The database needs to have the make and model listed in EECP as being EnergyStar qualified; if not, criteria below must be met | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 21
0 | SWFS005 | 2 | Steamer, Commercial | Any | Any | Any |  | EECP | 6 | New commercial steam cookers must meet the ENERGY STAR Program Requirements for Commercial Steam Cookers, Version 1.2 or the specification in the Measure Case Description. | Yes | Size | Pan Capacity | Drop Down List | 3 Pan;4 Pan;5 Pan;6+ Pan; | [8 empty] | QA Checklist | Use the manufacturer specification sheet to capture the number of pans of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be 3, 4, 5, or 6 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 12
0 | SWFS005 | 2 | Steamer, Commercial | A | Any | Any |  | EECP | 7 | New commercial steam cookers must meet the ENERGY STAR Program Requirements for Commercial Steam Cookers, Version 1.2 or the specification in the Measure Case Description. | Yes | EFFICIENCY | Min. Cooking Energy Efficiency (%) | Numeric Value | [8 empty] | If 'Energy Star Qualified' is No then make active Must be >=50% | QA Checklist | If the product is not ENERGYSTAR listed, use the manufacturer specification sheet to capture the minimum cooking efficiency (%) of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be >= 50% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS005 | 2 | Steamer, Commercial | A | Any | Any |  | EECP | 8 | New commercial steam cookers must meet the ENERGY STAR Program Requirements for Commercial Steam Cookers, Version 1.2 or the specification in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (W) | Numeric Value | [8 empty] | If 'Pan Capacity' is '3 Pan' then Must be <= 800 If 'Pan Capacity' is '4 Pan' then Must be <= 530 If 'Pan Capacity' is '5 Pan' then Must be <= 670 If 'Pan Capacity' is '6+ Pan' then Must be <= 800 | QA Checklist | If the product is not ENERGYSTAR listed, use the manufacturer specification sheet to capture the max idle energy rate (W) of the unit | If 'Pan Capacity' is '3 Pan' then must be <= 800 W If 'Pan Capacity' is '4 Pan' then must be <= 530 W If 'Pan Capacity' is '5 Pan' then must be <= 670 W If 'Pan Capacity' is '6+ Pan' then must be <= 800 W | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 24
0 | SWFS005 | 2 | Steamer, Commercial | B | Any | Any |  | EECP | 9 | New commercial steam cookers must meet the ENERGY STAR Program Requirements for Commercial Steam Cookers, Version 1.2 or the specification in the Measure Case Description. | Yes | EFFICIENCY | Min. Cooking Energy Efficiency (%) | Numeric Value | [8 empty] | If 'Energy Star Qualified' is No Must be >=38% | QA Checklist | If the product is not ENERGYSTAR listed, use the manufacturer specification sheet to capture the minimum cooking efficiency (%) of the unit | The value listed in EECP should match what is listed in the manufacturer specification sheet; the value needs to be >= 38% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 34
0 | SWFS005 | 2 | Steamer, Commercial | B | Any | Any |  | EECP | 10 | New commercial steam cookers must meet the ENERGY STAR Program Requirements for Commercial Steam Cookers, Version 1.2 or the specification in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (Btu/hr) | Numeric Value | [8 empty] | If 'Pan Capacity' is '3 Pan' then Must be <= 6250 If 'Pan Capacity' is '4 Pan' then Must be <= 8350 If 'Pan Capacity' is '5 Pan' then Must be <= 10400 If 'Pan Capacity' is '6+ Pan' then Must be <= 12500 | QA Checklist | If the product is not ENERGYSTAR listed, use the manufacturer specification sheet to capture the max idle energy rate (W) of the unit | If 'Pan Capacity' is '3 Pan' then Must be <= 6250 Btu/hr If 'Pan Capacity' is '4 Pan' then Must be <= 8350 Btu/hr If 'Pan Capacity' is '5 Pan' then Must be <= 10400 Btu/hr If 'Pan Capacity' is '6+ Pan' then Must be <= 12500 Btu/hr | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 29
1 | SWFS006 | 1 | Ice Machine, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate of the top section of the ice machine showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
1 | SWFS006 | 1 | Ice Machine, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate of the top section of the ice machine showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
1 | SWFS006 | 1 | Ice Machine, Commercial | Any | Any | Any |  | EECP | 3 | Measure Description | Yes |  | Does the ice machine match the measure case equipment type? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | - | - | - | - | - | - | Not configured in original upload | 2021-05-28 | Kenny Liljestrom | Removed, measure description clarifies what is being installed | Add | 59
1 | SWFS006 | 1 | Ice Machine, Commercial | Any | Any | Any |  | EECP | 4 | Water-cooled ice machines and used or rebuilt equipment are not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | Any | Any | Any |  | EECP | 5 | Program qualifying ice machines are defined by equipment type and daily ice harvest rate. The efficiency specifications must meet the requirements listed in the Measure Case Description for batch and continuous machines, per the ENERGY STAR V3.0 Program Requirements for Automatic Commercial Ice Makers. | Yes |  | ENERGY STAR Qualified | Drop Down List | Yes;No; | [7 empty] | If 'No', make available Harvest Rate and Energy Use | QA Checklist | Use the EnergyStar database and compare the listed make and model in EECP to the list | The database needs to have the make and model listed in EECP as being EnergyStar qualified; if not, criteria below must be met | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-06-07 | Kenny Liljestrom |  | Add | 21
1 | SWFS006 | 1 | Ice Machine, Commercial | Any | Any | Any |  | EECP | 6 | The entire AHRI-tested ice making system must be purchased. Remote machines must be purchased with qualifying remote condenser or remote condenser/compressor unit. | Yes | Entire AHRI System Purchased | Was entire AHRI-tested ice making system purchased? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 51
1 | SWFS006 | 1 | Ice Machine, Commercial | Any | Any | Any |  | EECP | 7 | Only air-cooled machines (self-contained, icemaker heads, or remote condensing) are eligible. Water-cooled ice machines and used or rebuilt equipment are not eligible. | Yes | Air Cooled Unit | Is the unit an air cooled ice maker? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | Using the submitted manufacturer spec sheet validate if the unit is air-cooled or water cooled | The unit must be listed as being air cooled | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 36
1 | SWFS006 | 1 | Ice Machine, Commercial | Any | Any | Any |  | EECP | 8 | Required for defining Energy Use | Yes | Ice Machine Production Type | Ice making system type | Drop Down List | Batch;Continuous; | [8 empty] | QA Checklist | Using the submitted manufacturer spec sheet validate the ice system making type (batch or continuous) | There are no validation criteria for this property | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 22
1 | SWFS006 | 1 | Ice Machine, Commercial | A | Any | Any |  | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [8 empty] | Must be < 110 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be < 110 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | B | Any | Any |  | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [8 empty] | Must be >= 110 and < 200 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be >= 110 and < 200 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | C | Any | Any |  | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [8 empty] | Must be >= 200 and < 4000 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be >= 200 and < 4000 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | D | Any | Any |  | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [8 empty] | Must be < 300 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be < 300 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | E | Any | Any |  | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [8 empty] | Must be >= 300 and < 800 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be >= 300 and < 800 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | F | Any | Any |  | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [8 empty] | Must be >= 800 and < 1500 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be >= 800 and < 1500 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | G | Any | Any |  | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [8 empty] | Must be >= 1500 and < 4000 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be >= 1500 and < 4000 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | H | Any | Any |  | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [8 empty] | Must be < 987 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be < 987 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | I | Any | Any |  | EECP | 9 | Required for defining Energy Use | Yes | Production Per Day | Production Per Day (lbs) | Numeric Value | [8 empty] | Must be >= 988 and < 4000 | QA Checklist | Using the submitted manufacturer spec sheet validate the Production Per Day (lbs) | The Production Per Day (lbs) Must be >= 988 and < 4000 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 24
1 | SWFS006 | 1 | Ice Machine, Commercial | A | Any | Any |  | EECP | 10 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [8 empty] | If System Type is 'Batch' must be <= 12.57 - 0.0399 x Production per Day | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | If System Type is 'Batch' must be <= 12.57 - 0.0399 x Production per Day | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | B | Any | Any |  | EECP | 11 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [8 empty] | If System Type is 'Batch' must be <=10.56 - 0.0215 x Production per Day | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | The Maximum Daily Energy Use (kWh/100 lbs. ice) If System Type is 'Batch' must be <=10.56 - 0.0215 x Production per Day | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | C | Any | Any |  | EECP | 12 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [8 empty] | If System Type is 'Batch' and Production per Day is >= 200 and <= 4000 then must be <= 6.25 'If System Type is 'Continuous' and Production per Day is >= 200 and <= 700 then must be <= 8.24 - 0.005429 x Production per Day 'If System Type is 'Continuous' and Production per Day is >= 700 and <= 4000 then must be <= 4.44 | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | The Maximum Daily Energy Use (kWh/100 lbs. ice) If System Type is 'Batch' and Production per Day is >= 200 and <= 4000 then must be <= 6.25 'If System Type is 'Continuous' and Production per Day is >= 200 and <= 700 then must be <= 8.24 - 0.005429 x Production per Day 'If System Type is 'Continuous' and Production per Day is >= 700 and <= 4000 then must be <= 4.44 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | D | Any | Any |  | EECP | 13 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [8 empty] | If System Type is 'Batch' then must be <= 9.20 - 0.01134 x Production per Day 'If System Type is 'Continuous' then must be <= 7.90 - 0.005409 x Production per Day | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | The Maximum Daily Energy Use (kWh/100 lbs. ice) If System Type is 'Batch' then must be <= 9.20 - 0.01134 x Production per Day 'If System Type is 'Continuous' then must be <= 7.90 - 0.005409 x Production per Day | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | E | Any | Any |  | EECP | 14 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [8 empty] | If System Type is 'Batch' then must be <= 6.49-0.0023 x Production per Day 'If System Type is 'Continuous' and Production per Day < 310 then must be <= 7.90-0.005409 x Production per Day 'If System Type is 'Continuous' and Production per Day >= 310 then must be <= 7.08-0.002752 x Production per Day | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | The Maximum Daily Energy Use (kWh/100 lbs. ice) If System Type is 'Batch' then must be <= 6.49-0.0023 x Production per Day 'If System Type is 'Continuous' and Production per Day < 310 then must be <= 7.90-0.005409 x Production per Day 'If System Type is 'Continuous' and Production per Day >= 310 then must be <= 7.08-0.002752 x Production per Day | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | F | Any | Any |  | EECP | 15 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [8 empty] | If System Type is 'Batch' then must be <=5.11-0.00058 x Production per Day 'If System Type is 'Continuous' and Production per Day < 820 then must be <= 7.08-0.002752 x Production per Day 'If System Type is 'Continuous' and Production per Day >= 820 then must be <= 4.82 | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | The Maximum Daily Energy Use (kWh/100 lbs. ice) If System Type is 'Batch' then must be <=5.11-0.00058 x Production per Day 'If System Type is 'Continuous' and Production per Day < 820 then must be <= 7.08-0.002752 x Production per Day 'If System Type is 'Continuous' and Production per Day >= 820 then must be <= 4.82 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | G | Any | Any |  | EECP | 16 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [8 empty] | If System Type is 'Batch' then must be <= 4.24 'If System Type is 'Continuous' then must be <= 4.82 | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | The Maximum Daily Energy Use (kWh/100 lbs. ice) If System Type is 'Batch' then must be <= 4.24 'If System Type is 'Continuous' then must be <= 4.82 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | H | Any | Any |  | EECP | 17 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [8 empty] | If System Type is 'Batch' then must be <= 7.17-0.00308 x Production per Day 'If System Type is 'Continuous' and Production per Day < 800 then must be <= 7.76-0.00464 x Production per Day 'If System Type is 'Continuous' and Production per Day >= 800 then must be <= 4.05 | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | The Maximum Daily Energy Use (kWh/100 lbs. ice) If System Type is 'Batch' then must be <= 7.17-0.00308 x Production per Day 'If System Type is 'Continuous' and Production per Day < 800 then must be <= 7.76-0.00464 x Production per Day 'If System Type is 'Continuous' and Production per Day >= 800 then must be <= 4.05 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | I | Any | Any |  | EECP | 18 | The ice machine must meet the energy efficiency specifications listed the Measure Case Description. | Yes | Daily Energy Use | Maximum Daily Energy Use (kWh/100 lbs. ice) | Numeric Value | [8 empty] | If System Type is 'Batch' then must be <= 4.13 'If System Type is 'Continuous' then must be <= 4.05 | QA Checklist | Using the submitted manufacturer spec sheet validate the Maximum Daily Energy Use (kWh/100 lbs. ice) | The Maximum Daily Energy Use (kWh/100 lbs. ice) If System Type is 'Batch' then must be <= 4.13 'If System Type is 'Continuous' then must be <= 4.05 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
1 | SWFS006 | 1 | Ice Machine, Commercial | A | Any | Any |  | EECP | 19 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [8 empty] | If 'System Type' is Batch then <=25 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=25 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
1 | SWFS006 | 1 | Ice Machine, Commercial | B | Any | Any |  | EECP | 20 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [8 empty] | If 'System Type' is Batch then <=25 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=25 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
1 | SWFS006 | 1 | Ice Machine, Commercial | C | Any | Any |  | EECP | 21 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [8 empty] | If 'System Type' is Batch then <=25 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=25 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
1 | SWFS006 | 1 | Ice Machine, Commercial | D | Any | Any |  | EECP | 22 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [8 empty] | If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
1 | SWFS006 | 1 | Ice Machine, Commercial | E | Any | Any |  | EECP | 23 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [8 empty] | If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
1 | SWFS006 | 1 | Ice Machine, Commercial | F | Any | Any |  | EECP | 24 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [8 empty] | If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
1 | SWFS006 | 1 | Ice Machine, Commercial | G | Any | Any |  | EECP | 25 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [8 empty] | If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
1 | SWFS006 | 1 | Ice Machine, Commercial | H | Any | Any |  | EECP | 26 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [8 empty] | If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
1 | SWFS006 | 1 | Ice Machine, Commercial | I | Any | Any |  | EECP | 27 | Max Daily Potable Water Use Limit (gal/100 lbs of ice) | Yes | Max Daily Potable Water Use | Max Daily Potable Water Use Limit (gal/100 lbs. ice) | Numeric Value | [8 empty] | If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Daily Potable Water Use Limit (gal/100 lbs. ice) | The Max Daily Potable Water Use Limit (gal/100 lbs. ice) If 'System Type' is Batch then <=20 If 'System Type' is Continuous then <=15 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 52
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | Any | Any | Any |  | EECP | 3 | Any cabinets considered in this measure must have an electric resistance heating element, passive holding cabinets with no heating elements are not eligible. | Yes | Gas_Electric | Is Equipment Gas or Electric? | Drop Down List | Gas;Electric | [7 empty] | Must be Electric | QA Checklist | Using the submitted manufacturer spec sheet validate the fuel source type (electric or gas) | The equipment must be electric | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 29
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | Any | Any | Any |  | EECP | 4 | Used or rebuilt equipment are not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | A | Any | Any |  | EECP | 5 | Qualifying cabinets must not exceed the maximum idle energy rate of 25 W/ft3 for full-size cabinets and 35 W/ft3 for half-size cabinets, in accordance with the American Society for Testing and Materials (ASTM) Standard Test Method for the Performance of Hot Food Holding Cabinets (F2140). | Yes | Idle Energy Rate | Max Idle Energy Rate (watts/ft3) | Numeric Value | [8 empty] | Must be <= 25 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Idle Energy Rate (watts/ft3) | The Max Idle Energy Rate (watts/ft3) Must be <= 25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 32
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | B | Any | Any |  | EECP | 6 | Qualifying cabinets must not exceed the maximum idle energy rate of 25 W/ft3 for full-size cabinets and 35 W/ft3 for half-size cabinets, in accordance with the American Society for Testing and Materials (ASTM) Standard Test Method for the Performance of Hot Food Holding Cabinets (F2140). | Yes | Idle Energy Rate | Max Idle Energy Rate (watts/ft3) | Numeric Value | [8 empty] | Must be <= 35 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Idle Energy Rate (watts/ft3) | The Max Idle Energy Rate (watts/ft3) Must be <= 35 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 32
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | A | Any | Any |  | EECP | 7 | This measure includes new full-size (≥ 15 ft3) and half-size (< 15 ft3) insulated food holding cabinets. | Yes | Size | Insulated Holding Cabinet Size (square feet) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Insulated Holding Cabinet Size (square feet) | The Insulated Holding Cabinet Size (square feet) Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 45
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | B | Any | Any |  | EECP | 8 | This measure includes new full-size (≥ 15 ft3) and half-size (< 15 ft3) insulated food holding cabinets. | Yes | Size | Insulated Holding Cabinet Size (square feet) | Numeric Value | [8 empty] | Must be < 15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Insulated Holding Cabinet Size (square feet) | The Insulated Holding Cabinet Size (square feet) Must be < 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 45
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | Any | Any | Any |  | EECP | 9 | Eligible holding cabinets must be listed on the Food Service Technology Center (FSTC) qualified product list (https://fishnick.com/saveenergy/rebates/). | Yes | FSTC Listed | Is the installed holding cabinet listed on the Food Service Technology Center (FSTC) qualified product list (https://fishnick.com/saveenergy/rebates/)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Using the rebate site below, determine if the product is listed as being a qualified unit https://fishnick.com/saveenergy/rebates/ | The product must be listed as a qualified product on the fishnick website | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 151
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | Any | Any | Any |  | EECP | 10 | All measures must be electric hot food holding cabinets that are fully insulated (i.e., on all sides) and have solid or transparent doors designed to maintain the temperature of hot food that has been cooked using a separate appliance. This measure does not include cook-and-hold or retherm equipment. | Yes |  | Holding cabinet fully insulated (i.e., on all sides) and has solid or transparent doors? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | When inspecting the holding cabinet, check to see if the cabinet has any glass or transparent (see through) doors or sides | The holding cabinet must be fully insulated with no glass or transparent doors or sides | QA Checklist | Use the manufacturer spec sheet to check to see if the cabinet has any glass or transparent (see through) doors or sides | The holding cabinet must be fully insulated with no glass or transparent doors or sides | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 88
0 | SWFS007 | 2 | Insulated Hot Food Holding Cabinet | Any | Any | Any |  | EECP | 10 | All measures must be electric hot food holding cabinets that are fully insulated (i.e., on all sides) and have solid or transparent doors designed to maintain the temperature of hot food that has been cooked using a separate appliance. This measure does not include cook-and-hold or retherm equipment. | Yes |  | Is this a cook-and-hold retherm equipment? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet to determine if the holding cabinet is classified as a cook-and-hold retherm equipment | The cook-and-hold retherm type of cabinet is not eligible for rebate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 42
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 12
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 5
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | Any | Any | Any |  | EECP | 3 | Any cabinets considered in this measure must have an electric resistance heating element, passive holding cabinets with no heating elements are not eligible. | Yes | Gas_Electric | Is Equipment Gas or Electric? | Drop Down List | Gas;Electric | [7 empty] | Must be Electric | QA Checklist | Using the submitted manufacturer spec sheet validate the fuel source type (electric or gas) | The equipment must be electric | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 29
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | Any | Any | Any |  | QA Checklist | 4 | Used or rebuilt equipment are not eligible. | Yes | New Equipment | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 43
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | A | Any | Any |  | EECP | 5 | Qualifying cabinets must not exceed the maximum idle energy rate of 25 W/ft3 for full-size cabinets and 35 W/ft3 for half-size cabinets, in accordance with the American Society for Testing and Materials (ASTM) Standard Test Method for the Performance of Hot Food Holding Cabinets (F2140). | Yes | Idle Energy Rate | Max Idle Energy Rate (watts/ft3) | Numeric Value | [8 empty] | Must be <= 12 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Idle Energy Rate (watts/ft3) | The Max Idle Energy Rate (watts/ft3) Must be <= 12 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-09-09 | Kenny Liljestrom |  | Add | 32
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | B | Any | Any |  | EECP | 6 | Qualifying cabinets must not exceed the maximum idle energy rate of 25 W/ft3 for full-size cabinets and 35 W/ft3 for half-size cabinets, in accordance with the American Society for Testing and Materials (ASTM) Standard Test Method for the Performance of Hot Food Holding Cabinets (F2140). | Yes | Idle Energy Rate | Max Idle Energy Rate (watts/ft3) | Numeric Value | [8 empty] | Must be <= 18 | QA Checklist | Using the submitted manufacturer spec sheet validate the Max Idle Energy Rate (watts/ft3) | The Max Idle Energy Rate (watts/ft3) Must be <= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-09-09 | Kenny Liljestrom |  | Add | 32
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | A | Any | Any |  | EECP | 7 | This measure includes new full-size (≥ 15 ft3) and half-size (< 15 ft3) insulated food holding cabinets. | Yes | Size | Insulated Holding Cabinet Size (square feet) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Insulated Holding Cabinet Size (square feet) | The Insulated Holding Cabinet Size (square feet) Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 45
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | B | Any | Any |  | EECP | 8 | This measure includes new full-size (≥ 15 ft3) and half-size (< 15 ft3) insulated food holding cabinets. | Yes | Size | Insulated Holding Cabinet Size (square feet) | Numeric Value | [8 empty] | Must be < 15 | QA Checklist | Using the submitted manufacturer spec sheet validate the Insulated Holding Cabinet Size (square feet) | The Insulated Holding Cabinet Size (square feet) Must be < 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 45
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | Any | Any | Any |  | EECP | 9 | Eligible holding cabinets must be listed on the Food Service Technology Center (FSTC) qualified product list (https://fishnick.com/saveenergy/rebates/). | Yes | FSTC Listed | Is the installed holding cabinet listed on the Food Service Technology Center (FSTC) qualified product list (https://fishnick.com/saveenergy/rebates/)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Using the rebate site below, determine if the product is listed as being a qualified unit https://fishnick.com/saveenergy/rebates/ | The product must be listed as a qualified product on the fishnick website | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 151
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | Any | Any | Any |  | EECP | 10 | All measures must be electric hot food holding cabinets that are fully insulated (i.e., on all sides) and have solid or transparent doors designed to maintain the temperature of hot food that has been cooked using a separate appliance. This measure does not include cook-and-hold or retherm equipment. | Yes |  | Holding cabinet fully insulated (i.e., on all sides) and has solid or transparent doors? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | When inspecting the holding cabinet, check to see if the cabinet has any glass or transparent (see through) doors or sides | The holding cabinet must be fully insulated with no glass or transparent doors or sides | QA Checklist | Use the manufacturer spec sheet to check to see if the cabinet has any glass or transparent (see through) doors or sides | The holding cabinet must be fully insulated with no glass or transparent doors or sides |  | 2021-09-09 | Kenny Liljestrom |  | Add | 88
1 | SWFS007 | 3 | Insulated Hot Food Holding Cabinet | Any | Any | Any |  | EECP | 11 | This measure does not include cook-and-hold or retherm equipment. Any cabinets considered in this measure must have an electric resistance heating element, passive holding cabinets with no heating elements are not eligible. | Yes |  | Is this an electric resistance, passive, or cook-and-hold retherm equipment? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet to determine if the holding cabinet is classified as a cook-and-hold retherm equipment | The cook-and-hold retherm type of cabinet is not eligible for rebate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated property label with new measure requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 76
0 | SWFS008 | 1 | Conveyor Oven, Gas, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
0 | SWFS008 | 1 | Conveyor Oven, Gas, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
0 | SWFS008 | 1 | Conveyor Oven, Gas, Commercial | Any | Any | Any |  | EECP | 3 | Used or rebuilt equipment are not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
0 | SWFS008 | 1 | Conveyor Oven, Gas, Commercial | Any | Any | Any |  | EECP | 4 | This measure includes new commercial gas conveyor ovens that exceed baking energy efficiency of ≥ 42% and have an idle energy rate ≤ 57,000 Btu/hr, utilizing ASTM Standard F1817. | Yes | Size | Conveyer Width (in) | Numeric Value | [8 empty] | Must be <= 25 | QA Checklist | Use the manufacturer spec sheet to validate the Conveyer Width (in) | The Conveyer Width (in) Must be <= 25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 19
0 | SWFS008 | 1 | Conveyor Oven, Gas, Commercial | Any | Any | Any |  | EECP | 5 | This measure includes new commercial gas conveyor ovens that exceed baking energy efficiency of ≥ 42% and have an idle energy rate ≤ 57,000 Btu/hr, utilizing ASTM Standard F1817. | Yes | Idle Energy Rate | Max Idle Energy Rate (Btu/h) | Numeric Value | [8 empty] | Must be <= 57000 | QA Checklist | Use the manufacturer spec sheet to validate the Max Idle Energy Rate (Btu/h) | The Max Idle Energy Rate (Btu/h) Must be <= 57000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 28
0 | SWFS008 | 1 | Conveyor Oven, Gas, Commercial | Any | Any | Any |  | EECP | 6 | This measure includes new commercial gas conveyor ovens that exceed baking energy efficiency of ≥ 42% and have an idle energy rate ≤ 57,000 Btu/hr, utilizing ASTM Standard F1817. | Yes | EFFICIENCY | Min. Cooking Energy Efficiency (%) | Numeric Value | [8 empty] | Must be >= 42% | QA Checklist | Use the manufacturer spec sheet to validate the Min. Cooking Energy Efficiency (%) | The Min. Cooking Energy Efficiency (%) Must be >= 42% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 34
1 | SWFS010 | 1 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
1 | SWFS010 | 1 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
1 | SWFS010 | 1 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any |  | QA Checklist | 3 | Used or rebuilt equipment are not eligible. | Yes | New Equipment | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
1 | SWFS010 | 1 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any |  | EECP | 4 | This measure is a new commercial on-demand hand-wrap machine that replaces a conventional or always-on hand-wrap machine. The measure must use either a mechanical or optical control system. | Yes | Control System | Does the installed unit use a mechanical or optical control system? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer spec sheet to validate if the unit has a mechanical or optical control system | The equipment must have a mechanical or optical control system | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured for all programs | 2021-06-15 | Kenny Liljestrom |  | Add | 67
1 | SWFS010 | 1 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any |  | EECP | 5 | This measure is a new commercial on-demand hand-wrap machine that replaces a conventional or always-on hand-wrap machine. The measure must use either a mechanical or optical control system. | Yes | Replace | Did the installed unit replace a conventional or always-on hand-wrap machine? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured for all programs | 2021-06-15 | Kenny Liljestrom |  | Add | 77
1 | SWFS010 | 1 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any |  | EECP | 6 | This measure is a new commercial on-demand hand-wrap machine that replaces a conventional or always-on hand-wrap machine. The measure must use either a mechanical or optical control system. | Yes | On Demand Hand Wrap Machine | Is the installed unit an on-demand hand-wrap machine? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer spec sheet to validate if the unit is an on-demand type | The equipment must be listed as being an on-demand type unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured for all programs | 2021-06-21 | Kenny Liljestrom |  | Add | 53
0 | SWFS010 | 2 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  |  | 12
0 | SWFS010 | 2 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  |  | 5
0 | SWFS010 | 2 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any |  | EECP | 3 | Used or rebuilt equipment are not eligible. | Yes | New Equipment | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  |  | 43
0 | SWFS010 | 2 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any |  | EECP | 4 | This measure is a new commercial on-demand hand-wrap machine that replaces a conventional or always-on hand-wrap machine. The measure must use either a mechanical or optical control system. | Yes | Control System | Does the installed unit use a mechanical or optical control system? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer spec sheet to validate if the unit has a mechanical or optical control system | The equipment must have a mechanical or optical control system | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured for all programs | 2021-06-15 | Kenny Liljestrom |  |  | 67
0 | SWFS010 | 2 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any |  | EECP | 5 | This measure is a new commercial on-demand hand-wrap machine that replaces a conventional or always-on hand-wrap machine. The measure must use either a mechanical or optical control system. | Yes | Replace | Did the installed unit replace a conventional or always-on hand-wrap machine? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured for all programs | 2021-06-15 | Kenny Liljestrom |  |  | 77
0 | SWFS010 | 2 | Commercial Hand-Wrap Machine, Electric | Any | Any | Any |  | EECP | 6 | This measure is a new commercial on-demand hand-wrap machine that replaces a conventional or always-on hand-wrap machine. The measure must use either a mechanical or optical control system. | Yes | On Demand Hand Wrap Machine | Is the installed unit an on-demand hand-wrap machine? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer spec sheet to validate if the unit is an on-demand type | The equipment must be listed as being an on-demand type unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured for all programs | 2021-06-21 | Kenny Liljestrom |  |  | 53
1 | SWFS011 | 2 | Fryer, Commercial | Any | Any | Any |  | EECP | 1 | - | No | Manufacturer | Manufacturer | Text Box | [9 empty] | - | - | - | - | - | - |  | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 12
1 | SWFS011 | 2 | Fryer, Commercial | Any | Any | Any |  | EECP | 2 | - | No | Model | Model | Text Box | [9 empty] | - | - | - | - | - | - |  | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 5
1 | SWFS011 | 2 | Fryer, Commercial | Any | Any | Any |  | EECP | 3 | Used or rebuilt equipment are not eligible. | No | New Equipment | New Equipment | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | - | - | - | - | - | - | Not configured in original upload | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 13
1 | SWFS011 | 2 | Fryer, Commercial | Any | Any | Any |  | EECP | 4 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | No | Type | Fryer Type | Drop Down List | Standard Vat;Large Vat | [8 empty] | - | - | - | - | - | - |  | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 10
1 | SWFS011 | 2 | Fryer, Commercial | Any | Any | Any |  | EECP | 5 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | No | Energy Star Qualified | ENERGY STAR Qualified? | Drop Down List | Yes;No | [8 empty] | - | - | - | - | - | - |  | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 22
1 | SWFS011 | 2 | Fryer, Commercial | A | Any | Any |  | EECP | 6 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | No | Idle Energy Rate | Idle Energy Rate (watts) | Numeric Value | [8 empty] | If 'Energy Star Qualified" is 'No' then make active If 'Fryer Type' is 'Standard Vat' then must be <= 800 If 'Fryer Type' is 'Large Vat' then must be <= 1100 | - | - | - | - | - | - |  | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 24
1 | SWFS011 | 2 | Fryer, Commercial | A | Any | Any |  | EECP | 7 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | No | EFFICIENCY | Heavy Load Cooking Efficiency (%) | Numeric Value | [8 empty] | If 'Energy Star Qualified" is 'No' then make active If 'Fryer Type' is 'Standard Vat' then must be >= 83% If 'Fryer Type' is 'Large Vat' then must be >= 80 | - | - | - | - | - | - |  | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 33
1 | SWFS011 | 2 | Fryer, Commercial | B | Any | Any |  | EECP | 8 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | No | Idle Energy Rate | Idle Energy Rate (Btu/hr) | Numeric Value | [8 empty] | If 'Energy Star Qualified" is 'No' then make active If 'Fryer Type' is 'Standard Vat' then must be <= 9000 If 'Fryer Type' is 'Large Vat' then must be <= 12000 | - | - | - | - | - | - |  | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 25
1 | SWFS011 | 2 | Fryer, Commercial | B | Any | Any |  | EECP | 9 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | No | EFFICIENCY | Heavy Load Cooking Efficiency (%) | Numeric Value | [8 empty] | If 'Energy Star Qualified" is 'No' then make active Must be >= 50% | - | - | - | - | - | - |  | 2021-06-07 | Kenny Liljestrom | Workpaper is no longer active. Close date of 6/6/2021. | Add | 33
0 | SWFS011 | 3 | Fryer, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-07 | Kenny Liljestrom |  | Add | 12
0 | SWFS011 | 3 | Fryer, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-07 | Kenny Liljestrom |  | Add | 5
0 | SWFS011 | 3 | Fryer, Commercial | Any | Any | Any |  | EECP | 3 | Used or rebuilt equipment are not eligible. | Yes | New Equipment | New Equipment | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 13
0 | SWFS011 | 3 | Fryer, Commercial | Any | Any | Any |  | EECP | 4 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | Type | Fryer Type | Drop Down List | Standard Vat;Large Vat | [8 empty] | QA Checklist | Use the manufacturer spec sheet to validate the fryer vat type (Standard or Large) | The vat type must meet the measure case description | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 10
0 | SWFS011 | 3 | Fryer, Commercial | Any | Any | Any |  | EECP | 5 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | Energy Star Qualified | ENERGY STAR Qualified? | Drop Down List | Yes;No | [8 empty] | QA Checklist | Use the EnergyStar database and compare the listed make and model in EECP to the list | The database needs to have the make and model listed in EECP as being EnergyStar qualified; if not, criteria below must be met | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 22
0 | SWFS011 | 3 | Fryer, Commercial | A | Any | Any |  | EECP | 6 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | Idle Energy Rate | Idle Energy Rate (watts) | Numeric Value | [8 empty] | If 'Energy Star Qualified" is 'No' then make active If 'Fryer Type' is 'Standard Vat' then must be <= 800 If 'Fryer Type' is 'Large Vat' then must be <= 1100 | QA Checklist | Use the manufacturer spec sheet to validate the Idle Energy Rate (watts) | If 'Energy Star Qualified" is 'No' then, If 'Fryer Type' is 'Standard Vat' then must be <= 800 If 'Fryer Type' is 'Large Vat' then must be <= 1100 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 24
0 | SWFS011 | 3 | Fryer, Commercial | A | Any | Any |  | EECP | 7 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | EFFICIENCY | Heavy Load Cooking Efficiency (%) | Numeric Value | [8 empty] | If 'Energy Star Qualified" is 'No' then make active If 'Fryer Type' is 'Standard Vat' then must be >= 83% If 'Fryer Type' is 'Large Vat' then must be >= 80 | QA Checklist | Use the manufacturer spec sheet to validate the Heavy Load Cooking Efficiency (%) | If 'Energy Star Qualified" is 'No' then, If 'Fryer Type' is 'Standard Vat' then must be >= 83% If 'Fryer Type' is 'Large Vat' then must be >= 80 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS011 | 3 | Fryer, Commercial | B | Any | Any |  | EECP | 8 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | Idle Energy Rate | Idle Energy Rate (Btu/hr) | Numeric Value | [8 empty] | If 'Energy Star Qualified" is 'No' then make active If 'Fryer Type' is 'Standard Vat' then must be <= 9000 If 'Fryer Type' is 'Large Vat' then must be <= 12000 | QA Checklist | Use the manufacturer spec sheet to validate the Idle Energy Rate (Btu/hr) | If 'Energy Star Qualified" is 'No' then, If 'Fryer Type' is 'Standard Vat' then must be <= 9000 If 'Fryer Type' is 'Large Vat' then must be <= 12000 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 25
0 | SWFS011 | 3 | Fryer, Commercial | B | Any | Any |  | EECP | 9 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | EFFICIENCY | Heavy Load Cooking Efficiency (%) | Numeric Value | [8 empty] | If 'Energy Star Qualified" is 'No' then make active Must be >= 50% | QA Checklist | Use the manufacturer spec sheet to validate the Heavy Load Cooking Efficiency (%) | If 'Energy Star Qualified" is 'No' then, Must be >= 50% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-07 | Kenny Liljestrom |  | Add | 33
0 | SWFS011 | 3 | Fryer, Commercial | C | Any | Any |  | EECP | 10 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | Idle Energy Rate | Idle Energy Rate (Btu/hr) | Numeric Value | [8 empty] | If 'Energy Star Qualified" is 'No' then make active Must be <= 6100 | QA Checklist | Use the manufacturer spec sheet to validate the Idle Energy Rate (Btu/hr) | If 'Energy Star Qualified" is 'No' then, Must be <= 6100 | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 25
0 | SWFS011 | 3 | Fryer, Commercial | C | Any | Any |  | EECP | 11 | This measure includes new commercial fryers that are ENERGY STAR-qualified or meet the qualifications in the Measure Case Description | Yes | EFFICIENCY | Heavy Load Cooking Efficiency (%) | Numeric Value | [8 empty] | If 'Energy Star Qualified" is 'No' then make active Must be >= 60% | QA Checklist | Use the manufacturer spec sheet to validate the Heavy Load Cooking Efficiency (%) | If 'Energy Star Qualified" is 'No' then, Must be >= 60% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 33
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom |  | Add | 12
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom |  | Add | 5
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any |  | EECP | 3 | Used or rebuilt controls are not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 43
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any |  | EECP | 4 | This measure pertains to the purchase and installation of a new commercial kitchen exhaust hood control system installed in an existing or a new dedicated commercial kitchen exhaust hood and makeup air system. Specific requirements include: • The measure requires the installation of temperature sensor(s) in the hood exhaust collar or within the hood, and/or an optic sensor on the end of the hood or within the hood that senses cooking conditions and allows the system to automatically vary the rate of exhaust and make-up (ventilation) air by adjusting unit fan speeds accordingly. • The installation of a DCKV must include a temperature or optic sensor that senses cooking conditions. • The control system must be used in conjunction with a variable-speed drive (VSD) on the fan motor. • Installations in a new exhaust hood must have a total kitchen hood airflow ≤ 5,000 cfm. • If installed in an existing exhaust hood > 5,000 cfm, the existing hood must have been installed before July 1, 2014, when the 2013 California Building Energy Efficiency Standards (Title 24) standards came into effect. See Code Requirements | Yes |  | Installation includes temperature sensor(s) and/or an optic sensor to adjust fan speeds? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Using the manufacturer spec sheet validate if the unit comes with a temperature sensor(s) and/or an optic sensor which adjusts the fan speeds | The unit must come with a temperature sensor(s) and/or an optic sensor which adjusts the fan speeds | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 88
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any |  | EECP | 5 | This measure pertains to the purchase and installation of a new commercial kitchen exhaust hood control system installed in an existing or a new dedicated commercial kitchen exhaust hood and makeup air system. Specific requirements include: • The measure requires the installation of temperature sensor(s) in the hood exhaust collar or within the hood, and/or an optic sensor on the end of the hood or within the hood that senses cooking conditions and allows the system to automatically vary the rate of exhaust and make-up (ventilation) air by adjusting unit fan speeds accordingly. • The installation of a DCKV must include a temperature or optic sensor that senses cooking conditions. • The control system must be used in conjunction with a variable-speed drive (VSD) on the fan motor. • Installations in a new exhaust hood must have a total kitchen hood airflow ≤ 5,000 cfm. • If installed in an existing exhaust hood > 5,000 cfm, the existing hood must have been installed before July 1, 2014, when the 2013 California Building Energy Efficiency Standards (Title 24) standards came into effect. See Code Requirements | Yes |  | Does the control system use a Variable Speed Drive (VSD) on the fan motor? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Using the manufacturer spec sheet validate if the unit comes with a variable speed drive (VSD) for the fan motor | The unit must come with a VSD for the fan | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 74
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any |  | EECP | 6 | - | No | HP | HP | Numeric Value | [9 empty] | - | - | - | - | - | - | Duplicate property, can be removed and replaced by Size (Rated-HP) already configured | 2021-08-19 | Kenny Liljestrom |  | Add | 2
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any |  | EECP | 7 | Good to have | Yes | Size | Rated-HP | Numeric Value | [9 empty] | Inspections | If accessible, photograph the nameplate of the fan motor to capture the power rating (hp) | The power rating on the nameplate should match what is listed in EECP | QA Checklist | Using the installation report or manufacturer spec sheet, determine the power rating (hp) of the fan motor or VSD | The power rating (hp) should match what is listed in EECP; if unable to determine the fan size, this property can be assumed correct |  | 2021-08-19 | Kenny Liljestrom |  | Add | 8
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any |  | EECP | 8 | This measure pertains to the purchase and installation of a new commercial kitchen exhaust hood control system installed in an existing or a new dedicated commercial kitchen exhaust hood and makeup air system. Specific requirements include: • The measure requires the installation of temperature sensor(s) in the hood exhaust collar or within the hood, and/or an optic sensor on the end of the hood or within the hood that senses cooking conditions and allows the system to automatically vary the rate of exhaust and make-up (ventilation) air by adjusting unit fan speeds accordingly. • The installation of a DCKV must include a temperature or optic sensor that senses cooking conditions. • The control system must be used in conjunction with a variable-speed drive (VSD) on the fan motor. • Installations in a new exhaust hood must have a total kitchen hood airflow ≤ 5,000 cfm. • If installed in an existing exhaust hood > 5,000 cfm, the existing hood must have been installed before July 1, 2014, when the 2013 California Building Energy Efficiency Standards (Title 24) standards came into effect. See Code Requirements | Yes |  | Exhaust hood airflow (cfm) | Numeric Value | [8 empty] | If >= 5000 then make available 'Installation date of existing hood' | QA Checklist | Using the installation report validate the exhaust hood flow rate (cfm) | If the airflow is less than 5,000 cfm, there are no validation criteria; if the flowrate is 5,000 cfm or above, the installation date property needs to be validated | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 26
1 | SWFS012 | 1 | Exhaust Hood Demand Controlled Ventilation, Commercial | Any | Any | Any |  | EECP | 9 | This measure pertains to the purchase and installation of a new commercial kitchen exhaust hood control system installed in an existing or a new dedicated commercial kitchen exhaust hood and makeup air system. Specific requirements include: • The measure requires the installation of temperature sensor(s) in the hood exhaust collar or within the hood, and/or an optic sensor on the end of the hood or within the hood that senses cooking conditions and allows the system to automatically vary the rate of exhaust and make-up (ventilation) air by adjusting unit fan speeds accordingly. • The installation of a DCKV must include a temperature or optic sensor that senses cooking conditions. • The control system must be used in conjunction with a variable-speed drive (VSD) on the fan motor. • Installations in a new exhaust hood must have a total kitchen hood airflow ≤ 5,000 cfm. • If installed in an existing exhaust hood > 5,000 cfm, the existing hood must have been installed before July 1, 2014, when the 2013 California Building Energy Efficiency Standards (Title 24) standards came into effect. See Code Requirements | Yes |  | Installation date of existing hood | Date | Make available if Exhaust Hood Airflow > 5000 | [7 empty] | Must be before 07/01/2014 | QA Checklist | If the installation report indicates the airflow of the unit is >= 5,000 cfm, check the installation report for when the exhaust hood was installed in the building | If the airflow rate is >= 5,000 cfm, the exhaust hood must have been installed after 7/1/2014 in order to qualify | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 34
0 | SWFS013 | 1 | Low-Flow Pre-Rinse Spray Valve | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-23 | Kenny Liljestrom |  | Add | 12
0 | SWFS013 | 1 | Low-Flow Pre-Rinse Spray Valve | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-23 | Kenny Liljestrom |  | Add | 5
0 | SWFS013 | 1 | Low-Flow Pre-Rinse Spray Valve | Any | Any | Any |  | EECP | 3 | Used or rebuilt equipment are not eligible. | Yes |  | New Equipment | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-23 | Kenny Liljestrom |  | Add | 13
0 | SWFS013 | 1 | Low-Flow Pre-Rinse Spray Valve | Any | Any | Any |  | EECP | 4 | This measure is restricted to operations with natural gas water heaters only. | Yes | Gas PRSV | Is the hot water for the installed commercial-grade PRSV supplied from natural gas water heaters? | Drop Down List | Yes;No | [8 empty] | Inspections | Locate the water heater supplying the spray valve; you may need to ask the customer for the location of the water heater; photograph the nameplate of the water heater or observe the fuel source (look for the yellow pipe going into the water heater) | The water heater serving the spray valve needs to be fueled by natural gas | QA Checklist | Use photographs from the implementer or inspections team to verify if the water heater on site is fueled by natural gas | The water heater serving the spray valve needs to be fueled by natural gas |  | 2021-08-23 | Kenny Liljestrom |  | Add | 97
0 | SWFS013 | 1 | Low-Flow Pre-Rinse Spray Valve | A | Any | Any |  | EECP | 5 | This measure is defined as a new commercial-grade PRSV with a maximum flow rate ≤ 1.07 gpm that replaces a PRSV with a maximum flow rate of 1.20 gpm for a spray force of > 5.0 ozf and ≤ 8.0 ozf; and as a new commercial-grade PRSV with a maximum flow rate ≤ 0.75 gpm that replaces a PRSV with a maximum flow rate of 1.00 gpm for a spray force of < 5.0 ozf. | Yes | Gas PRSV flow rate | Was a new commercial-grade PRSV with a maximum flow rate = 1.07 gpm installed that replaced an existing PRSV with a maximum flow rate of 1.20 gpm for a spray force of > 5.0 ozf and < 8.0 ozf? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer spec sheet to verify the new spray valve has a maximum flow rate of 1.07 gallons per minute (gpm) | The spray valve must have a maximum flow rate of 1.07 gpm | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-23 | Kenny Liljestrom |  | Add | 191
0 | SWFS013 | 1 | Low-Flow Pre-Rinse Spray Valve | B | Any | Any |  | EECP | 6 | This measure is defined as a new commercial-grade PRSV with a maximum flow rate ≤ 1.07 gpm that replaces a PRSV with a maximum flow rate of 1.20 gpm for a spray force of > 5.0 ozf and ≤ 8.0 ozf; and as a new commercial-grade PRSV with a maximum flow rate ≤ 0.75 gpm that replaces a PRSV with a maximum flow rate of 1.00 gpm for a spray force of < 5.0 ozf. | Yes | Gas PRSV flow rate | Was a new commercial-grade PRSV with a maximum flow rate = 0.75 gpm installed that replaced an existing PRSV with a maximum flow rate of 1.00 gpm for a spray force of < 5.0 ozf? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer spec sheet to verify the new spray valve has a maximum flow rate of 0.75 gallons per minute (gpm) | The spray valve must have a maximum flow rate of 0.75 gpm | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-23 | Kenny Liljestrom |  | Add | 177
1 | SWFS014 | 2 | Rack Oven, Gas, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
1 | SWFS014 | 2 | Rack Oven, Gas, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
1 | SWFS014 | 2 | Rack Oven, Gas, Commercial | Any | Any | Any |  | EECP | 3 | Used or rebuilt equipment is not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
1 | SWFS014 | 2 | Rack Oven, Gas, Commercial | A | Any | Any |  | EECP | 4 | This measure includes new commercial gas single and double rack ovens tested to meet or exceed baking energy efficiency of 50%. | Yes | Size | Oven Size | Drop Down List | Single;Double | [7 empty] | Must be 'Single' | QA Checklist | Use the submitted manufacturer spec sheet to determine the oven size (single or double) | The oven must be listed as a Single oven in the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-23 | Kenny Liljestrom |  | Add | 9
1 | SWFS014 | 2 | Rack Oven, Gas, Commercial | B | Any | Any |  | EECP | 5 | This measure includes new commercial gas single and double rack ovens tested to meet or exceed baking energy efficiency of 50%. | Yes | Size | Oven Size | Drop Down List | Single;Double | [7 empty] | Must be 'Double' | QA Checklist | Use the submitted manufacturer spec sheet to determine the oven size (single or double) | The oven must be listed as a Double oven in the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 9
1 | SWFS014 | 2 | Rack Oven, Gas, Commercial | Any | Any | Any |  | EECP | 6 | This measure includes new commercial gas single and double rack ovens tested to meet or exceed baking energy efficiency of 50%. | Yes | EFFICIENCY | Min. Cooking Energy Efficiency (%) | Numeric Value | [8 empty] | Must be >= 50% | QA Checklist | Use the submitted manufacturer spec sheet to determine the oven min cooking efficiency (%) | The min cooking efficiency must be >= 50% and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 34
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | Any | Any | Any |  | EECP | 3 | Used or rebuilt equipment is not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | Any | Any | Any |  | EECP | 4 | The replacement automatic conveyor broiler must have a catalyst and an input rate less than 80 kBtu/hr or a dual stage or modulating gas valve with a capability of throttling the input rate below 80 kBtu/hr. | Yes | Existing Conveyor Input Rate | Does the installed automatic conveyor broiler have a catalyst and an input rate less than 80 kBtu/hr or a dual stage or modulating gas valve with a capability of throttling the input rate below 80 kBtu/hr? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Check the manufacturer spec sheet to see if the automatic conveyor broiler has a catalyst and an input rate less than 80 kBtu/hr or a dual stage or modulating gas valve with a capability of throttling the input rate below 80 kBtu/hr | The replacement automatic conveyor broiler must have a catalyst and an input rate less than 80 kBtu/hr or a dual stage or modulating gas valve with a capability of throttling the input rate below 80 kBtu/hr | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 205
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | A | Any | Any |  | EECP | 5 | Measure Description | Yes | Size | Automatic Conveyor Broilers Belt Width (in) | Numeric Value | [8 empty] | Must be < 20 | QA Checklist | Check the manufacturer spec sheet for the belt width on the broiler | The belt width needs to be < 20 inches | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | B | Any | Any |  | EECP | 6 | Measure Description | Yes | Size | Automatic Conveyor Broilers Belt Width (in) | Numeric Value | [8 empty] | Must be >= 20 and <= 26 | QA Checklist | Check the manufacturer spec sheet for the belt width on the broiler | The belt width needs to be >= 20 and < 26 inches | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | C | Any | Any |  | EECP | 7 | Measure Description | Yes | Size | Automatic Conveyor Broilers Belt Width (in) | Numeric Value | [8 empty] | Must be > 26 | QA Checklist | Check the manufacturer spec sheet for the belt width on the broiler | The belt width needs to be > 26 inches | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 43
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | A | Any | Any |  | EECP | 8 | The existing (base case) broiler must be an automatic conveyor broiler than can maintain a temperature above 600 °F with a tested idle rate greater than: • 40 kBtu/hr for a belt narrower than 20" • 60 kBtu/hr for a belt between 20 and 26" • 70 kBtu/hr for a belt wider than 26" | Yes | Existing Conveyor Temp | Was the existing broiler an automatic conveyor broiler than could maintain a temperature above 600 °F with a tested idle rate greater than 40 kBtu/hr for a belt narrower than 20 inches? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 185
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | B | Any | Any |  | EECP | 9 | The existing (base case) broiler must be an automatic conveyor broiler than can maintain a temperature above 600 °F with a tested idle rate greater than: • 40 kBtu/hr for a belt narrower than 20" • 60 kBtu/hr for a belt between 20 and 26" • 70 kBtu/hr for a belt wider than 26" | Yes | Existing Conveyor Temp | Was the existing broiler an automatic conveyor broiler than could maintain a temperature above 600 °F with a tested idle rate greater than 40 kBtu/hr for a belt narrower than 20 inches? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 185
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | C | Any | Any |  | EECP | 10 | The existing (base case) broiler must be an automatic conveyor broiler than can maintain a temperature above 600 °F with a tested idle rate greater than: • 40 kBtu/hr for a belt narrower than 20" • 60 kBtu/hr for a belt between 20 and 26" • 70 kBtu/hr for a belt wider than 26" | Yes | Existing Conveyor Temp | Was the existing broiler an automatic conveyor broiler than could maintain a temperature above 600 °F with a tested idle rate greater than 40 kBtu/hr for a belt narrower than 20 inches? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 185
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | Any | Any | Any |  | EECP | 11 | The conveyor broiler must be replaced by a conveyor broiler similar in size or smaller. | Yes | Existing Conveyor Replaced | Is the existing conveyor broiler being replaced by a conveyor broiler similar in size or smaller? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 97
0 | SWFS017 | 2 | Automatic Conveyor Broiler, Commercial | Any | Any | Any |  | EECP | 12 | Installation shall comply with all policies, codes and regulations within the installation territory. | Yes |  | Installation complies with all policies, codes and regulations within the site territory? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-23 | Kenny Liljestrom |  | Add | 89
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | Any | Any | Any |  | EECP | 3 | Used or rebuilt equipment is not eligible. | Yes | New Equipment | New Equipment | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 13
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | Any | Any | Any |  | EECP | 4 | Other dishwasher types (conveyor, door-type, flight-type) are not eligible. | Yes | Undercounter dishwasher | Was an undercounter high temperature dishwasher installed (not another dishwasher types such as: conveyor, door-type, flight-type)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted manufacturer spec sheet to validate the dishwasher type | The dishwasher type must be listed as undercounter | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 131
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | A | Any | Any |  | EECP | 5 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [8 empty] | Must be <=0.86 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 0.86 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 44
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | B | Any | Any |  | EECP | 6 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [8 empty] | Must be <= 0.73 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 0.73 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 44
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | C | Any | Any |  | EECP | 7 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [8 empty] | Must be <= 1.19 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 1.19 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 44
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | D | Any | Any |  | EECP | 8 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [8 empty] | Must be <= 1.01 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 1.01 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 44
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | A | Any | Any |  | EECP | 9 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <= 0.50 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.50 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 25
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | B | Any | Any |  | EECP | 10 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <=0.43 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.43 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 25
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | C | Any | Any |  | EECP | 11 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <= 0.50 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.50 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 25
1 | SWFS018 | 1 | Undercounter Dishwasher, Commercial | D | Any | Any |  | EECP | 12 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <=0.43 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.43 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 25
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 12
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 5
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | Any | Any | Any |  | QA Checklist | 3 | Used or rebuilt equipment is not eligible. | Yes | New Equipment | New Equipment | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | Any | Any | Any |  | QA Checklist | 4 | Other dishwasher types (conveyor, door-type, flight-type) are not eligible. | Yes | Undercounter dishwasher | Was an undercounter high temperature dishwasher installed (not another dishwasher types such as: conveyor, door-type, flight-type)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted manufacturer spec sheet to validate the dishwasher type | The dishwasher type must be listed as undercounter | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 131
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | A | Any | Any |  | EECP | 5 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [8 empty] | Must be <=0.86 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 0.86 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 44
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | B | Any | Any |  | EECP | 6 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [8 empty] | Must be <= 0.73 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 0.73 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 44
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | C | Any | Any |  | EECP | 7 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [8 empty] | Must be <= 1.19 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 1.19 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 44
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | D | Any | Any |  | EECP | 8 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [8 empty] | Must be <= 1.01 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 1.01 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-09 | Kenny Liljestrom |  | Add | 44
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | A | Any | Any |  | EECP | 9 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <= 0.30 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.30 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-09-09 | Kenny Liljestrom |  | Add | 25
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | B | Any | Any |  | EECP | 10 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <=0.26 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.26 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-09-09 | Kenny Liljestrom |  | Add | 25
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | C | Any | Any |  | EECP | 11 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <= 0.25 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.25 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-09-09 | Kenny Liljestrom |  | Add | 25
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | D | Any | Any |  | EECP | 12 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <=0.21 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.21 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-09-09 | Kenny Liljestrom |  | Add | 25
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | A | Any | Any |  | EECP | 13 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | EFFICIENCY | Max washing energy (kWh/rack) | Numeric Value | [8 empty] | Must be <=0.35 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum washing energy (kWh/rack) | The max washing energy rate must be <= 0.35 kWh/rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-09-09 | Kenny Liljestrom |  | Add | 29
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | B | Any | Any |  | EECP | 14 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | EFFICIENCY | Max washing energy (kWh/rack) | Numeric Value | [8 empty] | Must be <=0.30 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum washing energy (kWh/rack) | The max washing energy rate must be <= 0.30 kWh/rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-09-09 | Kenny Liljestrom |  | Add | 29
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | C | Any | Any |  | EECP | 15 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | EFFICIENCY | Max washing energy (kWh/rack) | Numeric Value | [8 empty] | Must be <=0.15 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum washing energy (kWh/rack) | The max washing energy rate must be <= 0.15 kWh/rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-09-09 | Kenny Liljestrom |  | Add | 29
0 | SWFS018 | 2 | Undercounter Dishwasher, Commercial | D | Any | Any |  | EECP | 16 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | EFFICIENCY | Max washing energy (kWh/rack) | Numeric Value | [8 empty] | Must be <=0.13 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum washing energy (kWh/rack) | The max washing energy rate must be <= 0.13 kWh/rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-09-09 | Kenny Liljestrom |  | Add | 29
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-22 | Kenny Liljestrom |  |  | 12
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-22 | Kenny Liljestrom |  |  | 5
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | Any | Any | Any |  | QA Checklist | 3 | Used or rebuilt equipment is not eligible. | Yes | New Equipment | New Equipment | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-22 | Kenny Liljestrom |  |  | 13
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | Any | Any | Any |  | QA Checklist | 4 | Other dishwasher types (conveyor, door-type, flight-type) are not eligible. | Yes | Undercounter dishwasher | Was an undercounter high temperature dishwasher installed (not another dishwasher types such as: conveyor, door-type, flight-type)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted manufacturer spec sheet to validate the dishwasher type | The dishwasher type must be listed as undercounter | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-22 | Kenny Liljestrom |  |  | 131
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | A | Any | Any |  | EECP | 5 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [8 empty] | Must be <=0.86 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 0.86 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-22 | Kenny Liljestrom |  |  | 44
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | B | Any | Any |  | EECP | 6 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [8 empty] | Must be <= 0.73 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 0.73 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-22 | Kenny Liljestrom |  |  | 44
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | C | Any | Any |  | EECP | 7 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [8 empty] | Must be <= 1.19 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 1.19 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-22 | Kenny Liljestrom |  |  | 44
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | D | Any | Any |  | EECP | 8 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Max Water Consumption | Maximum Water Consumption (Gallons per Rack) | Numeric Value | [8 empty] | Must be <= 1.01 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Water Consumption (gallons per rack) | The water consumption must be <= 1.01 gallons per rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-22 | Kenny Liljestrom |  |  | 44
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | A | Any | Any |  | EECP | 9 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <= 0.30 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.30 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-11-22 | Kenny Liljestrom |  |  | 25
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | B | Any | Any |  | EECP | 10 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <=0.26 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.26 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-11-22 | Kenny Liljestrom |  |  | 25
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | C | Any | Any |  | EECP | 11 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <= 0.25 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.25 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-11-22 | Kenny Liljestrom |  |  | 25
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | D | Any | Any |  | EECP | 12 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes | Idle Energy Rate | Max Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <=0.21 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum Idle Energy Rate (kW) | The max idle energy rate must be <= 0.21 kW and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Updated validation criteria | 2021-11-22 | Kenny Liljestrom |  |  | 25
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | A | Any | Any |  | EECP | 13 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes |  | Max washing energy (kWh/rack) | Numeric Value | [8 empty] | Must be <=0.35 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum washing energy (kWh/rack) | The max washing energy rate must be <= 0.35 kWh/rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | B | Any | Any |  | EECP | 14 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes |  | Max washing energy (kWh/rack) | Numeric Value | [8 empty] | Must be <=0.30 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum washing energy (kWh/rack) | The max washing energy rate must be <= 0.30 kWh/rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | C | Any | Any |  | EECP | 15 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes |  | Max washing energy (kWh/rack) | Numeric Value | [8 empty] | Must be <=0.15 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum washing energy (kWh/rack) | The max washing energy rate must be <= 0.15 kWh/rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWFS018 | 3 | Undercounter Dishwasher, Commercial | D | Any | Any |  | EECP | 16 | This measure includes new commercial low- and high-temperature undercounter dishwashers that meet the efficiency requirements presented in the Measure Case Description. | Yes |  | Max washing energy (kWh/rack) | Numeric Value | [8 empty] | Must be <=0.13 | QA Checklist | Use the submitted manufacturer spec sheet to validate the Maximum washing energy (kWh/rack) | The max washing energy rate must be <= 0.13 kWh/rack and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property for MP update | 2021-11-22 | Kenny Liljestrom |  |  | 29
0 | SWFS019 | 1 | Underfired Broiler, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
0 | SWFS019 | 1 | Underfired Broiler, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
0 | SWFS019 | 1 | Underfired Broiler, Commercial | Any | Any | Any |  | EECP | 3 | Used or rebuilt equipment is not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
0 | SWFS019 | 1 | Underfired Broiler, Commercial | Any | Any | Any |  | EECP | 4 | The measure case (replacement) underfired broiler must have an input rate ≤ 22 kBtu/hr/len-ft while maintaining a surface temperature of 600 °F, per ASTM F1695 standard. | Yes | ASTM standard | Installed broiler has an input rate <= 22 kBtu/hr/len-ft with a surface temperature of 600 °F? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the equipment is has the Input Rating listed (kBtu/hr/len-ft) and surface temperature (F) listed | The submitted installation report or manufacturer spec sheet needs to have the Input Rating listed as being <= 22 kBtu/hr/len-ft (or 22,000 Btu/hr/len-ft) and surface temperature of 600 F | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be updated to include the "<" symbol in the property label | 2021-06-15 | Kenny Liljestrom |  | Add | 94
0 | SWFS019 | 1 | Underfired Broiler, Commercial | Any | Any | Any |  | EECP | 5 | The base case broiler must be similar size or larger than the replacement unit. | Yes | Broiler size | Is the base case broiler a similar size or larger than the replacement unit? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 76
1 | SWFS019 | 2 | Underfired Broiler, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
1 | SWFS019 | 2 | Underfired Broiler, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
1 | SWFS019 | 2 | Underfired Broiler, Commercial | Any | Any | Any |  | EECP | 3 | Used or rebuilt equipment is not eligible. | Yes |  | Is the equipment new (not used or rebuilt)? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Use the submitted invoice or installation report to validate the equipment is new | The equipment should be listed as new, not used or rebuilt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-11 | Kenny Liljestrom |  | Add | 43
1 | SWFS019 | 2 | Underfired Broiler, Commercial | Any | Any | Any |  | EECP | 4 | The measure case (replacement) underfired broiler must have an input rate ≤ 22 kBtu/hr/len-ft while maintaining a surface temperature of 600 °F, per ASTM F1695 standard. | Yes | ASTM standard | Installed broiler has an input rate <= 22 kBtu/hr/len-ft with a surface temperature of 600 °F? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the equipment is has the Input Rating listed (kBtu/hr/len-ft) and surface temperature (F) listed | The submitted installation report or manufacturer spec sheet needs to have the Input Rating listed as being <= 22 kBtu/hr/len-ft (or 22,000 Btu/hr/len-ft) and surface temperature of 600 F | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be updated to include the "<" symbol in the property label | 2021-06-15 | Kenny Liljestrom |  | Add | 94
1 | SWFS019 | 2 | Underfired Broiler, Commercial | Any | Any | Any |  | EECP | 5 | The base case broiler must be similar size or larger than the replacement unit. | Yes | Broiler size | Is the base case broiler a similar size or larger than the replacement unit? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 76
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-15 | Kenny Liljestrom |  | Add | 12
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-15 | Kenny Liljestrom |  | Add | 5
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any |  | EECP | 3 | Used or rebuilt equipment are not eligible. | Yes | New Equipment | New Equipment | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | - | - | - | - | - | - | Remove property | 2021-07-15 | Kenny Liljestrom |  | Add | 13
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any |  | EECP | 4 | To qualify as a high performance conveyor toaster, the unit must meet the energy per sandwich requirement specified in the Measure Case Description. | Yes |  | Production Capacity (units/hr) | Numeric Value | [8 empty] | Must be >= 698 | - | - | - | - | - | - | Remove property | 2021-07-15 | Kenny Liljestrom | Measure property removed, workpaper requirements incorrectly identified in EECP upload. 7/15/2021 request to remove property from EECP and replace with Energy per Bun. | Add | 30
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any |  | EECP | 5 | To qualify as a high performance conveyor toaster, the unit must meet the energy per sandwich requirement specified in the Measure Case Description. | Yes |  | Idle Energy Rate (kW) | Numeric Value | [8 empty] | Must be <= 0.64 | - | - | - | - | - | - | Remove property | 2021-07-15 | Kenny Liljestrom | Measure property removed, workpaper requirements incorrectly identified in EECP upload. 7/15/2021 request to remove property from EECP and replace with Energy per Bun. | Add | 21
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any |  | EECP | 6 | To qualify as a high performance conveyor toaster, the unit must meet the energy per sandwich requirement specified in the Measure Case Description. | Yes |  | Cooking Energy Rate (kW) | Numeric Value | [8 empty] | Must be <= 2.0633 | - | - | - | - | - | - | Remove property | 2021-07-15 | Kenny Liljestrom | Measure property removed, workpaper requirements incorrectly identified in EECP upload. 7/15/2021 request to remove property from EECP and replace with Energy per Bun. | Add | 24
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any |  | EECP | 7 | To qualify as a high performance conveyor toaster, the unit must meet the energy per sandwich requirement specified in the Measure Case Description. | Yes |  | Preheat Energy Rate (kW) | Numeric Value | [8 empty] | Must be <= 2.1196 | - | - | - | - | - | - | Remove property | 2021-07-15 | Kenny Liljestrom | Measure property removed, workpaper requirements incorrectly identified in EECP upload. 7/15/2021 request to remove property from EECP and replace with Energy per Bun. | Add | 24
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any |  | EECP | 8 | To qualify as a high performance conveyor toaster, the unit must meet the energy per sandwich requirement specified in the Measure Case Description. | Yes |  | Preheat Time (mins) | Numeric Value | [8 empty] | Must be <= 9.83 | - | - | - | - | - | - | Remove property | 2021-07-15 | Kenny Liljestrom | Measure property removed, workpaper requirements incorrectly identified in EECP upload. 7/15/2021 request to remove property from EECP and replace with Energy per Bun. | Add | 19
0 | SWFS023 | 1 | Conveyor Toaster, Commercial | Any | Any | Any |  | EECP | 9 | To qualify as a high performance conveyor toaster, the unit must meet the energy per sandwich requirement specified in the Measure Case Description. | Yes |  | Energy per Bun (W/bun) | Numeric Value | [8 empty] | Must be <=3.75 | QA Checklist | Use manufacturer specification sheet to determine if energy per bun is less than the measure case description, 3.75 W/bun | Use the equation: Energy per Bun = (Cooking Energy Rate, kW * 1,000 W/kW) / (Units produced per hour) *Cooking Energy Rate, kW: May be given in Watts, in which case remove the 1,000 W/kW conversion from the equation *Units produced per hour can be calculated by: (Units produced / time interval in seconds) * (60 sec / 1 min) * (60 min / 1 hr) This value needs to be equal to or less than 3.75 W/bun | QA Checklist | Consult with the manufacturer to determine if the energy per bun meets the measure case description of 3.75 W/bun | The manufacturer should be able to specify if the cooking energy and production rate of the unit results in a energy per bun of less than or equal to 3.75 W/bun | Add property | 2021-07-15 | Kenny Liljestrom | Added 7/15/2021 after review of measure properties and requirements. | Add | 22
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | UpDeemed |  | EECP | 1 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | UpDeemed |  | EECP | 2 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | Any |  | EECP | 3 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-02 | Kenny Liljestrom |  | Add | 12
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | Any |  | EECP | 4 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-02 | Kenny Liljestrom |  | Add | 5
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | UpDeemed |  | EECP | 5 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | UpDeemed |  | EECP | 6 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | UpDeemed |  | EECP | 7 | E-5152 Data Collection Requirements | Yes | Measure Size Category | Measure Size Category | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | UpDeemed |  | EECP | 8 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | UpDeemed |  | EECP | 9 | Required for SW Program | Yes | ZC | Zip Code | Numeric Value | [9 empty] | QA Checklist | Evaluate the zip code in EECP for accuracy | Ensure zip code is real and locatable | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-02 | Kenny Liljestrom | Configured for SW UpDeemed Program | Add | 8
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | UpDeemed |  | EECP | 10 | Required for SW Program | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | Lookup table for ZC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-02 | Kenny Liljestrom | Configured for SW UpDeemed Program | Add | 15
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | Any |  | QA Checklist | 11 | Wall furnaces that are direct-vent systems that mount on an outside wall are not eligible. | Yes | - | Wall furnaces that are direct-vent systems that mount on an outside wall are not eligible. | None | [9 empty] | Inspections | Photograph the wall furnace and make note of it's location relative to the house or dwelling unit | The system should not be located outside | QA Checklist | Look for photographic evidence in the installation report indicating the unit is not installed outdoors | Photographs of the existing or installed system showing location of unit is not outside |  | 2021-07-02 | Kenny Liljestrom |  | Add | 90
1 | SWHC001 | 2 | Wall Furnace, Residential | A | Any | Any |  | EECP | 12 | Gravity wall furnaces ≤ 19,000 Btu/hr and ≥ 60,000 Btu/hr are not eligible | Yes | Gas Input Rating (Btu/hr) | Gas Input Rating (Btu/hr) | Numeric Value | [8 empty] | Must be ≥ 19,000 Btu/hr and ≤ 27,000 Btu/hr | Inspections | Photograph of the furnace nameplate showing the make and model; data can be crosschecked with specification sheet or ENERGYSTAR or ANSI databases; photograph of Gas Input rating (Btu/hr) | The Gas Input Rating (Btu/hr) must be between 19,000 and 60,000 Btu/hr | QA Checklist | Check the make and model against specification sheet, ENERGYSTAR or ANSI databases; to validate the Gas Input Rating (Btu/hr) | The Gas Input Rating (Btu/hr) must be between 19,000 and 60,000 Btu/hr | Not configured in original upload | 2022-05-17 | Kenny Liljestrom |  | Add | 25
1 | SWHC001 | 2 | Wall Furnace, Residential | B | Any | Any |  | EECP | 13 | Gravity wall furnaces ≤ 19,000 Btu/hr and ≥ 60,000 Btu/hr are not eligible | Yes | Gas Input Rating (Btu/hr) | Gas Input Rating (Btu/hr) | Numeric Value | [8 empty] | Must be > 27,000 Btu/hr and ≤ 46,000 Btu/hr | Inspections | Photograph of the furnace nameplate showing the make and model; data can be crosschecked with specification sheet or ENERGYSTAR or ANSI databases; photograph of Gas Input rating (Btu/hr) | The Gas Input Rating (Btu/hr) must be between 19,000 and 60,000 Btu/hr | QA Checklist | Check the make and model against specification sheet, ENERGYSTAR or ANSI databases; to validate the Gas Input Rating (Btu/hr) | The Gas Input Rating (Btu/hr) must be between 19,000 and 60,000 Btu/hr | Not configured in original upload | 2022-05-17 | Kenny Liljestrom |  | Add | 25
1 | SWHC001 | 2 | Wall Furnace, Residential | C | Any | Any |  | EECP | 14 | Gravity wall furnaces ≤ 19,000 Btu/hr and ≥ 60,000 Btu/hr are not eligible | Yes | Gas Input Rating (Btu/hr) | Gas Input Rating (Btu/hr) | Numeric Value | [8 empty] | Must be > 46,000 Btu/hr and ≤ 60,000 Btu/hr | Inspections | Photograph of the furnace nameplate showing the make and model; data can be crosschecked with specification sheet or ENERGYSTAR or ANSI databases; photograph of Gas Input rating (Btu/hr) | The Gas Input Rating (Btu/hr) must be between 19,000 and 60,000 Btu/hr | QA Checklist | Check the make and model against specification sheet, ENERGYSTAR or ANSI databases; to validate the Gas Input Rating (Btu/hr) | The Gas Input Rating (Btu/hr) must be between 19,000 and 60,000 Btu/hr | Not configured in original upload | 2022-05-17 | Kenny Liljestrom |  | Add | 25
1 | SWHC001 | 2 | Wall Furnace, Residential | D | Any | Any |  | EECP | 15 | Fan type wall furnaces ≤ 19,000 Btu/hr and ≥ 42,000 Btu/hr are not eligible | Yes | Gas Input Rating (Btu/hr) | Gas Input Rating (Btu/hr) | Numeric Value | [8 empty] | Must be ≥ 19,000 Btu/hr and ≤ 42,000 Btu/hr | Inspections | Photograph of the furnace nameplate showing the make and model; data can be crosschecked with specification sheet or ENERGYSTAR or ANSI databases; photograph of Gas Input rating (Btu/hr) | The Gas Input Rating (Btu/hr) must be between 19,000 and 42,000 Btu/hr | QA Checklist | Check the make and model against specification sheet, ENERGYSTAR or ANSI databases; to validate the Gas Input Rating (Btu/hr) | The Gas Input Rating (Btu/hr) must be between 19,000 and 42,000 Btu/hr | Not configured in original upload | 2022-05-17 | Kenny Liljestrom |  | Add | 25
1 | SWHC001 | 2 | Wall Furnace, Residential | A | Any | Any |  | EECP | 16 | E-5152 Data Collection Requirements | Yes | AFUE | AFUE % | Numeric Value | [8 empty] | Must be >70% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 70% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use EnergyStar or ANSI databases of equipment to check the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 70% |  | 2022-05-18 | Kenny Liljestrom |  |  | 6
1 | SWHC001 | 2 | Wall Furnace, Residential | B | Any | Any |  | EECP | 17 | E-5152 Data Collection Requirements | Yes | AFUE | AFUE % | Numeric Value | [8 empty] | Must be >70% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 70% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use EnergyStar or ANSI databases of equipment to check the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 70% |  | 2022-05-18 | Kenny Liljestrom |  |  | 6
1 | SWHC001 | 2 | Wall Furnace, Residential | C | Any | Any |  | EECP | 18 | E-5152 Data Collection Requirements | Yes | AFUE | AFUE % | Numeric Value | [8 empty] | Must be >70% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 70% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use EnergyStar or ANSI databases of equipment to check the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 70% |  | 2022-05-18 | Kenny Liljestrom |  |  | 6
1 | SWHC001 | 2 | Wall Furnace, Residential | D | Any | Any |  | EECP | 19 | E-5152 Data Collection Requirements | Yes | AFUE | AFUE % | Numeric Value | [8 empty] | Must be >82% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 82% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use EnergyStar or ANSI databases of equipment to check the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 82% |  | 2022-05-18 | Kenny Liljestrom |  |  | 6
1 | SWHC001 | 2 | Wall Furnace, Residential | Any | Any | Any |  | QA Checklist | 20 | The purchase invoice must be provided as a proof that the wall furnace has been purchased to replace a previously existing unit. Additionally, the customer must agree to a post measure installation inspection. | Yes | - | The purchase invoice must be provided as a proof that the wall furnace has been purchased to replace a previously existing unit. Additionally, the customer must agree to a post measure installation inspection. | [10 empty] | QA Checklist | Check the EECP documentation for an invoice | Ensure the purchase invoice is submitted as part of the uploaded documentation | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-02 | Kenny Liljestrom |  | Add | 209
0 | SWHC002 | 2 | Intermittent Pilot Light, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 12
0 | SWHC002 | 2 | Intermittent Pilot Light, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 5
0 | SWHC002 | 2 | Intermittent Pilot Light, Residential | Any | Any | Any |  | EECP | 3 | The customer must agree to a post installation inspection. | Yes |  | Has the customer agreed to a post installation inspection? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 58
0 | SWHC002 | 2 | Intermittent Pilot Light, Residential | B | Any | Any |  | EECP | 4 | Proof of purchase of a gravity wall furnace manufactured with an integrated intermittent pilot light must be provided. | Yes |  | Proof of purchase submitted showing Integrated intermittent pilot light in the wall furnace? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Check the documentation submitted to check for a proof of purchase documents (i.e. receipt and specification sheet) showing the new gravity wall furnace has an integrated intermittent pilot light | Proof of purchase documents must be submitted to verify the gravity wall furnace is new and has an intermittent integrated pilot light | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 92
0 | SWHC002 | 2 | Intermittent Pilot Light, Residential | B | Any | Any |  | EECP | 5 | Eligibility requirements for this measure are: • This measure pertains to gravity wall furnaces manufactured with integrated IPL controls, furnaces with a standing pilot light, and any fireplace with standing pilot light. • A furnace manufactured with integrated IPL controls can only replace a gravity wall furnace. • The IPL controls shall be capable of either using a battery or voltage line to effectively operate as intended. | Yes |  | New gravity wall furnace is replacing an existing gravity wall furnace? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 71
0 | SWHC002 | 2 | Intermittent Pilot Light, Residential | Any | Any | Any |  | EECP | 6 | Eligibility requirements for this measure are: • This measure pertains to gravity wall furnaces manufactured with integrated IPL controls, furnaces with a standing pilot light, and any fireplace with standing pilot light. • A furnace manufactured with integrated IPL controls can only replace a gravity wall furnace. • The IPL controls shall be capable of either using a battery or voltage line to effectively operate as intended. | Yes |  | Integrated pilot light controls are capable of using a battery or voltage line to operate? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer spec sheet to determine if the IPL is capable of using either a battery or electricity to operate | The controls must be capable of operating via a battery or direct line voltage (electricity) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 90
0 | SWHC002 | 2 | Intermittent Pilot Light, Residential | A | Any | DnDeemDI |  | EECP | 7 | Implementation and installation requirements are: • For direct install installations, the wall furnace or fireplace insert shall be functional prior to the IPL retrofit. • For direct install installations, the IPL control cannot replace an existing functional or non- functional pilot light control on a furnace or fireplace insert. • Any technology manufacturer qualifies for measure offerings specified, if safety and all other regulations are met and the technology is commercially available. | Yes |  | Is the existing wall furnace or fireplace insert in working condition (not requiring major repairs)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | An installation report or photos of the existing system should be submitted to verify the existing equipment | The existing equipment must be in working condition, not in need of any major repairs or retrofits; this is difficult to distinguish but photographs of existing systems should suffice | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 100
0 | SWHC002 | 2 | Intermittent Pilot Light, Residential | Any | Any | DnDeemDI |  | EECP | 8 | Implementation and installation requirements are: • For direct install installations, the wall furnace or fireplace insert shall be functional prior to the IPL retrofit. • For direct install installations, the IPL control cannot replace an existing functional or non- functional pilot light control on a furnace or fireplace insert. • Any technology manufacturer qualifies for measure offerings specified, if safety and all other regulations are met and the technology is commercially available. | Yes |  | Does the existing wall furnace or fireplace insert have pilot light controls? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | QA Checklist | An installation report or photos of the existing system should be submitted to verify the existing equipment | The existing equipment must not have controls already installed for the pilot light | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 77
1 | SWHC004 | 1 | Space Heating Boiler | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-10 | Kenny Liljestrom |  | Add | 12
1 | SWHC004 | 1 | Space Heating Boiler | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-10 | Kenny Liljestrom |  | Add | 5
1 | SWHC004 | 1 | Space Heating Boiler | Any | Any | Any |  | EECP | 3 | Retire | Yes | Cap-kBtuh | Cap-kBtuh | Numeric Value | [9 empty] | - | - | - | - | - | - | Legacy property, retire | 2021-08-10 | Kenny Liljestrom |  | Add | 9
1 | SWHC004 | 1 | Space Heating Boiler | Any | Any | Any |  | EECP | 4 | Retire | Yes | OA Reset Control (degrees in Fahrenheit) | OA Reset Control (F) | Numeric Value | [9 empty] | - | - | - | - | - | - | Remove property, can be located in measure description | 2021-08-10 | Kenny Liljestrom |  | Add | 20
1 | SWHC004 | 1 | Space Heating Boiler | Any | Any | Any |  | EECP | 5 | Good to have | Yes | Rated Input (Btuh) | Rated Input (Btuh) | Numeric Value | [9 empty] | Inspections | Photograph the equipment nameplate to capture the Input Rating; commonly referenced with the units MMBtu/hr, kBtu/hr, or Btu/hr | The value on the nameplate, if listed in Btu/hr, should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Input Rating Btu/hr is listed | The capacity (Btu/hr) listed in EECP should match the value listed in the specification sheet | Update property name and property label, Remove validation criteria | 2021-08-10 | Kenny Liljestrom |  | Add | 18
1 | SWHC004 | 1 | Space Heating Boiler | Any | Any | Any |  | EECP | 6 | Retire | Yes | Size | Cap-kBtuh | Numeric Value | [9 empty] | - | - | - | - | - | - | Legacy property, retire | 2021-08-10 | Kenny Liljestrom |  | Add | 9
1 | SWHC004 | 1 | Space Heating Boiler | A | Any | Any |  | EECP | 7 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | AFUE (%) | Numeric Value | [8 empty] | Must be >= 84% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 8
1 | SWHC004 | 1 | Space Heating Boiler | B | Any | Any |  | EECP | 8 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 85% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | C | Any | Any |  | EECP | 9 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | D | Any | Any |  | EECP | 10 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | E | Any | Any |  | EECP | 11 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 83% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | E | Any | Any |  | EECP | 12 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes |  | Combustion Efficiency (%) | Numeric Value | [8 empty] | Must be >= 85% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Combustion Efficiency (%) is listed | The Combustion Efficiency (%) listed in EECP should match the value listed in the specification sheet | New property | 2021-08-10 | Kenny Liljestrom |  | Add | 25
1 | SWHC004 | 1 | Space Heating Boiler | F | Any | Any |  | EECP | 13 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | G | Any | Any |  | EECP | 14 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | H | Any | Any |  | EECP | 15 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 82% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | I | Any | Any |  | EECP | 16 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 80% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | J | Any | Any |  | EECP | 17 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 82% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 1 | Space Heating Boiler | Any | Any | Any |  | EECP | 18 | The boiler must be used for space heating to induce human comfort, as defined by the California Appliance Efficiency Regulations (Title 20) and Building Energy Efficiency Standards (Title 24). | Yes | Title 24 | Boiler used for space comfort (not domestic or process hot water)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured for all SWHC004 measures | 2021-08-10 | Kenny Liljestrom |  | Add | 66
1 | SWHC004 | 1 | Space Heating Boiler | Any | Any | Any |  | QA Checklist | 19 | The installation address must have a commercial natural gas account. | Yes |  | The installation address must have a commercial natural gas account. | [10 empty] | QA Checklist | Use EECP to determine if the customer purchases natural gas from SDG&E | The customer must be an active account holder and purchase natural gas from SDG&E | - | - | - |  | 2021-08-10 | Kenny Liljestrom |  | Add | 68
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any |  | EECP | 1 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 12
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any |  | EECP | 2 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 5
0 | SWHC004 | 2 | Space Heating Boiler | A | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type is Residential Multifamily? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | Observe the building type | The building type must be Residential Multi-family | QA Checklist | Use the installation report to validate the building type | The building type must be Residential Multi-family | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 41
0 | SWHC004 | 2 | Space Heating Boiler | B | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | C | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | D | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | E | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | F | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | G | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | H | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | I | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | J | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Yes |  | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [7 empty] | Must not be 'Residential Multifamily' | Inspections | Observe the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements | 2021-09-09 | Kenny Liljestrom |  | Add | 13
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any |  | EECP | 4 |  | Yes | Serial Number | Condenser Serial Number | [10 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 23
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any |  | EECP | 5 |  | Yes | RefNum | AHRI Reference Number | [10 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any |  | EECP | 6 |  | Yes | RetailPrice | Retail Price | [10 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any |  | EECP | 7 |  | Yes | ZC | Zip Code | [10 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any |  | EECP | 8 |  | Yes | ClimateZone | CA Climate Zone | [10 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any |  | EECP | 9 | Good to have | Yes | Rated Input (Btuh) | Rated Input (Btuh) | Numeric Value | [9 empty] | Inspections | Photograph the equipment nameplate to capture the Input Rating; commonly referenced with the units MMBtu/hr, kBtu/hr, or Btu/hr | The value on the nameplate, if listed in Btu/hr, should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Input Rating Btu/hr is listed | The capacity (Btu/hr) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 18
0 | SWHC004 | 2 | Space Heating Boiler | A | Any | Any |  | EECP | 10 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | AFUE (%) | Numeric Value | [8 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the AFUE (%) is listed | The AFUE (%) listed in EECP should match the value listed in the specification sheet; the value must be >= 94% | Updated validation criteria | 2021-09-09 | Kenny Liljestrom |  | Add | 8
0 | SWHC004 | 2 | Space Heating Boiler | B | Any | Any |  | EECP | 11 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 85% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | C | Any | Any |  | EECP | 12 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | D | Any | Any |  | EECP | 13 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | E | Any | Any |  | EECP | 14 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 83% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | E | Any | Any |  | EECP | 15 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes |  | Combustion Efficiency (%) | Numeric Value | [8 empty] | Must be >= 85% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Combustion Efficiency (%) is listed | The Combustion Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 25
0 | SWHC004 | 2 | Space Heating Boiler | F | Any | Any |  | EECP | 16 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | G | Any | Any |  | EECP | 17 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | H | Any | Any |  | EECP | 18 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 82% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | I | Any | Any |  | EECP | 19 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 80% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | J | Any | Any |  | EECP | 20 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 82% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any |  | EECP | 21 | The boiler must be used for space heating to induce human comfort, as defined by the California Appliance Efficiency Regulations (Title 20) and Building Energy Efficiency Standards (Title 24). | Yes | Title 24 | Boiler used for space comfort (not domestic or process hot water)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-09-09 | Kenny Liljestrom |  | Add | 66
0 | SWHC004 | 2 | Space Heating Boiler | Any | Any | Any |  | QA Checklist | 22 | The installation address must have a commercial natural gas account. | Yes | - | The installation address must have a commercial natural gas account. | [10 empty] | QA Checklist | Use EECP to determine if the customer purchases natural gas from SDG&E | The customer must be an active account holder and purchase natural gas from SDG&E | - | - | - |  | 2021-09-09 | Kenny Liljestrom |  | Add | 68
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | UpDeemed |  | EECP | 1 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any |  | EECP | 1 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 12
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | UpDeemed |  | EECP | 2 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any |  | EECP | 2 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-09 | Kenny Liljestrom |  | Add | 5
1 | SWHC004 | 3 | Space Heating Boiler | A | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | Observe the building type | The building type must be Residential Multi-family | QA Checklist | Use the installation report to validate the building type | The building type must be Residential Multi-family | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | B | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | C | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | D | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | E | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | F | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | G | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | H | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Residential Multi-family; Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | I | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | J | Any | Any |  | EECP | 3 | This measure is applicable for the following existing and new commercial and multifamily installations. | Pending | - | Building Type | Drop Down List | Residential Multi-family;Education - Community College;Education - Secondary School;Education - University;Health/Medical - Hospital;Lodging - Hotel;Health/Medical - Nursing Home;Office - Large;Office - Small;Retail - Multistory Large;Manufacturing Biotech; | [8 empty] | Inspections | Observe the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | QA Checklist | Use the installation report to validate the building type | The building type must be one of the following: Education - Community College; Education - Secondary School; Education - University; Health/Medical - Hospital; Lodging - Hotel; Health/Medical - Nursing Home; Office - Large; Office - Small; Retail - Multistory Large; Manufacturing Biotech; | Added measure property from MP requirements, when adding to EECP, ensure this is configured at the enrollment level | 2021-09-09 | Kenny Liljestrom |  | Not a Property - configured on Enrollment - measure can be filtered for proper building type | 13
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any |  | EECP | 4 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any |  | EECP | 4 | E-5152 Data Collection Requirements | Yes | Rated Input (Btuh) | Rated Input (Btuh) | Numeric Value | [9 empty] | Inspections | Photograph the equipment nameplate to capture the Input Rating; commonly referenced with the units MMBtu/hr, kBtu/hr, or Btu/hr | The value on the nameplate, if listed in Btu/hr, should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Input Rating Btu/hr is listed | The capacity (Btu/hr) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 18
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any |  | EECP | 5 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC004 | 3 | Space Heating Boiler | A | Any | Any |  | EECP | 5 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | AFUE (%) | Numeric Value | [8 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the AFUE (%) is listed | The AFUE (%) listed in EECP should match the value listed in the specification sheet; the value must be >= 94% | Updated validation criteria | 2021-09-09 | Kenny Liljestrom |  | Add | 8
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any |  | EECP | 6 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC004 | 3 | Space Heating Boiler | B | Any | Any |  | EECP | 6 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 85% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any |  | EECP | 7 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
1 | SWHC004 | 3 | Space Heating Boiler | C | Any | Any |  | EECP | 7 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any |  | EECP | 8 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
1 | SWHC004 | 3 | Space Heating Boiler | D | Any | Any |  | EECP | 8 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | E | Any | Any |  | EECP | 9 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 83% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | E | Any | Any |  | EECP | 10 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Combustion Efficiency (%) | Combustion Efficiency (%) | Numeric Value | [8 empty] | Must be >= 85% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Combustion Efficiency (%) is listed | The Combustion Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 25
1 | SWHC004 | 3 | Space Heating Boiler | F | Any | Any |  | EECP | 11 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | G | Any | Any |  | EECP | 12 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 94% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | H | Any | Any |  | EECP | 13 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 82% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | I | Any | Any |  | EECP | 14 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 80% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | J | Any | Any |  | EECP | 15 | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Yes | Thermal Efficiency (%) | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 82% | Inspections | Photograph the equipment nameplate to capture the equipment efficiency (%) | The value on the nameplate should match what is listed in EECP | QA Checklist | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | The Thermal Efficiency (%) listed in EECP should match the value listed in the specification sheet |  | 2021-09-09 | Kenny Liljestrom |  | Add | 22
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any |  | EECP | 16 | The boiler must be used for space heating to induce human comfort, as defined by the California Appliance Efficiency Regulations (Title 20) and Building Energy Efficiency Standards (Title 24). | Yes | Title 24 | Boiler used for space comfort (not domestic or process hot water)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-09-09 | Kenny Liljestrom |  | Add | 66
1 | SWHC004 | 3 | Space Heating Boiler | Any | Any | Any |  | QA Checklist | 17 | The installation address must have a commercial natural gas account. | Yes | - | The installation address must have a commercial natural gas account. | [10 empty] | QA Checklist | Use EECP to determine if the customer purchases natural gas from SDG&E | The customer must be an active account holder and purchase natural gas from SDG&E | - | - | - |  | 2021-09-09 | Kenny Liljestrom |  |  | 68
0 | SWHC005 | 1 | Water-Cooled Chiller | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-10 | Kenny Liljestrom |  | Add | 12
0 | SWHC005 | 1 | Water-Cooled Chiller | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-10 | Kenny Liljestrom |  | Add | 5
0 | SWHC005 | 1 | Water-Cooled Chiller | Any | Any | Any |  | EECP | 3 | Good to have | Yes | Nominal Capacity (Tons) | Nominal Capacity (tons) | Numeric Value | [9 empty] | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 23
0 | SWHC005 | 1 | Water-Cooled Chiller | A | Any | Any |  | EECP | 4 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.540 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.540 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | A | Any | Any |  | EECP | 5 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.340 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.340 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | B | Any | Any |  | EECP | 6 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.572 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.572 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | B | Any | Any |  | EECP | 7 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.360 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.360 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | C | Any | Any |  | EECP | 8 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.506 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.506 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | C | Any | Any |  | EECP | 9 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.332 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.332 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | D | Any | Any |  | EECP | 10 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.536 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.536 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | D | Any | Any |  | EECP | 11 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.351 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.351 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | E | Any | Any |  | EECP | 12 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.497 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.497 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | E | Any | Any |  | EECP | 13 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.323 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.323 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | F | Any | Any |  | EECP | 14 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.527 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.527 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | F | Any | Any |  | EECP | 15 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.342 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.342 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | G | Any | Any |  | EECP | 16 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.497 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.497 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | G | Any | Any |  | EECP | 17 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.323 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.323 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | H | Any | Any |  | EECP | 18 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.527 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.527 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | H | Any | Any |  | EECP | 19 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.342 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.342 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | I | Any | Any |  | EECP | 20 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.591 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.591 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | I | Any | Any |  | EECP | 21 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.374 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.374 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | J | Any | Any |  | EECP | 22 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.626 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.626 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | J | Any | Any |  | EECP | 23 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.396 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.396 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | K | Any | Any |  | EECP | 24 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.578 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.578 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | K | Any | Any |  | EECP | 25 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.374 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.374 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | L | Any | Any |  | EECP | 26 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.612 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.612 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | L | Any | Any |  | EECP | 27 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.396 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.396 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | M | Any | Any |  | EECP | 28 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.531 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.531 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | M | Any | Any |  | EECP | 29 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.349 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.349 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | N | Any | Any |  | EECP | 30 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.563 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.563 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | N | Any | Any |  | EECP | 31 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.369 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.369 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | O | Any | Any |  | EECP | 32 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.638 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.638 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | O | Any | Any |  | EECP | 33 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.417 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.417 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | P | Any | Any |  | EECP | 34 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.675 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.675 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | P | Any | Any |  | EECP | 35 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.441 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.441 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | Q | Any | Any |  | EECP | 36 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.497 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.497 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | Q | Any | Any |  | EECP | 37 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.323 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.323 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | R | Any | Any |  | EECP | 38 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.527 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.527 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | R | Any | Any |  | EECP | 39 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.342 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.342 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | S | Any | Any |  | EECP | 40 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.663 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.663 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | S | Any | Any |  | EECP | 41 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.425 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.425 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | T | Any | Any |  | EECP | 42 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.702 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.702 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 36
0 | SWHC005 | 1 | Water-Cooled Chiller | T | Any | Any |  | EECP | 43 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.450 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.450 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-10 | Kenny Liljestrom |  | Add | 35
0 | SWHC005 | 1 | Water-Cooled Chiller | Any | Any | Any |  | QA Checklist | 44 | All measures related to constant speed screw, constant speed centrifugal, and frictionless chillers are excluded due to the stringency of the tiers specified for the 2020 update of the Database of Energy Efficient Resources (DEER) and equipment availability in the market. | Yes |  | All measures related to constant speed screw, constant speed centrifugal, and frictionless chillers are excluded due to the stringency of the tiers specified for the 2020 update of the Database of Energy Efficient Resources (DEER) and equipment availability in the market. | [10 empty] | QA Checklist | Using the manufacturer spec sheet, verify the chiller is not a constant speed or frictionless type chiller | The chiller type should match the measure case description (Centrifugal w/VSD or Screw w/ VSD) and not be constant speed or frictionless | - | - | - |  | 2021-08-11 | Kenny Liljestrom |  | Add | 272
1 | SWHC005 | 2 | Water-Cooled Chiller | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-22 | Kenny Liljestrom |  |  | 12
1 | SWHC005 | 2 | Water-Cooled Chiller | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-22 | Kenny Liljestrom |  |  | 5
1 | SWHC005 | 2 | Water-Cooled Chiller | Any | Any | Any |  | EECP | 3 | Good to have | Yes | Nominal Capacity (Tons) | Nominal Capacity (tons) | Numeric Value | [9 empty] | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 23
1 | SWHC005 | 2 | Water-Cooled Chiller | A | Any | Any |  | EECP | 4 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.540 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.540 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | A | Any | Any |  | EECP | 5 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.340 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.340 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | B | Any | Any |  | EECP | 6 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.572 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.572 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | B | Any | Any |  | EECP | 7 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.360 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.360 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | C | Any | Any |  | EECP | 8 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.506 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.506 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | C | Any | Any |  | EECP | 9 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.332 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.332 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | D | Any | Any |  | EECP | 10 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.536 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.536 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | D | Any | Any |  | EECP | 11 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.351 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.351 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | E | Any | Any |  | EECP | 12 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.497 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.497 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | E | Any | Any |  | EECP | 13 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.323 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.323 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | F | Any | Any |  | EECP | 14 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.527 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.527 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | F | Any | Any |  | EECP | 15 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.342 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.342 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | G | Any | Any |  | EECP | 16 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.497 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.497 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | G | Any | Any |  | EECP | 17 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.323 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.323 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | H | Any | Any |  | EECP | 18 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.527 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.527 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | H | Any | Any |  | EECP | 19 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.342 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.342 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | I | Any | Any |  | EECP | 20 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.591 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.591 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | I | Any | Any |  | EECP | 21 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.374 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.374 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | J | Any | Any |  | EECP | 22 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.626 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.626 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | J | Any | Any |  | EECP | 23 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.396 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.396 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | K | Any | Any |  | EECP | 24 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.578 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.578 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | K | Any | Any |  | EECP | 25 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.374 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.374 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | L | Any | Any |  | EECP | 26 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.612 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.612 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | L | Any | Any |  | EECP | 27 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.396 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.396 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | M | Any | Any |  | EECP | 28 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.531 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.531 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | M | Any | Any |  | EECP | 29 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.349 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.349 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | N | Any | Any |  | EECP | 30 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.563 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.563 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | N | Any | Any |  | EECP | 31 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.369 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.369 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | O | Any | Any |  | EECP | 32 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.638 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.638 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | O | Any | Any |  | EECP | 33 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.417 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.417 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | P | Any | Any |  | EECP | 34 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.675 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.675 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | P | Any | Any |  | EECP | 35 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.441 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.441 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | Q | Any | Any |  | EECP | 36 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.497 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.497 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | Q | Any | Any |  | EECP | 37 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.323 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.323 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | R | Any | Any |  | EECP | 38 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.527 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.527 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | R | Any | Any |  | EECP | 39 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.342 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.342 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | S | Any | Any |  | EECP | 40 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.663 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.663 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | S | Any | Any |  | EECP | 41 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.425 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.425 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | T | Any | Any |  | EECP | 42 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency (kW/ton) | Full Load Energy Efficiency (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.702 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | The Full Load Efficiency listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.702 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 36
1 | SWHC005 | 2 | Water-Cooled Chiller | T | Any | Any |  | EECP | 43 | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value (kW/ton) | Integrated Part Load Value (kW/ton) | Numeric Value | [8 empty] | Must be <= 0.450 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Part Load Efficiency, IPLV (kW/ton) is listed | The IPLV listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.450 kW/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 35
1 | SWHC005 | 2 | Water-Cooled Chiller | Any | Any | Any |  | QA Checklist | 44 | All measures related to constant speed screw, constant speed centrifugal, and frictionless chillers are excluded due to the stringency of the tiers specified for the 2020 update of the Database of Energy Efficient Resources (DEER) and equipment availability in the market. | Yes |  | All measures related to constant speed screw, constant speed centrifugal, and frictionless chillers are excluded due to the stringency of the tiers specified for the 2020 update of the Database of Energy Efficient Resources (DEER) and equipment availability in the market. | [10 empty] | QA Checklist | Using the manufacturer spec sheet, verify the chiller is not a constant speed or frictionless type chiller | The chiller type should match the measure case description (Centrifugal w/VSD or Screw w/ VSD) and not be constant speed or frictionless | - | - | - |  | 2021-11-22 | Kenny Liljestrom |  |  | 272
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 12
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 5
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | A | Any | Any |  | EECP | 3 | Required for defining Energy Use | Yes | Host Equipment | Host equipment type? | Drop Down List | AC Only Unit;AC Unit with Gas Heat;Heat Pump;Variable Volume AC Unit with Gas Heat; | [7 empty] | Must be 'AC Only Unit' | QA Checklist | Use the manufacturer spec sheet to determine the HVAC equipment type | The HVAC type must be listed as Packaged Air Conditioner or Rooftop Unit (not an AC with a furnace) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 20
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | B | Any | Any |  | EECP | 4 | Required for defining Energy Use | Yes | Host Equipment | Host equipment type? | Drop Down List | AC Only Unit;AC Unit with Gas Heat;Heat Pump;Variable Volume AC Unit with Gas Heat; | [7 empty] | Must be 'AC Unit with Gas Heat' | QA Checklist | Use the manufacturer spec sheet to determine the HVAC equipment type | The HVAC type must be listed as Packaged Air Conditioner with Gas Furnace or Heating | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 20
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | C | Any | Any |  | EECP | 5 | Required for defining Energy Use | Yes | Host Equipment | Host equipment type? | Drop Down List | AC Only Unit;AC Unit with Gas Heat;Heat Pump;Variable Volume AC Unit with Gas Heat; | [7 empty] | Must be 'Heat Pump' | QA Checklist | Use the manufacturer spec sheet to determine the HVAC equipment type | The HVAC type must be listed as a Heat Pump | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 20
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | D | Any | Any |  | EECP | 6 | Required for defining Energy Use | Yes | Host Equipment | Host equipment type? | Drop Down List | AC Only Unit with Gas Heat;Heat Pump;Variable Volume AC Unit with Gas Heat; | [7 empty] | Must be 'Variable Volume AC Unit with Gas Heat' | QA Checklist | Use the manufacturer spec sheet to determine the HVAC equipment type | The HVAC type must be listed as a Variable Air Volume Unit with Gas Furnace or heating | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property needs to be updated with correct validation criteria | 2021-06-15 | Kenny Liljestrom |  | Add | 20
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | Any | Any | Any |  | EECP | 7 | This measure does not apply if the rooftop unit (RTU) has a fully operational and/or non-snapdisc sensor and is adjusted to the appropriate changeover setpoint based on the number of thermostat stages available for cooling. | Yes |  | Existing RTU could adjust the changeover setpoint based on the number of thermostat cooling stages? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload, similar in language to 'Changeover Setpoint' | 2021-08-24 | Kenny Liljestrom |  | Add | 99
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | Any | Any | Any |  | EECP | 8 | This measure requires field documentation of the existing conditions that verify the measure was necessary and that the measure was successfully applied. | Yes | Field docs | Was field documentation of the existing conditions that verify the measure was necessary and that the measure was successfully applied submitted? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Review the submitted documentation in EECP to check the existing conditions of the system were recorded | This measure requires field documentation of the existing conditions that verify the measure was necessary and that the measure was successfully applied. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-15 | Kenny Liljestrom |  | Add | 145
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | Any | Any | Any |  | EECP | 9 | Additional technician verification of thermostat wiring and the number of cooling stages that should be performed to ensure that the first stage of cooling is dedicated to economizer operation and two-stage thermostat operation is enabled where possible. | Yes | Tech verification | Was add. tech verification of thermostat wiring and number of cooling stages that should be performed to ensure the 1st stage of cooling is dedicated to economizer operation and 2-stage thermostat operation is enabled performed if possible? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 240
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | Any | Any | Any |  | EECP | 10 | The controller changeover setpoint should be adjusted appropriately based on the available number of thermostat cooling stages. | Yes | Changeover Setpoint | Was the controller changeover setpoint adjusted appropriately based on the available number of thermostat cooling stages? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 121
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | Any | Any | Any |  | EECP | 11 | Contractors and technicians that implement the measure must meet all certification and training requirements in accordance with program requirements. | Yes | Cert and Train | Do the contractors and technicians that implement the measure meet all certification and training requirements in accordance with program requirements? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 151
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | Any | Any | Any |  | EECP | 12 | Contractors and technicians that implement this measure must ensure that the existing unit does not already have the supply fan in automatic mode or switched OFF during unoccupied periods. This measure does not apply if the unoccupied supply fan operation is already set to “Auto” or intermittent. | Yes | Switched Off | Did the existing unit have the supply fan in automatic mode or switched OFF during unoccupied periods? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-15 | Kenny Liljestrom |  | Add | 102
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | C | Any | Any |  | EECP | 13 | The measure SWHC009C (cDXHP) excludes building type WRf. | Yes |  | Is the HVAC type a DX Heat Pump (cDXHP) and the building a refrigerated warehouse (WRf)? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-24 | Kenny Liljestrom |  | Add | 88
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | D | Any | Any |  | EECP | 14 | Measure offering SWHC009D (cPVVG) excludes building type Asm, EPr, ERC, Gro, MLI, RFF, RSD, RtL, RtS, SCn, WRf | Yes |  | HVAC type is a packaged VAV with gas furnace (cPVVG)? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet to determine the HVAC equipment type | The HVAC system must not be listed as a packaged variable air volume unit with a gas furnace | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-24 | Kenny Liljestrom |  | Add | 53
0 | SWHC009 | 2 | Supply Fan Controls, Commercial | D | Any | Any |  | EECP | 14 | Measure offering SWHC009D (cPVVG) excludes building type Asm, EPr, ERC, Gro, MLI, RFF, RSD, RtL, RtS, SCn, WRf | Yes |  | Building type one of the following: Asm, EPr, ERC, Gro, MLI, RFF, RSD, RtL, RtS, SCn, WRf? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-24 | Kenny Liljestrom |  | Add | 90
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | UpDeemed |  | EECP | 1 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | UpDeemed |  | EECP | 2 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | Any |  | EECP | 3 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-11 | Kenny Liljestrom |  | Add | 12
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | Any |  | EECP | 4 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-11 | Kenny Liljestrom |  | Add | 5
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | UpDeemed |  | EECP | 5 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | UpDeemed |  | EECP | 6 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | UpDeemed |  | EECP | 7 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | UpDeemed |  | EECP | 8 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | Any |  | EECP | 9 | The measure is only applicable for classrooms in education primary schools (EPr), education secondary schools (ESe), and education re-locatable classrooms (ERC). This measure is not applicable for education community colleges, and education universities, unless these buildings have relocatable classrooms with packaged HVAC units. This measure is applicable to all vintages. | Yes | Installation Epr | Building Type | Drop Down List | Education primary schools (EPr);Education secondary schools (ESe);Education re-locatable classrooms (ERC); | [8 empty] | QA Checklist | Use EECP to determine the site location type | The building should be a primary education school (K-8), Secondary education school (9-12), or relocatable classrooms at any Primary, Secondary, Universities, or Community College school types | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property needs to be updated fully to be in compliance with the workpaper; update property label, property values, and remove validation criteria | 2021-08-11 | Kenny Liljestrom |  | Add | 13
1 | SWHC012 | 1 | Classroom HVAC Occupancy Sensor | Any | Any | Any |  | EECP | 10 | The measure requires installation of an HVAC occupancy sensing thermostat in the classroom. This control equipment includes, but is not limited to: • An occupancy sensing thermostat • An occupancy sensor (wired or wireless) • Wiring (if wired) • Signal receiver and power pack (if wireless) | Yes | System Include | Does the system include following? 1.An occupancy sensing thermostat 2. An occupancy sensor (wired or wireless) 3. Wiring (if wired) 4. Signal receiver and power pack (if wireless) | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | An installation report should indicate the components installed as part of the project | The components need to include: 1. An occupancy sensing thermostat 2. An occupancy sensor (wired or wireless) 3. Wiring (if wired) 4. Signal receiver and power pack (if wireless) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-11 | Kenny Liljestrom |  | Add | 180
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | QA Checklist | 1 | The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Yes |  | The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Drop Down List | Air-Conditioning, Heating, and Refrigeration Institute (AHRI);Consortium for Energy Efficiency (CEE) database;Manufacturers specification sheets | [8 empty] | QA Checklist | Document how you plan to validate the equipment properties related to this measure | The options for verification include: • Air-Conditioning, Heating, and Refrigeration Institute (AHRI) • Consortium for Energy Efficiency (CEE) database • Manufacturers specification sheets | - | - | - |  | 2021-08-11 | Kenny Liljestrom |  | Add | 444
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Manufacturer | Condenser Manufacturer | Text Box | [9 empty] | Inspections | Photograph the condenser (outdoor) equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet | Update property label | 2021-08-11 | Kenny Liljestrom |  | Add | 22
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 3 | - | Yes | Model | Condenser Model | Text Box | [9 empty] | Inspections | Photograph the condenser (outdoor) equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet | Update property label | 2021-08-11 | Kenny Liljestrom |  | Add | 15
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 4 | Good for Tracking | Yes | RefNum | AHRI Reference Number | Text Box | [9 empty] | QA Checklist | Use the data from EECP to check the AHRI equipment database; this reference number may also help in identifying other equipment specifications including type, capacity, EER, and IEER | Ensure the AHRI number matches with the make and model of the equipment | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update EECP sort order (this on top) | 2021-08-11 | Kenny Liljestrom |  | Add | 21
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 5 | - | Yes | Evaporator Manufacturer | Evaporator Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet |  | 2021-08-11 | Kenny Liljestrom |  | Add | 23
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 6 | - | Yes | Evaporator Model | Evaporator Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet |  | 2021-08-11 | Kenny Liljestrom |  | Add | 16
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 7 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes | System Type | System Type | Drop Down List | Split System;Unitary;Other; | [8 empty] | - | - | - | - | - | - | Property can be removed | 2021-08-11 | Kenny Liljestrom |  | Add | 11
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 8 | Good to have for tracking | Yes | Serial Number | Condenser Serial Number | Text Box | [9 empty] | Inspections | Photograph the condenser (outdoor) equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number listed in EECP should match the serial number listed in the invoice or installation report | Update EECP sorting order, below Condenser Model | 2021-08-11 | Kenny Liljestrom |  | Add | 23
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 9 | Good to have for tracking | Yes | RetailPrice | Retail Price | Numeric Value | [9 empty] | QA Checklist | Use the customer submitted invoice to verify the price of the unit | The value on the invoice should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-11 | Kenny Liljestrom |  | Add | 12
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 10 | Required for UpDeemed Programs | Yes | ZC | Zip Code | Numeric Value | [9 empty] | QA Checklist | Evaluate the zip code in EECP for accuracy | Ensure zip code is real and locatable | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-11 | Kenny Liljestrom |  | Add | 8
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 11 | Required for UpDeemed Programs | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-11 | Kenny Liljestrom |  | Add | 15
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 12 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes |  | Replacement like-for-like (i.e. air conditioner for an air conditioner or heat pump for heat pump)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 99
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 13 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes |  | Existing Equipment within +/- 5% of the replacement equipment Cooling Capacity (kBtuh)? | Drop Down List | Yes;No; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 87
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 14 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes |  | Contractor provided load calculations showing new unit is sized correctly for the load? | Drop Down List | Yes;No;N/A; | [7 empty] | If 'Is the Existing Equipment Cooling Capacity (kBtuh) within +/- 5% of the replacement equipment cooling capacity (kBtuh)?' is 'No' then must be 'Yes' Else must be N/A | QA Checklist | Review the EECP documentation and look for any load calculations submitted by the implementer | The load calculations from the implementer are used to justify an increase in load from the existing HVAC unit; the load calculations should show justification, which can be assisted by engineering, for new loads or inadequate load sizing of the original system | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 87
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 15 | Central systems and domestic hot water systems are not eligible. Package terminal air conditioning units, which are units manufactured for installation through a wall or window and are usually ≤ 2 tons, are not eligible. | Yes |  | System Type | Drop Down List | Air Conditioner or Heat Pump;Packaged Terminal Air Conditioner (PTAC);Packaged Terminal Heat Pump (PTHP);Central System; | [7 empty] | Must be 'Air Conditioner or Heat Pump' | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the System Type is listed | The System Type listed in EECP should match the type listed in the invoice, installation report, or spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 11
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 16 | Good to have | Yes |  | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be >= 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 24
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | A | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | B | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | C | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 12.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | D | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 13.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | E | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | F | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | G | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 12.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | H | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 10.8 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 10.8 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | I | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | J | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 12.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | K | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 10.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 10.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | L | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 11.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | M | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | N | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | O | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | P | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Q | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | R | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 10.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 10.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | S | Any | Any |  | EECP | 17 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 10.8 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 10.8 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 29
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | A | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 13.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | B | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 13.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | C | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 14.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 14.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | D | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 13.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | E | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 13.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | F | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 13.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | G | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 14.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 14.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | H | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 12.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | I | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 12.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | J | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 15.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | K | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 11.6 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.6 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | L | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 12.3 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.3 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | M | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 13.8 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.8 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 41
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | N | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 32
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | O | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 32
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | P | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 32
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Q | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 32
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | R | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 32
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | S | Any | Any |  | EECP | 18 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes |  | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-11 | Kenny Liljestrom |  | Add | 32
0 | SWHC013 | 1 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | QA Checklist | 19 | Field inspections should be performed to verify the condenser/unit model number for quality assurance purposes. | Yes |  | Has a field inspection been performed to verify the condenser and if applicable evaporator make and model? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Indicate if an inspection was completed by the inspections team | There is no pass or fail criteria | - | - | - |  | 2021-08-11 | Kenny Liljestrom |  | Add | 106
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | QA Checklist | 1 | The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Yes | - | The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Drop Down List | Air-Conditioning, Heating, and Refrigeration Institute (AHRI);Consortium for Energy Efficiency (CEE) database;Manufacturers specification sheets | [8 empty] | QA Checklist | Document how you plan to validate the equipment properties related to this measure | The options for verification include: • Air-Conditioning, Heating, and Refrigeration Institute (AHRI) • Consortium for Energy Efficiency (CEE) database • Manufacturers specification sheets | - | - | - |  | 2021-11-22 | Kenny Liljestrom |  |  | 444
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 2 | Data collection requirements for midstream and upstream deliveries, when possible, the program administrator (PA) shall claim the “specific building type savings” in which the equipment will be installed and submit that information at claims level on CEDARS website. In cases where there is no “building type” information available for a given project, program administrator shall claim the weighted savings of “Com” building type.” | Yes | - | Building Type | Text Box | [9 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report or invoice to determine the building type the equipment was installed at | The building type should match what is listed in EECP | Configure at enrollment level | 2021-11-22 | Kenny Liljestrom |  |  | 13
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 3 | Data Collection Requirements For upstream and midstream programs, data collection requirements are as follows: R1503 Site ID - A unique identifier for the installed location of the incentivized equipment Equipment ID - A unique identifier for each unit of incentivized equipment on the site Measure Size Category - General size or capacity range specific to each measure type Equipment manufacturer Equipment model number Rated capacity Rated efficiency unit - The engineering unit basis for the efficiency or performance rating Rated efficiency - Efficiency or performance rating value for the rated efficiency unit basis Quantity per sales transaction, project or site Existing equipment type (i.e., AC or HP) for the NR MAT | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-13 | Kenny Liljestrom |  |  | 7
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 4 | Data Collection Requirements For upstream and midstream programs, data collection requirements are as follows: R1503 Site ID - A unique identifier for the installed location of the incentivized equipment Equipment ID - A unique identifier for each unit of incentivized equipment on the site Measure Size Category - General size or capacity range specific to each measure type Equipment manufacturer Equipment model number Rated capacity Rated efficiency unit - The engineering unit basis for the efficiency or performance rating Rated efficiency - Efficiency or performance rating value for the rated efficiency unit basis Quantity per sales transaction, project or site Existing equipment type (i.e., AC or HP) for the NR MAT | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-13 | Kenny Liljestrom |  |  | 12
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 5 | Data Collection Requirements For upstream and midstream programs, data collection requirements are as follows: R1503 Site ID - A unique identifier for the installed location of the incentivized equipment Equipment ID - A unique identifier for each unit of incentivized equipment on the site Measure Size Category - General size or capacity range specific to each measure type Equipment manufacturer Equipment model number Rated capacity Rated efficiency unit - The engineering unit basis for the efficiency or performance rating Rated efficiency - Efficiency or performance rating value for the rated efficiency unit basis Quantity per sales transaction, project or site Existing equipment type (i.e., AC or HP) for the NR MAT | Yes | Measure Size Category | Measure Size Category | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-13 | Kenny Liljestrom |  |  | 21
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | A | NR | UpDeemed |  | EECP | 6 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | B | NR | UpDeemed |  | EECP | 7 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | C | NR | UpDeemed |  | EECP | 8 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | D | NR | UpDeemed |  | EECP | 9 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | E | NR | UpDeemed |  | EECP | 10 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | F | NR | UpDeemed |  | EECP | 11 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | G | NR | UpDeemed |  | EECP | 12 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | H | NR | UpDeemed |  | EECP | 13 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | I | NR | UpDeemed |  | EECP | 14 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | J | NR | UpDeemed |  | EECP | 15 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | K | NR | UpDeemed |  | EECP | 16 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | L | NR | UpDeemed |  | EECP | 17 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | M | NR | UpDeemed |  | EECP | 18 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | O | NR | UpDeemed |  | EECP | 19 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | P | NR | UpDeemed |  | EECP | 20 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Q | NR | UpDeemed |  | EECP | 21 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | R | NR | UpDeemed |  | EECP | 22 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | S | NR | UpDeemed |  | EECP | 23 | All unitary direct expansion (DX) equipment is eligible. For the normal replacement measure application type, the replacement equipment must be “like for like” (e.g., a heat pump for a heat pump). Likewise, for the new construction measure application type, although there is no existing system being replaced, the baseline fuel type must be the same as the equipment being installed (i.e., no fuel substitution) for the purposes of savings claims. | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 24 | E-5152 Data Collection Requirements | Yes | Manufacturer | Condenser Manufacturer | Text Box | [9 empty] | Inspections | Photograph the condenser (outdoor) equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 22
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 25 | E-5152 Data Collection Requirements | Yes | Model | Condenser Model | Text Box | [9 empty] | Inspections | Photograph the condenser (outdoor) equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet | Update property label | 2021-11-22 | Kenny Liljestrom |  |  | 15
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 26 | E-5152 Data Collection Requirements | Yes | Serial Number | Condenser Serial Number | Text Box | [9 empty] | Inspections | Photograph the condenser (outdoor) equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number listed in EECP should match the serial number listed in the invoice or installation report | Update EECP sorting order, below Condenser Model | 2021-11-22 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 27 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [9 empty] | QA Checklist | Use the data from EECP to check the AHRI equipment database; this reference number may also help in identifying other equipment specifications including type, capacity, EER, and IEER | Ensure the AHRI number matches with the make and model of the equipment | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update EECP sort order (this on top) | 2021-11-22 | Kenny Liljestrom |  |  | 21
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 28 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | System Type | System Type | Drop Down List | Split System;Unitary;Other; | [8 empty] | - | - | - | - | - | - | Property can be removed | 2021-11-22 | Kenny Liljestrom |  |  | 11
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 29 | E-5152 Data Collection Requirements | Yes | Evaporator Manufacturer | Evaporator Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet |  | 2021-11-22 | Kenny Liljestrom |  |  | 23
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 30 | E-5152 Data Collection Requirements | Yes | Evaporator Model | Evaporator Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet |  | 2021-11-22 | Kenny Liljestrom |  |  | 16
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 31 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [9 empty] | QA Checklist | Use the customer submitted invoice to verify the price of the unit | The value on the invoice should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-22 | Kenny Liljestrom |  |  | 12
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 32 | Required for UpDeemed Programs | Yes | ZC | Zip Code | Numeric Value | [9 empty] | QA Checklist | Evaluate the zip code in EECP for accuracy | Ensure zip code is real and locatable | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-22 | Kenny Liljestrom |  |  | 8
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 33 | Required for UpDeemed Programs | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-22 | Kenny Liljestrom |  |  | 15
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 34 | Required for UpDeemed Programs | No | Refrigerant Type | Refrigerant Type | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the refrigerant type | The listed refrigerant in EECP should match the nameplate | QA Checklist | Use the make and model number to locate the refrigerant type | The refrigerant type should be listed on the manufacturer specfication sheet or can be validated with nameplate data | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 16
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 35 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | - | Replacement like-for-like (i.e. air conditioner for an air conditioner or heat pump for heat pump)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Property removed based on discussion with CPUC on removal of +/-5% |  | 99
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 36 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | - | Existing Equipment within +/- 5% of the replacement equipment Cooling Capacity (kBtuh)? | Drop Down List | Yes;No; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Property removed based on discussion with CPUC on removal of +/-5% |  | 87
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | EECP | 37 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | - | Contractor provided load calculations showing new unit is sized correctly for the load? | Drop Down List | Yes;No;N/A; | [7 empty] | If 'Is the Existing Equipment Cooling Capacity (kBtuh) within +/- 5% of the replacement equipment cooling capacity (kBtuh)?' is 'No' then must be 'Yes' Else must be N/A | QA Checklist | Review the EECP documentation and look for any load calculations submitted by the implementer | The load calculations from the implementer are used to justify an increase in load from the existing HVAC unit; the load calculations should show justification, which can be assisted by engineering, for new loads or inadequate load sizing of the original system | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom | Property removed based on discussion with CPUC on removal of +/-5% |  | 87
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | QA Checklist | 38 | Central systems and domestic hot water systems are not eligible. Package terminal air conditioning units, which are units manufactured for installation through a wall or window and are usually ≤ 2 tons, are not eligible. | No | - | System Type | Drop Down List | Air Conditioner;Heat Pump;Other; | [7 empty] | Must be 'Air Conditioner or Heat Pump' | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the System Type is listed | The System Type listed in EECP should match the type listed in the invoice, installation report, or spec sheet | - | - | - |  | 2021-11-22 | Kenny Liljestrom | Property does not need to be included in EECP |  | 11
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | A | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 65 <= x < 134 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | B | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 65 <= x < 134 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | C | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 65 <= x < 134 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | D | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 65 <= x < 134 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | E | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 134 <= x < 239 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | F | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 134 <= x < 239 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | G | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 134 <= x < 239 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | H | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 240 <= x < 759 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | I | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 240 <= x < 759 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | J | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 240 <= x < 759 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | K | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be > 760 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | L | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be > 760 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | M | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be > 760 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | N | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 65 <= x < 134 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | O | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 65 <= x < 134 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | P | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 134 <= x < 239 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Q | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 134 <= x < 239 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | R | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 240 <= x < 759 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | S | Any | Any |  | EECP | 39 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 240 <= x < 759 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 24
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | A | Any | Any |  | EECP | 40 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | B | Any | Any |  | EECP | 41 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | C | Any | Any |  | EECP | 42 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 12.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | D | Any | Any |  | EECP | 43 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 13.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | E | Any | Any |  | EECP | 44 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | F | Any | Any |  | EECP | 45 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | G | Any | Any |  | EECP | 46 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 12.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | H | Any | Any |  | EECP | 47 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 10.8 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 10.8 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | I | Any | Any |  | EECP | 48 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | J | Any | Any |  | EECP | 49 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 12.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | K | Any | Any |  | EECP | 50 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 10.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 10.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | L | Any | Any |  | EECP | 51 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 11.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | M | Any | Any |  | EECP | 52 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | N | Any | Any |  | EECP | 53 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | O | Any | Any |  | EECP | 54 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | P | Any | Any |  | EECP | 55 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 11.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Q | Any | Any |  | EECP | 56 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 12.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | R | Any | Any |  | EECP | 57 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 10.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 10.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | S | Any | Any |  | EECP | 58 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | Yes | EER | Energy Efficiency Ratio (EER) | Numeric Value | [8 empty] | Must be >= 10.8 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 10.8 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-22 | Kenny Liljestrom |  |  | 29
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | A | Any | Any |  | EECP | 59 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 13.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | B | Any | Any |  | EECP | 60 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 13.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | C | Any | Any |  | EECP | 61 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 14.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 14.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | D | Any | Any |  | EECP | 62 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 13.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | E | Any | Any |  | EECP | 63 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 13.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | F | Any | Any |  | EECP | 64 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 13.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | G | Any | Any |  | EECP | 65 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 14.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 14.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | H | Any | Any |  | EECP | 66 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 12.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | I | Any | Any |  | EECP | 67 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 12.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | J | Any | Any |  | EECP | 68 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 15.5 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15.5 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | K | Any | Any |  | EECP | 69 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 11.6 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.6 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | L | Any | Any |  | EECP | 70 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 12.3 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.3 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | M | Any | Any |  | EECP | 71 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | IEER | Integrated Energy Efficiency Ratio (IEER) | Numeric Value | [8 empty] | Must be >= 13.8 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Integrated Energy Efficiency Ratio (IEER) is listed | The Integrated Energy Efficiency Ratio (IEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 13.8 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 41
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | N | Any | Any |  | EECP | 72 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 32
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | O | Any | Any |  | EECP | 73 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 32
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | P | Any | Any |  | EECP | 74 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 32
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Q | Any | Any |  | EECP | 75 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 32
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | R | Any | Any |  | EECP | 76 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 32
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | S | Any | Any |  | EECP | 77 | Eligible equipment must meet the measure case specifications in the Measure Case Description. Because of the large number of evaporator/condenser combinations available for split systems (several thousand combinations) some averages and/or minimum efficiencies may be used for certain groups of equipment | No | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Coefficient of Performance (COP) is listed | The Coefficient of Performance (COP) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 3.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-13 | Kenny Liljestrom | Not required based on clarification of efficiency requirements |  | 32
1 | SWHC013 | 2 | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 KBtuh, Commercial | Any | Any | Any |  | QA Checklist | 78 | Field inspections should be performed to verify the condenser/unit model number for quality assurance purposes. | Yes | - | Has a field inspection been performed to verify the condenser and if applicable evaporator make and model? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Indicate if an inspection was completed by the inspections team | There is no pass or fail criteria | - | - | - |  | 2021-11-22 | Kenny Liljestrom |  |  | 106
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | QA Checklist | 1 | The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Yes | - | The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Drop Down List | Air-Conditioning, Heating, and Refrigeration Institute (AHRI);Consortium for Energy Efficiency (CEE) database;Manufacturers specification sheets | [8 empty] | QA Checklist | Document how you plan to validate the equipment properties related to this measure | The options for verification include: • Air-Conditioning, Heating, and Refrigeration Institute (AHRI) • Consortium for Energy Efficiency (CEE) database • Manufacturers specification sheets | - | - | - |  | 2021-08-11 | Kenny Liljestrom |  | Add | 444
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Manufacturer | Condenser Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet | Update property label | 2021-08-11 | Kenny Liljestrom |  | Add | 22
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 3 | - | Yes | Model | Condenser Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet | Update property label | 2021-08-11 | Kenny Liljestrom |  | Add | 15
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 4 | Good to have for tracking | Yes | Serial Number | Condenser Serial Number | Text Box | [9 empty] | Inspections | Photograph the condenser (outdoor) equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number listed in EECP should match the serial number listed in the invoice or installation report | Update EECP sorting order, below Condenser Model | 2021-08-11 | Kenny Liljestrom |  | Add | 23
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 5 | Good for Tracking | Yes | RefNum | AHRI Reference Number | Text Box | [9 empty] | QA Checklist | Use the data from EECP to check the AHRI equipment database; this reference number may also help in identifying other equipment specifications including type, capacity, EER, and IEER | Ensure the AHRI number matches with the make and model of the equipment | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update EECP sort order (this on top) | 2021-08-11 | Kenny Liljestrom |  | Add | 21
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 6 | - | Yes | Evaporator Manufacturer | Evaporator Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet |  | 2021-08-11 | Kenny Liljestrom |  | Add | 23
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 7 | - | Yes | Evaporator Model | Evaporator Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet |  | 2021-08-11 | Kenny Liljestrom |  | Add | 16
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 8 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes | System Type | System Type | Drop Down List | Split System;Unitary;Other; | [8 empty] | - | - | - | - | - | - | Property can be removed | 2021-08-11 | Kenny Liljestrom |  | Add | 11
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 9 | Good to have for tracking | Yes | RetailPrice | Retail Price | Numeric Value | [9 empty] | QA Checklist | Use the customer submitted invoice to verify the price of the unit | The value on the invoice should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-11 | Kenny Liljestrom |  | Add | 12
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 10 | Required for UpDeemed Programs | Yes | ZC | Zip Code | Numeric Value | [9 empty] | QA Checklist | Evaluate the zip code in EECP for accuracy | Ensure zip code is real and locatable | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-11 | Kenny Liljestrom |  | Add | 8
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 11 | Required for UpDeemed Programs | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-11 | Kenny Liljestrom |  | Add | 15
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 12 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes | - | Replacement like-for-like (i.e. air conditioner for an air conditioner or heat pump for heat pump)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 99
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 13 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes | - | Existing Equipment within +/- 5% of the replacement equipment Cooling Capacity (kBtuh)? | Drop Down List | Yes;No; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 87
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 14 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | Yes | - | Contractor provided load calculations showing new unit is sized correctly for the load? | Drop Down List | Yes;No;N/A; | [7 empty] | If 'Is the Existing Equipment Cooling Capacity (kBtuh) within +/- 5% of the replacement equipment cooling capacity (kBtuh)?' is 'No' then must be 'Yes' Else must be N/A | QA Checklist | Review the EECP documentation and look for any load calculations submitted by the implementer | The load calculations from the implementer are used to justify an increase in load from the existing HVAC unit; the load calculations should show justification, which can be assisted by engineering, for new loads or inadequate load sizing of the original system | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 87
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | QA Checklist | 15 | Central systems and domestic hot water systems are not eligible. Package terminal air conditioning units, which are units manufactured for installation through a wall or window and are usually ≤ 2 tons, are not eligible. | Yes | - | System Type | Drop Down List | Air Conditioner or Heat Pump;Packaged Terminal Air Conditioner (PTAC);Packaged Terminal Heat Pump (PTHP);Central System; | [7 empty] | Must be 'Air Conditioner or Heat Pump' | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the System Type is listed | The System Type listed in EECP should match the type listed in the invoice, installation report, or spec sheet | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 11
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 16 | Good to have | Yes | - | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 24
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 17 | Need to have for validation | Yes | - | Efficiency type used for equipment eligibility | Drop Down List | Energy Efficiency Ratio (EER);Seasonal Energy Efficiency Ratio (SEER); | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-12 | Kenny Liljestrom |  | Add | 46
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | A | Any | Any |  | EECP | 18 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | B | Any | Any |  | EECP | 19 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.4 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.4 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | C | Any | Any |  | EECP | 20 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | D | Any | Any |  | EECP | 21 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | E | Any | Any |  | EECP | 22 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | F | Any | Any |  | EECP | 23 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.4 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.4 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | G | Any | Any |  | EECP | 24 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | H | Any | Any |  | EECP | 25 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | I | Any | Any |  | EECP | 26 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | J | Any | Any |  | EECP | 27 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | K | Any | Any |  | EECP | 28 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | L | Any | Any |  | EECP | 29 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | M | Any | Any |  | EECP | 30 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | N | Any | Any |  | EECP | 31 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | O | Any | Any |  | EECP | 32 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | P | Any | Any |  | EECP | 33 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Q | Any | Any |  | EECP | 34 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | R | Any | Any |  | EECP | 35 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | S | Any | Any |  | EECP | 36 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | T | Any | Any |  | EECP | 37 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | U | Any | Any |  | EECP | 38 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | V | Any | Any |  | EECP | 39 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.4 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.4 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | W | Any | Any |  | EECP | 40 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | X | Any | Any |  | EECP | 41 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Y | Any | Any |  | EECP | 42 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Z | Any | Any |  | EECP | 43 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.4 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.4 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AA | Any | Any |  | EECP | 44 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AB | Any | Any |  | EECP | 45 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AC | Any | Any |  | EECP | 46 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AD | Any | Any |  | EECP | 47 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AE | Any | Any |  | EECP | 48 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AF | Any | Any |  | EECP | 49 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AG | Any | Any |  | EECP | 50 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 12.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AH | Any | Any |  | EECP | 51 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AI | Any | Any |  | EECP | 52 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 13.5 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
0 | SWHC014 | 1 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AJ | Any | Any |  | EECP | 53 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | - | Energy Efficiency Ratio (EER) or Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) or the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | If 'Efficiency Type' is Energy Efficiency Ratio (EER) then must be >= 14.0 If 'Efficiency Type' is Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 78
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | QA Checklist | 1 | The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Yes | - | The model number is used to ascertain the equipment efficiency of a package system. The equipment efficiency of a split system will be based on a combination of the condenser and evaporator model numbers provided by a distributor. The efficiency rating will then be verified according to the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) or Consortium for Energy Efficiency (CEE) database or manufacturers specification sheets. | Drop Down List | Air-Conditioning, Heating, and Refrigeration Institute (AHRI);Consortium for Energy Efficiency (CEE) database;Manufacturers specification sheets | [8 empty] | QA Checklist | Document how you plan to validate the equipment properties related to this measure | The options for verification include: • Air-Conditioning, Heating, and Refrigeration Institute (AHRI) • Consortium for Energy Efficiency (CEE) database • Manufacturers specification sheets | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 444
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 2 | Data collection requirements for midstream and upstream deliveries, when possible, the program administrator (PA) shall claim the “specific building type savings” in which the equipment will be installed and submit that information at claims level on CEDARS website. In cases where there is no “building type” information available for a given project, program administrator shall claim the weighted savings of “Com” building type.” | Yes | - | Building Type | Text Box | [9 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report or invoice to determine the building type the equipment was installed at | The building type should match what is listed in EECP | Can be configured at the enrollment level | 2021-11-23 | Kenny Liljestrom |  |  | 13
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 3 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 4 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | A | NR | UpDeemed |  | EECP | 5 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | B | NR | UpDeemed |  | EECP | 6 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | C | NR | UpDeemed |  | EECP | 7 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | D | NR | UpDeemed |  | EECP | 8 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | E | NR | UpDeemed |  | EECP | 9 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | F | NR | UpDeemed |  | EECP | 10 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | G | NR | UpDeemed |  | EECP | 11 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | H | NR | UpDeemed |  | EECP | 12 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | I | NR | UpDeemed |  | EECP | 13 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | J | NR | UpDeemed |  | EECP | 14 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | K | NR | UpDeemed |  | EECP | 15 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | L | NR | UpDeemed |  | EECP | 16 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | M | NR | UpDeemed |  | EECP | 17 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | N | NR | UpDeemed |  | EECP | 18 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | O | NR | UpDeemed |  | EECP | 19 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | P | NR | UpDeemed |  | EECP | 20 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Q | NR | UpDeemed |  | EECP | 21 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | R | NR | UpDeemed |  | EECP | 22 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | S | NR | UpDeemed |  | EECP | 23 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | T | NR | UpDeemed |  | EECP | 24 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be AC | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | U | NR | UpDeemed |  | EECP | 25 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | V | NR | UpDeemed |  | EECP | 26 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | W | NR | UpDeemed |  | EECP | 27 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | X | NR | UpDeemed |  | EECP | 28 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Y | NR | UpDeemed |  | EECP | 29 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Z | NR | UpDeemed |  | EECP | 30 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AA | NR | UpDeemed |  | EECP | 31 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AB | NR | UpDeemed |  | EECP | 32 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AC | NR | UpDeemed |  | EECP | 33 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AD | NR | UpDeemed |  | EECP | 34 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AE | NR | UpDeemed |  | EECP | 35 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AF | NR | UpDeemed |  | EECP | 36 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AG | NR | UpDeemed |  | EECP | 37 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AH | NR | UpDeemed |  | EECP | 38 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AI | NR | UpDeemed |  | EECP | 39 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AJ | NR | UpDeemed |  | EECP | 40 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) | Yes | Existing Equipment Type | Existing Equipment Type | Drop Down List | AC;HP; | [7 empty] | Must be HP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | - | 2022-05-16 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 41 | E-5152 Data Collection Requirements | Yes | Manufacturer | Condenser Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet | Update property label | 2021-11-23 | Kenny Liljestrom |  |  | 22
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 42 | E-5152 Data Collection Requirements | Yes | Model | Condenser Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet | Update property label | 2021-11-23 | Kenny Liljestrom |  |  | 15
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 43 | E-5152 Data Collection Requirements | Yes | Serial Number | Condenser Serial Number | Text Box | [9 empty] | Inspections | Photograph the condenser (outdoor) equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number listed in EECP should match the serial number listed in the invoice or installation report | Update EECP sorting order, below Condenser Model | 2021-11-23 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 44 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [9 empty] | QA Checklist | Use the data from EECP to check the AHRI equipment database; this reference number may also help in identifying other equipment specifications including type, capacity, EER, and IEER | Ensure the AHRI number matches with the make and model of the equipment | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update EECP sort order (this on top) | 2021-11-23 | Kenny Liljestrom |  |  | 21
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 45 | E-5152 Data Collection Requirements | Yes | Evaporator Manufacturer | Evaporator Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet |  | 2021-11-23 | Kenny Liljestrom |  |  | 23
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 46 | E-5152 Data Collection Requirements | Yes | Evaporator Model | Evaporator Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet |  | 2021-11-23 | Kenny Liljestrom |  |  | 16
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 47 | E-5152 Data Collection Requirements | No | Refrigerant Type | Refrigerant Type | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the refrigerant type | The listed refrigerant in EECP should match the nameplate | QA Checklist | Use the make and model number to locate the refrigerant type | The refrigerant type should be listed on the manufacturer specfication sheet or can be validated with nameplate data | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 16
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 47 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | System Type | System Type | Drop Down List | Split System;Unitary;Other; | [8 empty] | - | - | - | - | - | - | Property can be removed | 2021-11-23 | Kenny Liljestrom |  |  | 11
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 48 | Good to have for tracking | Yes | RetailPrice | Retail Price | Numeric Value | [9 empty] | QA Checklist | Use the customer submitted invoice to verify the price of the unit | The value on the invoice should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 12
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 49 | Required for UpDeemed Programs | Yes | ZC | Zip Code | Numeric Value | [9 empty] | QA Checklist | Evaluate the zip code in EECP for accuracy | Ensure zip code is real and locatable | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 8
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | UpDeemed |  | EECP | 50 | Required for UpDeemed Programs | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 15
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 51 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | - | Replacement like-for-like (i.e. air conditioner for an air conditioner or heat pump for heat pump)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-05-16 | Kenny Liljestrom | Removal of requirement per collaboration with CPUC on measure package eligibility updates |  | 99
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 52 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | - | Existing Equipment within +/- 5% of the replacement equipment Cooling Capacity (kBtuh)? | Drop Down List | Yes;No; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-05-16 | Kenny Liljestrom | Removal of requirement per collaboration with CPUC on measure package eligibility updates |  | 87
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 53 | Additional eligibility requirements include: • All unitary direct expansion (DX) equipment is eligible. • The replacement must be “like for like” (e.g., a heat pump for a heat pump) • Retrofitted equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR the contractor must provide a load calculation verifying that the new unit is sized correctly for the load. | No | - | Contractor provided load calculations showing new unit is sized correctly for the load? | Drop Down List | Yes;No;N/A; | [7 empty] | If 'Is the Existing Equipment Cooling Capacity (kBtuh) within +/- 5% of the replacement equipment cooling capacity (kBtuh)?' is 'No' then must be 'Yes' Else must be N/A | QA Checklist | Review the EECP documentation and look for any load calculations submitted by the implementer | The load calculations from the implementer are used to justify an increase in load from the existing HVAC unit; the load calculations should show justification, which can be assisted by engineering, for new loads or inadequate load sizing of the original system | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-16 | Kenny Liljestrom | Removal of requirement per collaboration with CPUC on measure package eligibility updates |  | 87
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 54 | Central systems and domestic hot water systems are not eligible. Package terminal air conditioning units, which are units manufactured for installation through a wall or window and are usually ≤ 2 tons, are not eligible. | No | - | System Type | Drop Down List | Air Conditioner or Heat Pump;Packaged Terminal Air Conditioner (PTAC);Packaged Terminal Heat Pump (PTHP);Central System; | [7 empty] | Must be 'Air Conditioner or Heat Pump' | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the System Type is listed | The System Type listed in EECP should match the type listed in the invoice, installation report, or spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-05-16 | Kenny Liljestrom | Removal of requirement per collaboration with CPUC on measure package eligibility updates |  | 11
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 55 | Data Collection Requirements For upstream and midstream programs, data collection requirements are as follows: R1503 Site ID - A unique identifier for the installed location of the incentivized equipment Equipment ID - A unique identifier for each unit of incentivized equipment on the site Measure Size Category - General size or capacity range specific to each measure type Equipment manufacturer Equipment model number Rated capacity Rated efficiency unit - The engineering unit basis for the efficiency or performance rating Rated efficiency - Efficiency or performance rating value for the rated efficiency unit basis Quantity per sales transaction, project or site Existing equipment type (i.e., AC or HP) for the NR MAT | Yes | Measure Size Category | Measure Size Category | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-13 | Kenny Liljestrom |  |  | 21
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | A | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | B | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | C | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | D | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | E | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | F | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | G | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | H | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | I | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 45 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | J | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 45 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | K | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 45 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | L | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 45 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | M | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 45 - 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | N | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 45 - 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | O | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 45 - 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | P | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 45 - 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Q | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | R | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | S | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | T | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | U | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | V | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | W | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | X | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Y | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Z | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AA | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AB | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AC | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AD | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AE | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AF | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be < 55 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AG | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AH | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AI | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AJ | Any | Any |  | EECP | 56 | E-5152 Data Collection Requirements | Yes | Cooling Capacity (kBtuh) | Cooling Capacity (kBtuh) | Numeric Value | [8 empty] | Must be 55 - 65 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtu/hr | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (btu/hr) / 100,000 = kBtuh | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Any | Any | Any |  | EECP | 57 | Need to have for validation | No | Efficiency Type | Efficiency type used for equipment eligibility | Drop Down List | Energy Efficiency Ratio (EER);Seasonal Energy Efficiency Ratio (SEER); | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom | Clarification in the measure package indicates only one efficinecy requirement is relevant |  | 46
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | A | Any | Any |  | EECP | 58 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | B | Any | Any |  | EECP | 59 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | C | Any | Any |  | EECP | 60 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | D | Any | Any |  | EECP | 61 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | E | Any | Any |  | EECP | 62 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | F | Any | Any |  | EECP | 63 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | G | Any | Any |  | EECP | 64 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | H | Any | Any |  | EECP | 65 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | I | Any | Any |  | EECP | 66 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | J | Any | Any |  | EECP | 67 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | K | Any | Any |  | EECP | 68 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | L | Any | Any |  | EECP | 69 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | M | Any | Any |  | EECP | 70 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | N | Any | Any |  | EECP | 71 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | O | Any | Any |  | EECP | 72 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | P | Any | Any |  | EECP | 73 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Q | Any | Any |  | EECP | 74 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | R | Any | Any |  | EECP | 75 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | S | Any | Any |  | EECP | 76 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | T | Any | Any |  | EECP | 77 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | U | Any | Any |  | EECP | 78 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | V | Any | Any |  | EECP | 79 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | W | Any | Any |  | EECP | 80 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | X | Any | Any |  | EECP | 81 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Y | Any | Any |  | EECP | 82 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | Z | Any | Any |  | EECP | 83 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AA | Any | Any |  | EECP | 84 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AB | Any | Any |  | EECP | 85 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AC | Any | Any |  | EECP | 86 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AD | Any | Any |  | EECP | 87 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AE | Any | Any |  | EECP | 88 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AF | Any | Any |  | EECP | 89 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AG | Any | Any |  | EECP | 90 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 15 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AH | Any | Any |  | EECP | 91 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 16 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AI | Any | Any |  | EECP | 92 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 17 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC014 | 2 | Unitary Air-Cooled Ac Or Heat Pump, < 65 kBtuh, Commercial | AJ | Any | Any |  | EECP | 93 | Eligible products must meet the specification presented in the Measure Case Description; minimum efficiency requirements by tier are listed in the table below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 promote higher efficiency units offered by the HVAC industry. Note that a unit must meet either the SEER or EER requirement, it is not required to meet both. | Yes | SEER | Seasonal Energy Efficiency Ratio (SEER) value | Numeric Value | [8 empty] | must be >= 18 | QA Checklist | Use the manufacturer spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed and matches EECP | Seasonal Energy Efficiency Ratio (SEER) then must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 45
0 | SWHC018 | 2 | VSD for HVAC Fan Controls, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-28 | Kenny Liljestrom |  | Add | 12
0 | SWHC018 | 2 | VSD for HVAC Fan Controls, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-28 | Kenny Liljestrom |  | Add | 5
0 | SWHC018 | 2 | VSD for HVAC Fan Controls, Commercial | Any | Any | Any |  | EECP | 3 | This measure is applicable for the following nonresidential building types: Education – Secondary School Education – Community College Education – University Health/Medical – Hospital Health/Medical – Nursing Home Lodging – Hotel Office – Large Retail – Multistory Large Grocery – Grocery | Yes | - | Building Type | Drop Down List | Education – Secondary School;Education – Community College;Education – University;Health/Medical – Hospital;Health/Medical – Nursing Home;Lodging – Hotel;Office – Large;Retail – Multistory Large;Grocery – Grocery; | [8 empty] | Inspections | Make note of the building type at the inspection site | The building type must be one of the following and match what is listed in EECP: Education – Secondary School; Education – Community College; Education – University; Health/Medical – Hospital; Health/Medical – Nursing Home; Lodging – Hotel; Office – Large; Retail – Multistory Large; Grocery – Grocery; | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-24 | Kenny Liljestrom |  | Add | 13
0 | SWHC018 | 2 | VSD for HVAC Fan Controls, Commercial | Any | Any | Any |  | EECP | 4 | This measure requires the installation of a VSD and associated controls on a motor driving a ventilation fan. Eligibility requirements include: • The fan must be ≤ 100 hp. • As an add-on equipment installation, the VSD must be applied to the HVAC supply or return air system. • Any other throttling devices, such as inlet vanes or bypass dampers, and throttling valves, must be removed or permanently disabled. | Yes | Input Rating (HP) | Input rating (HP) | Numeric Value | [8 empty] | Must be ≤ 100 hp | Inspections | Photograph the nameplate of the HVAC Fan to capture the power rating, hp (if accessible); if the fan is inaccessible, inform the processor to verify the power rating via the manufacturer spec sheet | Use the nameplate power rating (hp) to validate what is listed in EECP; the power rating must be <= 100 hp | QA Checklist | Use photographs of the fan motor nameplate or manufacturer spec sheet to validate the power rating (hp) of the fan motor | The power rating of the fan must be <= 100 hp |  | 2021-06-28 | Kenny Liljestrom |  | Add | 17
0 | SWHC018 | 2 | VSD for HVAC Fan Controls, Commercial | Any | Any | Any |  | EECP | 5 | This measure requires the installation of a VSD and associated controls on a motor driving a ventilation fan. Eligibility requirements include: • The fan must be ≤ 100 hp. • As an add-on equipment installation, the VSD must be applied to the HVAC supply or return air system. • Any other throttling devices, such as inlet vanes or bypass dampers, and throttling valves, must be removed or permanently disabled. | Yes | VFD Installed Existing HVAC Supply_Return | Is the VFD being installed on an existing HVAC supply or return air system | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-28 | Kenny Liljestrom |  | Add | 74
0 | SWHC018 | 2 | VSD for HVAC Fan Controls, Commercial | Any | Any | Any |  | EECP | 6 | This measure requires the installation of a VSD and associated controls on a motor driving a ventilation fan. Eligibility requirements include: • The fan must be ≤ 100 hp. • As an add-on equipment installation, the VSD must be applied to the HVAC supply or return air system. • Any other throttling devices, such as inlet vanes or bypass dampers, and throttling valves, must be removed or permanently disabled. | Yes | Throttling Devices | Are there any other throttling devices, such as inlet vanes or bypass dampers, and throttling valves still operating? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-28 | Kenny Liljestrom |  | Add | 117
0 | SWHC018 | 2 | VSD for HVAC Fan Controls, Commercial | Any | Any | Any |  | EECP | 7 | Replacement of multiple-speed or variable speed motors (VSM) are not eligible. | Yes | Installation Include VSM | Does the installation include the replacement of multiple-speed or variable speed motors (VSM)? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-28 | Kenny Liljestrom |  | Add | 95
0 | SWHC018 | 2 | VSD for HVAC Fan Controls, Commercial | Any | Any | Any |  | EECP | 8 | Variable frequency drives on cooling tower fans are not eligible. | Yes | VFD Installed Cooling Tower Fans | Is the VFD being installed on cooling tower fans? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | Inspections | Observe the equipment where the motor was installed | The Variable Speed Drive must not be installed in a cooling tower | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-28 | Kenny Liljestrom |  | Add | 49
1 | SWHC020 | 1 | Air Cooled Chiller | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet |  | 2021-08-12 | Kenny Liljestrom |  | Add | 12
1 | SWHC020 | 1 | Air Cooled Chiller | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet |  | 2021-08-12 | Kenny Liljestrom |  | Add | 5
1 | SWHC020 | 1 | Air Cooled Chiller | Any | Any | Any |  | EECP | 3 | The energy and demand impacts of this measure are applicable only to commercial buildings with chiller equipment serving space comfort. Other chiller measures serving non-space comfort and/or processes and/or industrial applications shall be evaluated and incentivized under custom programs. | Yes |  | Does the chiller serve space conditioning equipment? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 52
1 | SWHC020 | 1 | Air Cooled Chiller | Any | Any | Any |  | EECP | 4 | Per Section 140.4 (j) of the 2019 California Building Energy Efficiency Standards (Title-24), chilled water plants shall not have more than 300 tons provided by air cooled chillers, except where the water quality at the building site fails to meet the manufacturer specifications for the use of water-cooled chillers, chillers that are used to charge a thermal energy storage system with a design temperature of less than 40 °F or systems serving healthcare facilities. | Yes |  | Sizing exemption for chillers > 300 tons | Drop Down List | N/A;Water quality does not meet equipment specs;Charge thermal energy storage with temp < 40F;Healthcare facility; | [8 empty] | Inspections | Use the data listed in EECP and try to validate the claim from the implementer | If EECP indicates, "N/A", then no action is required If EECP indicates, "Water quality does not meet equipment specs", then no action is required If EECP indicates, "Charge thermal energy storage with temp < 40F", then ask the customer to inspect the thermal energy storage system (the customer must have thermal energy storage) If EECP indicates, "Healthcare facility", then indicate whether or not the building is a healthcare facility (i.e. hospital, nursing home, etc.) | QA Checklist | Use the data listed in EECP and try to validate the claim from the implementer | If EECP indicates, "N/A", then no action is required If EECP indicates, "Water quality does not meet equipment specs", then check for proof of poor water quality in an installation report If EECP indicates, "Charge thermal energy storage with temp < 40F", then check for proof of the customer having a thermal energy storage system in an installation report If EECP indicates, "Healthcare facility", then check for proof of building type in EECP or installation report | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 40
1 | SWHC020 | 1 | Air Cooled Chiller | Any | Any | Any |  | EECP | 5 | Required for determining eligibility | Yes | Capacity (Tons) | Capacity (tons) | Numeric Value | [9 empty] | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 15
1 | SWHC020 | 1 | Air Cooled Chiller | A | Any | Any |  | EECP | 6 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency Rating | Full Load Energy Efficiency Rating (EER) | Numeric Value | [8 empty] | Must be >= 11.1 | QA Checklist | Use the manufacturer spec sheet to validate the Full Load Energy Efficiency Ratio (EER) is listed and matches EECP | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 40
1 | SWHC020 | 1 | Air Cooled Chiller | A | Any | Any |  | EECP | 7 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value | Integrated Part Load Value (IPLV) | Numeric Value | [8 empty] | Must be >= 15.4 | QA Checklist | Use the manufacturer spec sheet to validate the Integrated Part Load Value (IPLV) is listed and matches EECP | The Integrated Part Load Value (IPLV) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 33
1 | SWHC020 | 1 | Air Cooled Chiller | B | Any | Any |  | EECP | 8 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency Rating | Full Load Energy Efficiency Rating (EER) | Numeric Value | [8 empty] | Must be >= 12.1 | QA Checklist | Use the manufacturer spec sheet to validate the Full Load Energy Efficiency Ratio (EER) is listed and matches EECP | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 40
1 | SWHC020 | 1 | Air Cooled Chiller | B | Any | Any |  | EECP | 9 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value | Integrated Part Load Value (IPLV) | Numeric Value | [8 empty] | Must be >= 16.9 | QA Checklist | Use the manufacturer spec sheet to validate the Integrated Part Load Value (IPLV) is listed and matches EECP | The Integrated Part Load Value (IPLV) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16.9 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 33
1 | SWHC020 | 1 | Air Cooled Chiller | C | Any | Any |  | EECP | 10 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency Rating | Full Load Energy Efficiency Rating (EER) | Numeric Value | [8 empty] | Must be >= 11.1 | QA Checklist | Use the manufacturer spec sheet to validate the Full Load Energy Efficiency Ratio (EER) is listed and matches EECP | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 40
1 | SWHC020 | 1 | Air Cooled Chiller | C | Any | Any |  | EECP | 11 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value | Integrated Part Load Value (IPLV) | Numeric Value | [8 empty] | Must be >= 15.1 | QA Checklist | Use the manufacturer spec sheet to validate the Integrated Part Load Value (IPLV) is listed and matches EECP | The Integrated Part Load Value (IPLV) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 33
1 | SWHC020 | 1 | Air Cooled Chiller | D | Any | Any |  | EECP | 12 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Full Load Energy Efficiency Rating | Full Load Energy Efficiency Rating (EER) | Numeric Value | [8 empty] | Must be >= 12.1 | QA Checklist | Use the manufacturer spec sheet to validate the Full Load Energy Efficiency Ratio (EER) is listed and matches EECP | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 40
1 | SWHC020 | 1 | Air Cooled Chiller | D | Any | Any |  | EECP | 13 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | Integrated Part Load Value | Integrated Part Load Value (IPLV) | Numeric Value | [8 empty] | Must be >= 16.6 | QA Checklist | Use the manufacturer spec sheet to validate the Integrated Part Load Value (IPLV) is listed and matches EECP | The Integrated Part Load Value (IPLV) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16.6 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-08-12 | Kenny Liljestrom |  | Add | 33
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | UpDeemed |  | EECP | 0 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | UpDeemed |  | EECP | 5 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | Any |  | EECP | 10 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet |  | 2021-11-12 | Kenny Liljestrom |  |  | 12
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | Any |  | EECP | 15 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet |  | 2021-11-12 | Kenny Liljestrom |  |  | 5
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | UpDeemed |  | EECP | 20 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number in EECP should match what is listed in the invoice or installation report |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | UpDeemed |  | EECP | 25 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [9 empty] | QA Checklist | Review the AHRI database to check for the make and model of the installed equipment | The equipment in EECP should be locatable on the AHRI database as being a certified product and should match the make and model of the equipment | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | UpDeemed |  | EECP | 30 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value |  |  |  |  | Currency |  |  | 2 |  | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | UpDeemed |  | EECP | 190 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value |  |  |  |  | General |  |  | 0 |  | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | UpDeemed |  | EECP | 195 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | Any |  | EECP | 35 | The energy and demand impacts of this measure are applicable only to commercial buildings with chiller equipment serving space comfort. Other chiller measures serving non-space comfort and/or processes and/or industrial applications shall be evaluated and incentivized under custom programs. | Yes | ChillerPurpose | Does the chiller serve space conditioning/comfort equipment? | Drop Down List | Yes;No; |  | Equal | Yes |  |  |  |  | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Updated property label | 2021-11-12 | Kenny Liljestrom |  |  | 60
0 | SWHC020 | 2 | Air Cooled Chiller | Any | Any | Any |  | EECP | 40 | Per Section 140.4 (j) of the 2019 California Building Energy Efficiency Standards (Title-24), chilled water plants shall not have more than 300 tons provided by air cooled chillers, except where the water quality at the building site fails to meet the manufacturer specifications for the use of water-cooled chillers, chillers that are used to charge a thermal energy storage system with a design temperature of less than 40 °F or systems serving healthcare facilities. | Yes | Size Exemption | Sizing exemption for chillers > 300 tons | Drop Down List | N/A;Water quality does not meet equipment specs;Charge thermal energy storage with temp < 40F;Healthcare facility; | [8 empty] | Inspections | Use the data listed in EECP and try to validate the claim from the implementer | If EECP indicates, "N/A", then no action is required If EECP indicates, "Water quality does not meet equipment specs", then no action is required If EECP indicates, "Charge thermal energy storage with temp < 40F", then ask the customer to inspect the thermal energy storage system (the customer must have thermal energy storage) If EECP indicates, "Healthcare facility", then indicate whether or not the building is a healthcare facility (i.e. hospital, nursing home, etc.) | QA Checklist | Use the data listed in EECP and try to validate the claim from the implementer | If EECP indicates, "N/A", then no action is required If EECP indicates, "Water quality does not meet equipment specs", then check for proof of poor water quality in an installation report If EECP indicates, "Charge thermal energy storage with temp < 40F", then check for proof of the customer having a thermal energy storage system in an installation report If EECP indicates, "Healthcare facility", then check for proof of building type in EECP or installation report | Not configured in original upload | 2021-11-12 | Kenny Liljestrom |  |  | 40
0 | SWHC020 | 2 | Air Cooled Chiller | A | Any | Any |  | EECP | 45 | Required for determining eligibility | Yes | Capacity (Tons) | Capacity (tons) | Numeric Value |  |  |  |  | General | 150 |  | 0 | Must be >= 150 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 15
0 | SWHC020 | 2 | Air Cooled Chiller | B | Any | Any |  | EECP | 45 | Required for determining eligibility | Yes | Capacity (Tons) | Capacity (tons) | Numeric Value |  |  |  |  | General | 150 |  | 0 | Must be >= 150 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 15
0 | SWHC020 | 2 | Air Cooled Chiller | C | Any | Any |  | EECP | 45 | Required for determining eligibility | Yes | Capacity (Tons) | Capacity (tons) | Numeric Value |  |  |  |  | General | 0 | 149 | 0 | Must be < 150 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 15
0 | SWHC020 | 2 | Air Cooled Chiller | D | Any | Any |  | EECP | 45 | Required for determining eligibility | Yes | Capacity (Tons) | Capacity (tons) | Numeric Value |  |  |  |  | General | 0 | 149 | 0 | Must be < 150 | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | The listed capacity in EECP should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 15
0 | SWHC020 | 2 | Air Cooled Chiller | A | Any | Any |  | EECP | 50 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | FL EER | Full Load Energy Efficiency Rating (EER) | Numeric Value |  |  |  |  | General | 11.1 |  | 1 | Must be >= 11.1 | QA Checklist | Use the manufacturer spec sheet to validate the Full Load Energy Efficiency Ratio (EER) is listed and matches EECP | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 40
0 | SWHC020 | 2 | Air Cooled Chiller | A | Any | Any |  | EECP | 55 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | IPLV | Integrated Part Load Value (IPLV) | Numeric Value |  |  |  |  | General | 15.4 |  | 1 | Must be >= 15.4 | QA Checklist | Use the manufacturer spec sheet to validate the Integrated Part Load Value (IPLV) is listed and matches EECP | The Integrated Part Load Value (IPLV) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 33
0 | SWHC020 | 2 | Air Cooled Chiller | B | Any | Any |  | EECP | 50 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | FL EER | Full Load Energy Efficiency Rating (EER) | Numeric Value |  |  |  |  | General | 12.1 |  | 1 | Must be >= 12.1 | QA Checklist | Use the manufacturer spec sheet to validate the Full Load Energy Efficiency Ratio (EER) is listed and matches EECP | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 40
0 | SWHC020 | 2 | Air Cooled Chiller | B | Any | Any |  | EECP | 55 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | IPLV | Integrated Part Load Value (IPLV) | Numeric Value |  |  |  |  | General | 16.9 |  | 1 | Must be >= 16.9 | QA Checklist | Use the manufacturer spec sheet to validate the Integrated Part Load Value (IPLV) is listed and matches EECP | The Integrated Part Load Value (IPLV) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16.9 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 33
0 | SWHC020 | 2 | Air Cooled Chiller | C | Any | Any |  | EECP | 50 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | FL EER | Full Load Energy Efficiency Rating (EER) | Numeric Value |  |  |  |  | General | 11.1 |  | 1 | Must be >= 11.1 | QA Checklist | Use the manufacturer spec sheet to validate the Full Load Energy Efficiency Ratio (EER) is listed and matches EECP | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 11.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 40
0 | SWHC020 | 2 | Air Cooled Chiller | C | Any | Any |  | EECP | 55 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | IPLV | Integrated Part Load Value (IPLV) | Numeric Value |  |  |  |  | General | 15.1 |  | 1 | Must be >= 15.1 | QA Checklist | Use the manufacturer spec sheet to validate the Integrated Part Load Value (IPLV) is listed and matches EECP | The Integrated Part Load Value (IPLV) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 33
0 | SWHC020 | 2 | Air Cooled Chiller | D | Any | Any |  | EECP | 50 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | FL EER | Full Load Energy Efficiency Rating (EER) | Numeric Value |  |  |  |  | General | 12.1 |  | 1 | Must be >= 12.1 | QA Checklist | Use the manufacturer spec sheet to validate the Full Load Energy Efficiency Ratio (EER) is listed and matches EECP | The Energy Efficiency Ratio (EER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 12.1 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 40
0 | SWHC020 | 2 | Air Cooled Chiller | D | Any | Any |  | EECP | 55 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Yes | IPLV | Integrated Part Load Value (IPLV) | Numeric Value |  |  |  |  | General | 16.6 |  | 1 | Must be >= 16.6 | QA Checklist | Use the manufacturer spec sheet to validate the Integrated Part Load Value (IPLV) is listed and matches EECP | The Integrated Part Load Value (IPLV) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16.6 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label | 2021-11-12 | Kenny Liljestrom |  |  | 33
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-12 | Kenny Liljestrom |  | Add | 12
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-12 | Kenny Liljestrom |  | Add | 5
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any |  | EECP | 3 | This measure requires field documentation of the existing conditions that verify the measure was necessary and that the measure was successfully applied. Contractors and technicians that implement these measures must ensure that the existing unit does not already have these measures. This measure must replace existing equipment with the addition of controls for existing units. | Yes |  | Have existing conditions been recorded and measures are were NOT previously installed? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the submitted installation report to verify existing conditions have been documented (i.e. unit is operational, supply fan is working, economizer is functioning, etc.). | The installation report should indicate the existing conditions (conditions in following checkpoints) of the unit and the proposed measures were not previously installed on the unit. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 86
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any |  | EECP | 4 | Terms and conditions are noted below. Other terms and conditions are set by individual programs. • The existing system must be packaged single zone DX cooling unit with gas heat, cooling only unit, or heat pump. • The existing system must have a constant volume supply fan. • The existing system must have an operable airside economizer installed, and economizer high limit must be optimized for the climate per Title 24 2016 Table 140.4-B, adapted below in Table 2 for reference. • Maintenance, and repairs to economizer should be completed prior to or in conjunction with this measure. | Yes |  | Existing system is packaged single zone DX cooling w/ gas heat, cooling only, or heat pump? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Using the manufacturer spec sheet, verify the unit type is either a packaged single zone DX cooling w/ gas heat, cooling only, or heat pump | The unit type must either be a packaged single zone DX cooling w/ gas heat, cooling only, or heat pump. Rooftop Unit (RTU) is also acceptable. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 91
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any |  | EECP | 5 | Terms and conditions are noted below. Other terms and conditions are set by individual programs. • The existing system must be packaged single zone DX cooling unit with gas heat, cooling only unit, or heat pump. • The existing system must have a constant volume supply fan. • The existing system must have an operable airside economizer installed, and economizer high limit must be optimized for the climate per Title 24 2016 Table 140.4-B, adapted below in Table 2 for reference. • Maintenance, and repairs to economizer should be completed prior to or in conjunction with this measure. | Yes |  | Existing system has a constant volume supply fan? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Using the installation report, verify the supply fan is a constant volume type | The existing supply fan must be a constant volume type to be eligible | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 49
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any |  | EECP | 6 | Terms and conditions are noted below. Other terms and conditions are set by individual programs. • The existing system must be packaged single zone DX cooling unit with gas heat, cooling only unit, or heat pump. • The existing system must have a constant volume supply fan. • The existing system must have an operable airside economizer installed, and economizer high limit must be optimized for the climate per Title 24 2016 Table 140.4-B, adapted below in Table 2 for reference. • Maintenance, and repairs to economizer should be completed prior to or in conjunction with this measure. | Yes |  | Existing system has operable economizer with high limit set per Title 24 2016 Table 140.4-B? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | The installation report should indicate the Climate Zone of the site and the Economizer high limit (F) | Using the table in the workpaper, or using EnergyCodeAce's Reference Ace for Title-24 2016 Table 140.4-B, verify the Economizer setpoint is eligible based on the climate zone of the site. Toa in the workpaper is also referred to as Outside Air Temperature (OAT). Tra is also referred to as Return Air Temperature (RAT). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 92
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any |  | EECP | 7 | This measure does not apply if the rooftop unit (RTU) has a fully operational and/or non-snapdisc sensor and is adjusted to the appropriate changeover setpoint based on the number of thermostat stages available for cooling. | Yes |  | Existing system can adjust to changeover setpoint based on thermostat stages available for cooling? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 99
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any |  | EECP | 8 | This measure does not apply if the unoccupied supply fan operation is already set to “Auto” or intermittent. | Yes |  | Unoccupied supply fan operation already set to “Auto” or intermittent? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 70
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any |  | EECP | 9 | Terms and conditions are noted below. Other terms and conditions are set by individual programs. • The existing system must be packaged single zone DX cooling unit with gas heat, cooling only unit, or heat pump. • The existing system must have a constant volume supply fan. • The existing system must have an operable airside economizer installed, and economizer high limit must be optimized for the climate per Title 24 2016 Table 140.4-B, adapted below in Table 2 for reference. • Maintenance, and repairs to economizer should be completed prior to or in conjunction with this measure. | Yes |  | Any maintenance or repairs to economizer? If so, what was done? | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 63
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any |  | EECP | 10 | Implementation requires proper setup of the damper limits and fan speeds in order to provide ventilation in accordance with Title 24 2016 (see Code requirements). Total unit airflow must be verified for at least one of the fan speeds. The percentage of outdoor air must be verified for each of the unit operating modes, including heating and cooling for each stage as well as the ventilation only mode. | Yes |  | Total unit airflow has been verified for at least one of the fan speeds? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Using the installation report, verify the total unit airflow has been recorded after the measure installation | As long as there is a value for the total unit airflow at one of the operating speeds, there are no other validation criteria to check | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 72
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any |  | EECP | 11 | Implementation requires proper setup of the damper limits and fan speeds in order to provide ventilation in accordance with Title 24 2016 (see Code requirements). Total unit airflow must be verified for at least one of the fan speeds. The percentage of outdoor air must be verified for each of the unit operating modes, including heating and cooling for each stage as well as the ventilation only mode. | Yes |  | Percent OA verified for heating and cooling for each stage as well as ventilation only mode? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 92
1 | SWHC023 | 2 | Enhanced Ventilation For Packaged HVAC, Commercial | Any | Any | Any |  | EECP | 12 | This measure is applicable for all nonresidential buildings served by unitary direct expansion (DX) and split systems that do not serve process or refrigeration loads. The target market for this measure includes commercial buildings served by packaged single zone HVAC units, sometimes referred to as rooftop units (RTUs). | Yes |  | System used for comfort/space cooling, not process or refrigeration loads? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-12 | Kenny Liljestrom |  | Add | 74
0 | SWHC024 | 1 | Cogged V-Belt For HVAC Fan, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice, installation report, or spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-17 | Kenny Liljestrom |  | Add | 12
0 | SWHC024 | 1 | Cogged V-Belt For HVAC Fan, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice, installation report, or spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-17 | Kenny Liljestrom |  | Add | 5
0 | SWHC024 | 1 | Cogged V-Belt For HVAC Fan, Commercial | Any | Any | Any |  | EECP | 3 | This measure is applicable for package rooftop HVAC systems in the following nonresidential building types. The measure is eligible for all vintages (old, existing, recent, and new). | Yes |  | Building Type | Drop Down List | Assembly;Health/Medical – Nursing Home;Education – Community College;Office – Large;Education – Primary School;Office – Small;Education – Secondary School;Restaurant - Fast-Food;Education – University;Restaurant - Sit-Down;Education – Relocatable Classroom;Retail - Multistory Large;Health/Medical – Hospital;Retail - Single-Story Large;Lodging – Hotel;Retail – Small;Lodging – Motel;Storage – Conditioned;Manufacturing - Bio/Tech;Grocery;Manufacturing – Light Industrial; | [8 empty] | Inspections | Document the type of building the V-belt was installed in | The building type listed in EECP should match the building type during the inspection | QA Checklist | Use the building type from the EECP enrollment phase to determine if the project is eligible | The building type validation is set in EECP, verify building type is one of the following: Assembly; Health/Medical – Nursing Home; Education – Community College; Office – Large; Education – Primary School; Office – Small; Education – Secondary School; Restaurant - Fast-Food; Education – University; Restaurant - Sit-Down; Education – Relocatable Classroom; Retail - Multistory Large; Health/Medical – Hospital; Retail - Single-Story Large; Lodging – Hotel; Retail – Small; Lodging – Motel; Storage – Conditioned; Manufacturing - Bio/Tech; Grocery; Manufacturing – Light Industrial; | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 13
0 | SWHC024 | 1 | Cogged V-Belt For HVAC Fan, Commercial | Any | Any | Any |  | EECP | 4 | Good to have for data collection | Yes | Capacity (Tons) | Capacity (Tons) | Numeric Value | [9 empty] | Inspections | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | The listed capacity in EECP should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to tons can be done with the following formula: Capacity (btu/hr) / 12,000 = tons | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-17 | Kenny Liljestrom |  | Add | 15
0 | SWHC024 | 1 | Cogged V-Belt For HVAC Fan, Commercial | Any | Any | Any |  | EECP | 5 | - | Yes | Size | Capacity (Tons) | Numeric Value | [9 empty] | - | - | - | - | - | - | Duplicate property, can be removed | 2021-08-17 | Kenny Liljestrom |  | Add | 15
0 | SWHC024 | 1 | Cogged V-Belt For HVAC Fan, Commercial | Any | Any | Any |  | EECP | 6 | Only “A” and “B” V-belts, the two types typically used in rooftop units, are applicable for this measure. | Yes | Belt Type | Belt Type Installed | Drop Down List | A Belt¦1;B Belt¦2;Both¦3 | [8 empty] | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the type of V-Belt is listed | The V-Belt type listed in EECP should match what is listed in spec sheet; the V-Belt type should either be A, B, or both (it should not be type C or D) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-17 | Kenny Liljestrom |  | Add | 19
0 | SWHC024 | 1 | Cogged V-Belt For HVAC Fan, Commercial | Any | Any | Any |  | EECP | 7 | A cogged V-belt can be installed on supply air and return air fans in rooftop units that do not already have a cogged V-belt. | Yes | Cogged V Belt | Is the existing belt a cogged V-belt? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-17 | Kenny Liljestrom |  | Add | 37
1 | SWHC024 | 2 | Cogged V-Belt for HVAC Fan, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-28 | Kenny Liljestrom |  | Add | 12
1 | SWHC024 | 2 | Cogged V-Belt for HVAC Fan, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-28 | Kenny Liljestrom |  | Add | 5
1 | SWHC024 | 2 | Cogged V-Belt for HVAC Fan, Commercial | Any | Any | Any |  | EECP | 3 | A cogged V-belt can be installed on supply air and return air fans in rooftop units that do not already have a cogged V-belt. | Yes | Belt Type | Belt Type Installed | Drop Down List | A Belt¦1;B Belt¦2;Both¦3 | [8 empty] | QA Checklist | Use the manufacturer spec sheet to validate the type of V-Belt installed (A, B, C, or D) | The belt must be listed as Type A, Type B, or both Type A and B; it must not be listed as Type C or D | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-28 | Kenny Liljestrom |  | Add | 19
1 | SWHC024 | 2 | Cogged V-Belt for HVAC Fan, Commercial | Any | Any | Any |  | EECP | 4 | A cogged V-belt can be installed on supply air and return air fans in rooftop units that do not already have a cogged V-belt. | Yes | Cogged V Belt | Is the existing belt a cogged V-belt? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet to validate the belt is listed as a cogged V-belt | The belt must be listed as a cogged v-belt | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-28 | Kenny Liljestrom |  | Add | 37
1 | SWHC024 | 2 | Cogged V-Belt for HVAC Fan, Commercial | Any | Any | Any |  | QA Checklist | 5 | This measure is applicable for package rooftop HVAC systems in the following nonresidential building types. The measure is eligible for all vintages (old, existing, recent, and new). Assembly, Education - Community College, Education - Primary School, Education - Secondary School, Education - University, Education - Relocatable Classroom, Health/Medical - Hospital, Lodging - Hotel, Lodging - Motel, Manufacturing - Bio/Tech, Manufacturing - Light Industrial, Health/Medical - Nursing Home, Office Large, Office Small, Restaurant - Fast Food, Restaurant - Sit-Down, Retail - Multistory Large, Retail - Small, Storage - Conditioned, Grocery | Yes |  | Building Type | Drop Down List | Assembly;Education - Community College;Education - Primary School;Education - Secondary School;Education - University;Education - Relocatable Classroom;Health/Medical - Hospital;Lodging - Hotel;Lodging - Motel;Manufacturing - Bio/Tech;Manufacturing - Light Industrial;Health/Medical - Nursing Home;Office Large;Office Small;Restaurant - Fast Food;Restaurant - Sit-Down;Retail - Multistory Large;Retail - Small;Storage - Conditioned;Grocery; | [8 empty] | QA Checklist | Ensure building type in EECP matches one of the eligible building types | The building type must be one of the following and match what is listed in EECP: Assembly; Education - Community College; Education - Primary School; Education - Secondary School; Education - University; Education - Relocatable Classroom; Health/Medical - Hospital; Lodging - Hotel; Lodging - Motel; Manufacturing - Bio/Tech; Manufacturing - Light Industrial; Health/Medical - Nursing Home; Office Large; Office Small; Restaurant - Fast Food; Restaurant - Sit-Down; Retail - Multistory Large; Retail - Small; Storage - Conditioned; Grocery; | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Ensure building type in EECP matches one of the eligible building types | 2021-08-24 | Kenny Liljestrom |  | Add | 13
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-28 | Kenny Liljestrom |  | Add | 12
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-28 | Kenny Liljestrom |  | Add | 5
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any |  | QA Checklist | 3 | All existing building vintages are eligible for all building types; new construction is only available for nonresidential building types. Eligible building types include: Health/Medical - Nursing Home, Lodging - Hotel, Lodging - Guest Rooms, Lodging - Motel, Manufacturing - Bio/Tech, Manufacturing - Light Industrial, Office - Large, Office - Small, Restaurant - Fast-Food, Restaurant - Small, Warehouse - Refrigerated, Residential Multi-Family (Common), Residential Multi-Family (Dwelling Unit), Residential Single Family. | Yes |  | Building Type | [9 empty] | Must meet measure level building type | QA Checklist | Ensure building type in EECP matches one of the eligible building types | All existing building vintages are eligible for all building types; new construction is only available for nonresidential building types. Eligible building types include: Health/Medical - Nursing Home, Lodging - Hotel, Lodging - Guest Rooms, Lodging - Motel, Manufacturing - Bio/Tech, Manufacturing - Light Industrial, Office - Large, Office - Small, Restaurant - Fast-Food, Restaurant - Small, Warehouse - Refrigerated, Residential Multi-Family (Common), Residential Multi-Family (Dwelling Unit), Residential Single Family. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-24 | Kenny Liljestrom |  | Add | 13
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | A | Any | Any |  | EECP | 4 | Ductless mini-split AC are not eligible. | Yes | Mini-Split AC | Is the equipment a ductless mini-split air conditioner? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Use the manufacturer spec sheet to validate the HVAC equipment type | The HVAC equipment must not be listed as a ductless split system air conditioner or ductless split system heat pump | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-28 | Kenny Liljestrom |  | Add | 55
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | A | Any | Any |  | EECP | 5 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes |  | Size (Btu/hr) | Numeric Value | [9 empty] | Inspections | Photograph the nameplate showing the capacity (Btu/hr) of the unit; if the nameplate is inaccessible, this property can be validated by the processing team | The capacity listed in EECP should match what is listed on the nameplate | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the capacity (Btu/hr) is listed | The capacity listed in EECP should match the what is listed in the installation report or manufacturer spec sheet | Needs to be reconfigured to be in-line with measure case descriptions | 2021-08-24 | Kenny Liljestrom |  | Add | 13
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | A | Any | Any |  | EECP | 6 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | EER | Equipment Efficiency (EER) | Numeric Value | [9 empty] | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | The EER listed in EECP should match the what is listed in the installation report or manufacturer spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Remove, Incorrect property label and duplicate with 'Energy Efficiency Rating (EER)' | 2021-06-28 | Kenny Liljestrom |  | Add | 26
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | A | NR | Any |  | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [8 empty] | If 'Size' is <= 7000 then must be >= 11.29 If 'Size' is 7000 < x <= 15000 then must be >= 10.27 If 'Size' is > 15000 then must be >= 9.25 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-06-28 | Kenny Liljestrom |  | Add | 30
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | A | NC | Any |  | EECP | 8 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [8 empty] | If 'Size' is <= 7000 then must be >= 14.28 If 'Size' is 7000 < x <= 15000 then must be >= 12.84 If 'Size' is > 15000 then must be >= 11.40 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 14.28 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 12.84 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 11.40 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-06-28 | Kenny Liljestrom |  | Add | 30
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | A | Any | Any |  | EECP | 9 | The measure case is defined as a package terminal air conditioner (PTAC) or a package terminal heat pump (PTHP) that is through-the-wall, self-contained, with a cooling capacity ≤ 2 tons (≤ 24 kBtu/hr) and an energy efficient rating (EER) that is 20% higher than the base case. | Yes | EER Exceed Code | Does the EER of the installed unit exceed code by at least 20%? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | - | - | - | - | - | - | Seems a bit redundant with the measure case description, can remove | 2021-06-28 | Kenny Liljestrom |  | Add | 63
0 | SWHC027 | 1 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | A | Any | Any |  | EECP | 10 | Ductless mini-split AC are not eligible. | Yes | High Eff PTAC DX Unit Installed | Was a High Efficiency Package Terminal Air Conditioner (Non Res) DX Unit installed? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | - | - | - | - | - | - | Seems a bit redundant with the measure case description, can remove | 2021-06-28 | Kenny Liljestrom |  | Add | 83
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-11 | Kenny Liljestrom |  |  | 12
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-11 | Kenny Liljestrom |  |  | 5
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any |  | QA Checklist | 3 | All existing building vintages are eligible for all building types; new construction is only available for nonresidential building types. Eligible building types include: Health/Medical - Nursing Home, Lodging - Hotel, Lodging - Guest Rooms, Lodging - Motel, Manufacturing - Bio/Tech, Manufacturing - Light Industrial, Office - Large, Office - Small, Restaurant - Fast-Food, Restaurant - Small, Warehouse - Refrigerated, Residential Multi-Family (Common), Residential Multi-Family (Dwelling Unit), Residential Single Family. | Yes |  | Building Type | [9 empty] | Must meet measure level building type | QA Checklist | Ensure building type in EECP matches one of the eligible building types | All existing building vintages are eligible for all building types; new construction is only available for nonresidential building types. Eligible building types include: Health/Medical - Nursing Home, Lodging - Hotel, Lodging - Guest Rooms, Lodging - Motel, Manufacturing - Bio/Tech, Manufacturing - Light Industrial, Office - Large, Office - Small, Restaurant - Fast-Food, Restaurant - Small, Warehouse - Refrigerated, Residential Multi-Family (Common), Residential Multi-Family (Dwelling Unit), Residential Single Family. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-11 | Kenny Liljestrom |  |  | 13
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any |  | EECP | 4 | Required for measure case description check, Ductless mini-split AC are not eligible. | Yes | Mini-Split AC | Is the equipment a ductless mini-split air conditioner? | Drop Down List | Yes;No; | [7 empty] | Must be No | QA Checklist | Use the manufacturer spec sheet to validate the HVAC equipment type | The HVAC equipment must not be listed as a ductless split system air conditioner or ductless split system heat pump | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Retire/remove Property, captured in the property below and moved to QA Checklist | 2021-11-11 | Kenny Liljestrom |  |  | 55
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any |  | QA Checklist | 4 | Required for measure case description check, Ductless mini-split AC are not eligible. | Yes |  | Does the equipment type match the Measure Case Description (Air Conditioner or Heat Pump) and is not a ductless mini-split air conditioner? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer spec sheet to validate the HVAC equipment type | The HVAC equipment must not be listed as a ductless split system air conditioner or ductless split system heat pump | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-11 | Kenny Liljestrom |  |  | 139
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any |  | EECP | 5 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Capacity (BTU/hr) | Capacity (BTU/hr) | Numeric Value | [9 empty] | Inspections | Photograph the nameplate showing the capacity (Btu/hr) of the unit; if the nameplate is inaccessible, this property can be validated by the processing team | The capacity listed in EECP should match what is listed on the nameplate | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the capacity (Btu/hr) is listed | The capacity listed in EECP should match the what is listed in the installation report or manufacturer spec sheet | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 17
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | A | NR | Any |  | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [8 empty] | If 'Size' is <= 7000 then must be >= 11.29 If 'Size' is 7000 < x <= 15000 then must be >= 10.27 If 'Size' is > 15000 then must be >= 9.25 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | B | NR | Any |  | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [8 empty] | If 'Size' is <= 7000 then must be >= 11.29 If 'Size' is 7000 < x <= 15000 then must be >= 10.27 If 'Size' is > 15000 then must be >= 9.25 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | C | NR | Any |  | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [8 empty] | If 'Size' is <= 7000 then must be >= 11.17 If 'Size' is 7000 < x <= 15000 then must be >= 10.15 If 'Size' is > 15000 then must be >= 9.13 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | D | NR | Any |  | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [8 empty] | If 'Size' is <= 7000 then must be >= 11.29 If 'Size' is 7000 < x <= 15000 then must be >= 10.27 If 'Size' is > 15000 then must be >= 9.25 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | E | NR | Any |  | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [8 empty] | If 'Size' is <= 7000 then must be >= 11.17 If 'Size' is 7000 < x <= 15000 then must be >= 10.15 If 'Size' is > 15000 then must be >= 9.13 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | F | NR | Any |  | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [8 empty] | If 'Size' is <= 7000 then must be >= 11.17 If 'Size' is 7000 < x <= 15000 then must be >= 10.15 If 'Size' is > 15000 then must be >= 9.13 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | G | NR | Any |  | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [8 empty] | If 'Size' is <= 7000 then must be >= 11.29 If 'Size' is 7000 < x <= 15000 then must be >= 10.27 If 'Size' is > 15000 then must be >= 9.25 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | H | NR | Any |  | EECP | 7 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [8 empty] | If 'Size' is <= 7000 then must be >= 11.17 If 'Size' is 7000 < x <= 15000 then must be >= 10.15 If 'Size' is > 15000 then must be >= 9.13 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 11.29 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 10.27 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 9.25 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | NC | Any |  | EECP | 8 | The PTAC or PTHP must meet the measure case specification, see Measure Case Description. | Yes | Energy Efficiency Rating | Energy Efficiency Rating (EER) | Numeric Value | [8 empty] | If 'Size' is <= 7000 then must be >= 14.28 If 'Size' is 7000 < x <= 15000 then must be >= 12.84 If 'Size' is > 15000 then must be >= 11.40 | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the Energy Efficiency Ratio (EER) is listed | If the unit capacity (Btu/hr) is <= 7000 Btu/hr then the EER must be >= 14.28 If the unit capacity (Btu/hr) is 7000 < x <= 15000 then the EER must be >= 12.84 If the unit capacity (Btu/hr) is > 15000 then the EER must be >= 11.40 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Needs to be reconfigured to be in-line with measure case descriptions | 2021-11-11 | Kenny Liljestrom |  |  | 30
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any |  | EECP | 9 | The measure case is defined as a package terminal air conditioner (PTAC) or a package terminal heat pump (PTHP) that is through-the-wall, self-contained, with a cooling capacity ≤ 2 tons (≤ 24 kBtu/hr) and an energy efficient rating (EER) that is 20% higher than the base case. | Yes | EER Exceed Code | Does the EER of the installed unit exceed code by at least 20%? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | - | - | - | - | - | - | Seems a bit redundant with the measure case description, can remove/retire | 2021-11-11 | Kenny Liljestrom |  |  | 63
1 | SWHC027 | 2 | Package Terminal Air Conditioner or Heat Pump, Under 24 kBtu/hr | Any | Any | Any |  | EECP | 10 | Ductless mini-split AC are not eligible. | Yes | High Eff PTAC DX Unit Installed | Was a High Efficiency Package Terminal Air Conditioner (Non Res) DX Unit installed? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | - | - | - | - | - | - | Seems a bit redundant with the measure case description, can remove/retire | 2021-11-11 | Kenny Liljestrom |  |  | 83
0 | SWHC029 | 1 | Fan Controller for Air Conditioner, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWHC029 | 1 | Fan Controller for Air Conditioner, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWHC029 | 1 | Fan Controller for Air Conditioner, Residential | Any | Any | Any |  | EECP | 3 | Both automated (logic-based) fan controllers and manually set time-delay fan controllers are eligible. | Yes | Type | Type of fan controller installed? | Drop Down List | Automated (logic-based) fan controller;Manually set time-delay fan controller | [8 empty] | QA Checklist | Use the manufacturer specification sheet to determine the type of fan controller installed | The fan controller type should be: Automated (logic-based) fan controller or Manually set time-delay fan controller | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 33
0 | SWHC029 | 1 | Fan Controller for Air Conditioner, Residential | Any | Any | Any |  | EECP | 4 | The installation of a manually set time-delay fan controller requires the invoice and/or installation contract that verifies the equipment was installed by a qualified HVAC contractor. | Yes | Manually Set Time Delay | This equipment must be installed by a qualified HVAC Contractor. Please verify the invoice and/or installation contract that verifies the equipment was installed by a qualified HVAC contractor has been submitted. | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Invoice or documentation should indicate who installed the controller | Cross check if the installer is a qualified contractor by searching their contractor license number or company against the trade pro list | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 212
0 | SWHC029 | 1 | Fan Controller for Air Conditioner, Residential | Any | Any | Any |  | EECP | 5 | This measure only applies to a fully functional central residential air conditioning unit equipped with cooling/evaporator (DX) coils. | Yes | Working HVAC | Installed to a functional HVAC unit with cooling/evaporator (dx) coils? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Check the HVAC system to see if it is energized and functional | Check the HVAC system to see if it is energized and functional (operating if there is a call for conditioned air) | QA Checklist | Use the installation report to ensure the baseline (existing conditions) are documented | A detailed report from the implementer showing the baseline operating performance (tested data before and after); before data should show values indicating the fan was working |  | 2021-06-21 | Kenny Liljestrom |  | Add | 71
0 | SWHC029 | 1 | Fan Controller for Air Conditioner, Residential | Any | Any | Any |  | EECP | 6 | All installations shall comply with all current applicable regulations, code, and standards including (but not limited to) the California Building Energy Efficiency Standards (Title 24), the California Appliance Efficiency Regulations (Title 20), and the National Electrical Code (NEC). | Yes | Code | Does the installation comply with all current applicable regulations, code, and standards? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 90
0 | SWHC029 | 1 | Fan Controller for Air Conditioner, Residential | Any | Any | Any |  | EECP | 7 | A fan controller used for solely optimizing and improving heating efficiency including those for gas furnaces is not eligible. | Yes | Fan Controller | Is the fan controller used for solely optimizing and improving heating efficiency including those for gas furnaces? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Locate the fan controller for the associated gas furnace | Check to see whether the fan controller is installed on a fan in the ducting supplied by a gas fired furnace | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 115
0 | SWHC029 | 1 | Fan Controller for Air Conditioner, Residential | Any | Any | Any |  | EECP | 8 | The baseline air conditioning system cannot be equipped with a hardware based built-in delay controller. | Yes | Baseline AC | Is the baseline air conditioning system equipped with a hardware based built-in delay controller? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 97
1 | SWHC029 | 2 | Fan Controller for Air Conditioner, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
1 | SWHC029 | 2 | Fan Controller for Air Conditioner, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
1 | SWHC029 | 2 | Fan Controller for Air Conditioner, Residential | Any | Any | Any |  | EECP | 3 | Both automated (logic-based) fan controllers and manually set time-delay fan controllers are eligible. | Yes | Type | Type of fan controller installed? | Drop Down List | Automated (logic-based) fan controller;Manually set time-delay fan controller | [8 empty] | QA Checklist | Use the manufacturer specification sheet to determine the type of fan controller installed | The fan controller type should be: Automated (logic-based) fan controller or Manually set time-delay fan controller | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 33
1 | SWHC029 | 2 | Fan Controller for Air Conditioner, Residential | Any | Any | Any |  | EECP | 4 | The installation of a manually set time-delay fan controller requires the invoice and/or installation contract that verifies the equipment was installed by a qualified HVAC contractor. | Yes | Manually Set Time Delay | This equipment must be installed by a qualified HVAC Contractor. Please verify the invoice and/or installation contract that verifies the equipment was installed by a qualified HVAC contractor has been submitted. | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Invoice or documentation should indicate who installed the controller | Cross check if the installer is a qualified contractor by searching their contractor license number or company against the trade pro list | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 212
1 | SWHC029 | 2 | Fan Controller for Air Conditioner, Residential | Any | Any | Any |  | EECP | 5 | This measure only applies to a fully functional central residential air conditioning unit equipped with cooling/evaporator (DX) coils. | Yes | Working HVAC | Installed to a functional HVAC unit with cooling/evaporator (dx) coils? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Check the HVAC system to see if it is energized and functional | Check the HVAC system to see if it is energized and functional (operating if there is a call for conditioned air) | QA Checklist | Use the installation report to ensure the baseline (existing conditions) are documented | A detailed report from the implementer showing the baseline operating performance (tested data before and after); before data should show values indicating the fan was working |  | 2021-06-21 | Kenny Liljestrom |  | Add | 71
1 | SWHC029 | 2 | Fan Controller for Air Conditioner, Residential | Any | Any | Any |  | EECP | 6 | All installations shall comply with all current applicable regulations, code, and standards including (but not limited to) the California Building Energy Efficiency Standards (Title 24), the California Appliance Efficiency Regulations (Title 20), and the National Electrical Code (NEC). | Yes | Code | Does the installation comply with all current applicable regulations, code, and standards? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 90
1 | SWHC029 | 2 | Fan Controller for Air Conditioner, Residential | Any | Any | Any |  | EECP | 7 | A fan controller used for solely optimizing and improving heating efficiency including those for gas furnaces is not eligible. | Yes | Fan Controller | Is the fan controller used for solely optimizing and improving heating efficiency including those for gas furnaces? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Locate the fan controller for the associated gas furnace | Check to see whether the fan controller is installed on a fan in the ducting supplied by a gas fired furnace | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 115
1 | SWHC029 | 2 | Fan Controller for Air Conditioner, Residential | Any | Any | Any |  | EECP | 8 | The baseline air conditioning system cannot be equipped with a hardware based built-in delay controller. | Yes | Baseline AC | Is the baseline air conditioning system equipped with a hardware based built-in delay controller? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 97
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-24 | Kenny Liljestrom |  |  | 12
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-24 | Kenny Liljestrom |  |  | 5
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | Any | Any | Any |  | EECP | 3 | Eligibility requirements for this measure include: • The customer must have natural gas distributed to the installation address. • The new furnace must replace an existing gas furnace. | Yes |  | Customer has an active natural gas account? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Verify through internal systems or supplied documentation to verify the customer has an active gas account for one of the CA IOUs | Use EECP or other means to verify the customer has an active gas account supplied by SDG&E; or in the case of Statewide Programs, an account provided by SDG&E, SCG, or PG&E | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-24 | Kenny Liljestrom |  |  | 43
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | Any | Any | Any |  | EECP | 4 | Eligibility requirements for this measure include: • The customer must have natural gas distributed to the installation address. • The new furnace must replace an existing gas furnace. | Yes |  | Proposed furnace is replacing an existing gas furnace? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use an installation report or photographs from the existing conditions showing the gas furnace manufacturer and model | The existing furnace must be a gas fired furnace; this can be verified if the nameplate indicates the Input Rating of the furnace has the units of Btu/hr (Btuh) or there is a visible gas pipeline entering the furnace | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-24 | Kenny Liljestrom |  |  | 54
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | A | Any | Any |  | EECP | 5 | This measure must meet the minimum AFUE efficiency ratings in the Measure Case Description. | Yes |  | Annual Fuel Utilization Efficiency, AFUE (%) | Numeric Value | [8 empty] | Must be >= 92% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 92% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use the following link the verify the equipment is listed and the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 92% https://www.ahridirectory.org/ahridirectory/pages/home.aspx |  | 2021-11-24 | Kenny Liljestrom |  |  | 44
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | B | Any | Any |  | EECP | 6 | This measure must meet the minimum AFUE efficiency ratings in the Measure Case Description. | Yes |  | Annual Fuel Utilization Efficiency, AFUE (%) | Numeric Value | [8 empty] | Must be >= 95% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 95% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use the following link the verify the equipment is listed and the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 95% https://www.ahridirectory.org/ahridirectory/pages/home.aspx |  | 2021-11-24 | Kenny Liljestrom |  |  | 44
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | C | Any | Any |  | EECP | 7 | This measure must meet the minimum AFUE efficiency ratings in the Measure Case Description. | Yes |  | Annual Fuel Utilization Efficiency, AFUE (%) | Numeric Value | [8 empty] | Must be >= 97% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 97% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use the following link the verify the equipment is listed and the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 97% https://www.ahridirectory.org/ahridirectory/pages/home.aspx |  | 2021-11-24 | Kenny Liljestrom |  |  | 44
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | Any | Any | Any |  | EECP | 8 | A brushless DC motor, also known as an electronically commutated motor (ECM) may be eligible for the high-efficiency furnace with a variable speed motor (VSM). | Yes |  | Fan motor type | Drop Down List | Electronically Commutated Motor (ECM);Variable Speed Motor (VSM); | [8 empty] | QA Checklist | Use the make and model of the furnace to locate the product submittal or cutsheet; locate the type of fan used | The fan type listed on the product submittal/cutsheet needs to be either an Electronically Commutated Motor (ECM) or a Variable Speed Motor (VSM) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-24 | Kenny Liljestrom |  |  | 14
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | Any | Any | Any |  | EECP | 9 | A licensed contractor must verify the furnace has a built-in VSM, if applicable. | Yes |  | Contractor license number | Text Box | [9 empty] | QA Checklist | Verify the contractor used to install the furnace has a valid and active license in the state of CA | Use the following link to verify the contractor utilized is licensed by the ststae of CA; the contractor must have an active and valid license https://www.cslb.ca.gov/onlineservices/checklicenseII/checklicense.aspx | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-24 | Kenny Liljestrom |  |  | 25
0 | SWHC031 | 1 | High Efficiency Furnace, Residential | Any | Any | Any |  | QA Checklist | 10 | A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | Yes |  | A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | Text Box | [9 empty] | QA Checklist | The equipment must be listed on the AHRI directory | A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-24 | Kenny Liljestrom |  |  | 188
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | UpDeemed |  | EECP | 1 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | UpDeemed |  | EECP | 2 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | UpDeemed |  | EECP | 3 | E-5152 Data Collection Requirements | Yes | Measure Size Category | Measure Size Category | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | Any |  | EECP | 4 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-24 | Kenny Liljestrom |  |  | 12
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | Any |  | EECP | 5 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-24 | Kenny Liljestrom |  |  | 5
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | UpDeemed |  | EECP | 6 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | UpDeemed |  | EECP | 7 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [9 empty] | QA Checklist | The equipment must be listed on the AHRI directory | A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | UpDeemed |  | EECP | 8 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | UpDeemed |  | EECP | 9 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | UpDeemed |  | EECP | 10 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | Any |  | EECP | 11 | Eligibility requirements for this measure include: • The customer must have natural gas distributed to the installation address. • The new furnace must replace an existing gas furnace. | Yes | ActiveGas | Customer has an active natural gas account? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Verify through internal systems or supplied documentation to verify the customer has an active gas account for one of the CA IOUs | Use EECP or other means to verify the customer has an active gas account supplied by SDG&E; or in the case of Statewide Programs, an account provided by SDG&E, SCG, or PG&E | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-24 | Kenny Liljestrom |  |  | 43
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | Any |  | EECP | 12 | Eligibility requirements for this measure include: • The customer must have natural gas distributed to the installation address. • The new furnace must replace an existing gas furnace. | No | - | Proposed furnace is replacing an existing gas furnace? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use an installation report or photographs from the existing conditions showing the gas furnace manufacturer and model | The existing furnace must be a gas fired furnace; this can be verified if the nameplate indicates the Input Rating of the furnace has the units of Btu/hr (Btuh) or there is a visible gas pipeline entering the furnace | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property to be retired, no longer a measure package requirement | 2021-11-24 | Kenny Liljestrom |  |  | 54
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | Any |  | EECP | 13 | A brushless DC motor, also known as an electronically commutated motor (ECM) may be eligible for the high-efficiency furnace with a variable speed motor (VSM). | No | - | Fan motor type | Drop Down List | Electronically Commutated Motor (ECM);Variable Speed Motor (VSM); | [8 empty] | QA Checklist | Use the make and model of the furnace to locate the product submittal or cutsheet; locate the type of fan used | The fan type listed on the product submittal/cutsheet needs to be either an Electronically Commutated Motor (ECM) or a Variable Speed Motor (VSM) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property to be retired, no longer a measure package requirement | 2021-11-24 | Kenny Liljestrom |  |  | 14
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | Any |  | EECP | 13 | E-5152 Data Collection Requirements | Yes | Capacity (BTU/hr) | Input Capacity (BTU/hr) | Numeric Value | [9 empty] | Inspections | Photograph the nameplate showing theinput rating of the unit in BTU/HR | The Input Rating listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the Input Rating is listed | The Input Rating (BTU/HR) listed in EECP should match the Input Rating listed in the invoice or installation report |  | 2022-05-18 | Kenny Liljestrom |  |  | 23
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | A | Any | Any |  | EECP | 14 | This measure must meet the minimum AFUE efficiency ratings in the Measure Case Description. | Yes | AFUE | Annual Fuel Utilization Efficiency, AFUE (%) | Numeric Value | [8 empty] | Must be >= 92% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 92% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use the following link the verify the equipment is listed and the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 92% https://www.ahridirectory.org/ahridirectory/pages/home.aspx |  | 2021-11-24 | Kenny Liljestrom |  |  | 44
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | B | Any | Any |  | EECP | 15 | This measure must meet the minimum AFUE efficiency ratings in the Measure Case Description. | Yes | AFUE | Annual Fuel Utilization Efficiency, AFUE (%) | Numeric Value | [8 empty] | Must be >= 95% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 95% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use the following link the verify the equipment is listed and the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 95% https://www.ahridirectory.org/ahridirectory/pages/home.aspx |  | 2021-11-24 | Kenny Liljestrom |  |  | 44
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | C | Any | Any |  | EECP | 16 | This measure must meet the minimum AFUE efficiency ratings in the Measure Case Description. | Yes | AFUE | Annual Fuel Utilization Efficiency, AFUE (%) | Numeric Value | [8 empty] | Must be >= 97% | Inspections | Photograph the gas fired furnace nameplate to capture the efficiency (AFUE) of the unit; if no efficiency is listed, inform processing team | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 97% | QA Checklist | Use the make and model to verify the equipment AFUE rating (%) | Use the following link the verify the equipment is listed and the AFUE rating matches what is listed in EECP; the AFUE needs to be >= 97% https://www.ahridirectory.org/ahridirectory/pages/home.aspx |  | 2021-11-24 | Kenny Liljestrom |  |  | 44
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | Any |  | EECP | 17 | A licensed contractor must verify the furnace has a built-in VSM, if applicable. | No | - | Contractor license number | Text Box | [9 empty] | QA Checklist | Verify the contractor used to install the furnace has a valid and active license in the state of CA | Use the following link to verify the contractor utilized is licensed by the state of CA; the contractor must have an active and valid license https://www.cslb.ca.gov/onlineservices/checklicenseII/checklicense.aspx | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property to be retired, no longer a measure package requirement | 2022-05-16 | Kenny Liljestrom | Property removed as part of mid-year update to address eligiblity clarifications |  | 25
1 | SWHC031 | 2 | High Efficiency Furnace, Residential | Any | Any | Any |  | QA Checklist | 18 | A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | No | - | A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | Text Box | [9 empty] | QA Checklist | The equipment must be listed on the AHRI directory | A list of eligible furnaces can be found at https://www.ahridirectory.org/ahridirectory/pages/home.aspx (search for qualifying products that meet or exceed the measure case specification). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-05-16 | Kenny Liljestrom | Removed, added criteria to RefNum instead of standalone property |  | 188
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 3 | The HVAC system must be functional/operable and drawing power. | Yes | Operational | Is the HVAC system functional/operable and drawing power? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Ask the customer if they are able to start the AC unit and observe the equipment (outdoor condenser and indoor vents) | Check the HVAC system to see if it is energized and functional (operating without issues) | QA Checklist | A detailed report from the implementer showing the baseline operating performance (tested data before and after) | The existing conditions should show before data values indicating the fan was working |  | 2021-06-21 | Kenny Liljestrom |  | Add | 57
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 4 | The HVAC system shall be capable of delivering a supply air flow rate of at least 350 cfm/ton. The minimum 350 cfm/ton airflow requirement ensures that the refrigerant system can be properly diagnosed and charged as part of a maintenance service. If the system is not delivering 350 cfm/ton upon initial inspection, an assessment should be made to determine if the system will be able to deliver 350 cfm/ton by implementing repairs related to airflow. If it is determined that the supply fan and duct system in place do not have the capability to deliver at least 350 cfm/ton with or without airflow repairs, the savings in this measure are invalid. | Yes | Air Flow Rate | Minimum HVAC delivery air flow rate (cfm/ton) | Numeric Value | [8 empty] | Must be >= 350 | QA Checklist | A detailed report from the implementer showing the baseline and measure case operating performance | the airflow rate should be >= 350 cfm/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 5 | The replacement brushless fan motor (BFM) motor capacity and rated voltage shall match that of existing fan motor being replaced. | Yes | New Match Existing | Does the replacement BFM motor capacity and rated voltage match that of the existing fan motor being replaced? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | A detailed report from the implementer showing the baseline and measure case operating performance should show existing conditions | The replacement brushless fan motor (BFM) motor capacity and rated voltage shall match that of existing fan motor being replaced. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 110
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 6 | The replacement BFM motor and motor controls assembly shall be “UL Listed.” | Yes | UL Listed | Is the replacement brushless fan motor (BFM) motor and motor controls assembly “UL Listed.”? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Photograph of the motor nameplate and motor casing to look for the 'UL' sticker | A UL sticker or logo should be present on the motor or casing indicating it is a qualified UL listed motor | QA Checklist | Check the motor manufacturer and model number against the UL database of motors or have the implementer provide a screenshot of the manufacturer and model number on the UL database | The motor must be listed as being UL qualified | This property may require SDG&E to be part of a QPL membership | 2021-06-21 | Kenny Liljestrom |  | Add | 93
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 7 | The replacement BFM motor shall have a warranty of at least two years from date of installation. | Yes | Warranty | Does the replacement BFM motor have a warranty of at least two years from date of installation? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Standard warranty documentation should be submitted or included in the package upload | warranty coverage, if not included from the manufacturer, needs to be supplied by the installer | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 95
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 8 | The measure shall include HVAC system start-up. During the start-up, the installer shall ensure that system maintain programmed level airflows under both cooling and/or heating and that these are adequate. | Yes | HVAC Start Up | During start-up, system maintains programmed level airflows under both cooling and/or heating? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Update the property label | 2021-06-21 | Kenny Liljestrom |  | Add | 94
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 9 | The installation (as applicable) shall comply with all applicable regulations including but not limited to California Building Energy Efficiency Standards (Title-24), California Electrical Code, and NEC, and any applicable local jurisdiction regulations. See Code Requirement | Yes | Regulations | Does the installation comply with all applicable regulations? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 61
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 10 | This measure only supports HVAC (evaporator) fan motors with nominal capacities of ½-hp and/or less typically serving HVAC systems with nominal capacities of 3.5 ton (or less). | Yes | HVAC EVAP Fan | Is the measure an HVAC (evaporator) fan motor with nominal capacity of ½-hp (or less) typically serving HVAC systems with nominal capacities of 3.5 ton (or less)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Photograph the HVAC system nameplate and the evaporator fan (indoor fan near the cooling coils, if accessible) | HVAC system should have a capacity of less than or equal to 3.5 tons; fan motor should be less than 1/2hp | QA Checklist | Inspection report should indicate the size of the HVAC system and the manufacturer and model number can be used to identify the fan motor size | HVAC system should have a capacity of less than or equal to 3.5 tons; fan motor should be less than 1/2hp |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWHC038 | 1 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 11 | The measure applies to units with shaded pole (SHP) or permanent split capacitor (PSC) motors currently installed. As stated previously, the replacement motor is to be a brushless direct current motor with selectable speed control designed to replace a PSC motor in a residential direct drive fan application. | Yes | Replacement | Is the measure replacing a shaded pole or permanent split capacitor (PSC) motor with a brushless direct current motor with selectable speed control? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | An installation report can list the existing equipment and specifications | the existing equipment make and model can be searched online to show if it is a shaded pole or permanent split capacitor motor | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 148
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-23 | Kenny Liljestrom |  |  | 12
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-23 | Kenny Liljestrom |  |  | 5
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 3 | The HVAC system must be functional/operable and drawing power. | Yes | Operational | Is the HVAC system functional/operable and drawing power? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Ask the customer if they are able to start the AC unit and observe the equipment (outdoor condenser and indoor vents) | Check the HVAC system to see if it is energized and functional (operating without issues) | QA Checklist | A detailed report from the implementer showing the baseline operating performance (tested data before and after) | The existing conditions should show before data values indicating the fan was working |  | 2021-11-23 | Kenny Liljestrom |  |  | 57
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 4 | The HVAC system shall be capable of delivering a supply air flow rate of at least 350 cfm/ton. The minimum 350 cfm/ton airflow requirement ensures that the refrigerant system can be properly diagnosed and charged as part of a maintenance service. If the system is not delivering 350 cfm/ton upon initial inspection, an assessment should be made to determine if the system will be able to deliver 350 cfm/ton by implementing repairs related to airflow. If it is determined that the supply fan and duct system in place do not have the capability to deliver at least 350 cfm/ton with or without airflow repairs, the savings in this measure are invalid. | Yes | Air Flow Rate | Minimum HVAC delivery air flow rate (cfm/ton) | Numeric Value | [8 empty] | Must be >= 350 | QA Checklist | A detailed report from the implementer showing the baseline and measure case operating performance | the airflow rate should be >= 350 cfm/ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 45
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 5 | The replacement brushless fan motor (BFM) motor capacity and rated voltage shall match that of existing fan motor being replaced. | Yes | New Match Existing | Does the replacement BFM motor capacity and rated voltage match that of the existing fan motor being replaced? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | A detailed report from the implementer showing the baseline and measure case operating performance should show existing conditions | The replacement brushless fan motor (BFM) motor capacity and rated voltage shall match that of existing fan motor being replaced. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 110
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 6 | The replacement BFM motor and motor controls assembly shall be “UL Listed.” | Yes | UL Listed | Is the replacement brushless fan motor (BFM) motor and motor controls assembly “UL Listed.”? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Photograph of the motor nameplate and motor casing to look for the 'UL' sticker | A UL sticker or logo should be present on the motor or casing indicating it is a qualified UL listed motor | QA Checklist | Check the motor manufacturer and model number against the UL database of motors or have the implementer provide a screenshot of the manufacturer and model number on the UL database | The motor must be listed as being UL qualified | This property may require SDG&E to be part of a QPL membership | 2021-11-23 | Kenny Liljestrom |  |  | 93
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 7 | The replacement BFM motor shall have a warranty of at least two years from date of installation. | Yes | Warranty | Does the replacement BFM motor have a warranty of at least two years from date of installation? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Standard warranty documentation should be submitted or included in the package upload | warranty coverage, if not included from the manufacturer, needs to be supplied by the installer | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 95
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 8 | The measure shall include HVAC system start-up. During the start-up, the installer shall ensure that system maintain programmed level airflows under both cooling and/or heating and that these are adequate. | Yes | HVAC Start Up | During start-up, system maintains programmed level airflows under both cooling and/or heating? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Update the property label | 2021-11-23 | Kenny Liljestrom |  |  | 94
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 9 | The installation (as applicable) shall comply with all applicable regulations including but not limited to California Building Energy Efficiency Standards (Title-24), California Electrical Code, and NEC, and any applicable local jurisdiction regulations. See Code Requirement | Yes | Regulations | Does the installation comply with all applicable regulations? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 61
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 10 | This measure only supports HVAC (evaporator) fan motors with nominal capacities of ½-hp and/or less typically serving HVAC systems with nominal capacities of 3.5 ton (or less). | Yes | HVAC EVAP Fan | Is the measure an HVAC (evaporator) fan motor with nominal capacity of ½-hp (or less) typically serving HVAC systems with nominal capacities of 3.5 ton (or less)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Photograph the HVAC system nameplate and the evaporator fan (indoor fan near the cooling coils, if accessible) | HVAC system should have a capacity of less than or equal to 3.5 tons; fan motor should be less than 1/2hp | QA Checklist | Inspection report should indicate the size of the HVAC system and the manufacturer and model number can be used to identify the fan motor size | HVAC system should have a capacity of less than or equal to 3.5 tons; fan motor should be less than 1/2hp |  | 2021-11-23 | Kenny Liljestrom |  |  | 162
1 | SWHC038 | 2 | Brushless Fan Motor Replacement, Residential | Any | Any | Any |  | EECP | 11 | The measure applies to units with shaded pole (SHP) or permanent split capacitor (PSC) motors currently installed. As stated previously, the replacement motor is to be a brushless direct current motor with selectable speed control designed to replace a PSC motor in a residential direct drive fan application. | Yes | Replacement | Is the measure replacing a shaded pole or permanent split capacitor (PSC) motor with a brushless direct current motor with selectable speed control? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | An installation report can list the existing equipment and specifications | the existing equipment make and model can be searched online to show if it is a shaded pole or permanent split capacitor motor | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 148
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph of thermostat, if manufacturer number is visible document or photograph | Manufacturer on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph of thermostat, if model number is visible document or photograph | Model number on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any |  | EECP | 3 | The customer must use the thermostat to control heating and/or cooling equipment supplied by fuels provided by the program administrator: • For single-fuel utilities (or dual-fuel utilities in a portion of their service area where they only supply one fuel), only savings for the applicable delivered fuel may be claimed • Eligible heating equipment: gas forced-air furnace, electric forced-air furnace, heat pump • Eligible cooling equipment: central air conditioning | Yes | Eligible Home | Was the measure installed in an eligible home and attached to the type of HVAC equipment that is being incentivized? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Photograph of the heating system nameplate to capture the Manufacturer and Model Number, or look for any electric or gas lines going to the equipment | Measures for gas furnaces (natural gas heated equipment) include 465983 and 467953 Measures for Heat Pump (electric heated equipment) include 467954 and 467955 | QA Checklist | An installation report can show what type of HVAC equipment the smart thermostat was installed on; Eligible heating equipment: gas forced-air furnace, electric forced-air furnace, heat pump; Eligible cooling equipment: central air conditioning | The measure must be installed in an eligible home and attached to the type of HVAC equipment that is being incentivized |  | 2021-06-21 | Kenny Liljestrom |  | Add | 116
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any |  | EECP | 4 | Unknown | Yes | Purchase Date | Purchase date of newly installed thermostat | Date | [9 empty] | QA Checklist | Cross check EECP data against submitted invoice | The purchase date on the receipt or invoice should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any |  | EECP | 5 | Unknown | Yes | Receipt | Was a copy of the purchase receipt submitted? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Check EECP to see if a copy of the invoice or sales receipt was uploaded in the enrollment | Ensure Invoice was submitted and uploaded to EECP | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any |  | EECP | 6 | The smart thermostat must be in full compliance with the ENERGYSTAR® Program Requirements and Product Specification for Connected Thermostats products Version 1.0 or later. R950 | Yes | Energy Star | Is the installed smart thermostat in full compliance with the ENERGYSTAR Program Requirements and Product Specification for Connected Thermostats Products Version 1.0 or later? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Using the make and model, cross reference the EnergyStar database to ensure the model is listed | The listed make and model in EECP should be included in the EnergyStar database | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 176
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any |  | QA Checklist | 7 | The program administrator (PA) shall employ QA/QC procedures to ensure that the thermostat is installed in an eligible home and is attached to the type of HVAC equipment that is being incentivized, whether it is for natural gas or electricity savings. | Yes |  | The program administrator (PA) shall employ QA/QC procedures to ensure that the thermostat is installed in an eligible home and is attached to the type of HVAC equipment that is being incentivized, whether it is for natural gas or electricity savings. | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Check the home to ensure it is eligible to receive a rebate and ensure the measure is being applied to the correct piece of heating equipment (Gas Furnace or Heat Pump) | The home should not be flagged in EECP as a double dipper for smart thermostats and meet all program eligibility requirements and the HVAC type should match with the measure description | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-07-20 | Kenny Liljestrom |  | Add | 251
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any |  | QA Checklist | 8 | The PA shall confirm that the customer has a newly purchased smart thermostat. At minimum, the PA shall obtain a copy of the thermostat sales receipt and the PA shall confirm the purchase date is on or after the program start date. | Yes |  | PA shall confirm that the customer has a newly purchased smart thermostat. At minimum, the PA shall obtain a copy of the thermostat sales receipt and the PA shall confirm the purchase date is on or after the program start date. | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Implementer should provide a copy of the sales receipt in the submittal package | The receipt should list the purchase date and that purchase date should not be prior to the program start-up date | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 227
0 | SWHC039 | 3 | Smart Thermostat, Residential | Any | Any | Any |  | QA Checklist | 9 | The PA shall determine customer eligibility prior to rebate payment. Upon request, all data associated with determining eligibility shall be provided to Energy Division of the California Public Utilities Commission (CPUC). All PAs shall extend this requirement to all third-party vendors that assist PAs with determining customer eligibility. To the extent that they are used to determine eligibility, data regarding dates of purchase, location of home, customer HVAC equipment type, pre-installation HVAC energy use, etc. shall be made available. | Yes |  | The PA shall determine customer eligibility prior to rebate payment. Upon request, all data associated with determining eligibility shall be provided to Energy Division of the California Public Utilities Commission (CPUC). All PAs shall extend this requirement to all third-party vendors that assist PAs with determining customer eligibility. To the extent that they are used to determine eligibility, data regarding dates of purchase, location of home, customer HVAC equipment type, pre-installation HVAC energy use, etc. shall be made available. | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Verify customer eligibility | The PA shall determine customer eligibility prior to rebate payment. Upon request, all data associated with determining eligibility shall be provided to Energy Division of the California Public Utilities Commission (CPUC). All PAs shall extend this requirement to all third-party vendors that assist PAs with determining customer eligibility. To the extent that they are used to determine eligibility, data regarding dates of purchase, location of home, customer HVAC equipment type, pre-installation HVAC energy use, etc. shall be made available. | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 547
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | UpDeemed |  | EECP | 0 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 7
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | UpDeemed |  | EECP | 5 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 12
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | Any |  | EECP | 10 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer in EECP should match what is listed in the invoice or installation report |  | 2022-06-10 | Kenny Liljestrom |  |  | 12
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | Any |  | EECP | 15 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number in EECP should match what is listed in the invoice or installation report |  | 2022-06-10 | Kenny Liljestrom |  |  | 5
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | UpDeemed |  | EECP | 20 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number in EECP should match what is listed in the invoice or installation report |  | 2022-06-10 | Kenny Liljestrom |  |  | 13
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | Any |  | EECP | 30 | The smart thermostat must be in full compliance with the ENERGYSTAR® Program Requirements and Product Specification for Connected Thermostats products Version 1.0 or later. | Yes | Energy Star ID | Energy Star unique ID | Text Box | [9 empty] | QA Checklist | Review the EnergyStar database to check for the make and model of the installed equipment | The equipment in EECP should be locatable on the EnergyStar database as being a certified product and should match the make and model of the equipment | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Can we have this qualify via Energy Star within CPSS and not entered yes/no by the 3P? | 2022-06-10 |  |  |  | 21
1 | SWHC039 | 4 | Smart Thermostat, Residential | C | Any | Any |  | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Building type. For upstream or midstream measures where building type is not available, the “Res” building type shall be assumed. Climate zone Existing HVAC system type In any event, data collection shall fully comply with both general and device eligibility requirements. | Yes | Existing Equipment Type | Existing air conditioning equipment type | Drop Down List | AC;HP; |  | Equal | AC |  |  |  |  | Must be AC | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 40
1 | SWHC039 | 4 | Smart Thermostat, Residential | D | Any | Any |  | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Building type. For upstream or midstream measures where building type is not available, the “Res” building type shall be assumed. Climate zone Existing HVAC system type In any event, data collection shall fully comply with both general and device eligibility requirements. | Yes | Existing Equipment Type | Existing air conditioning equipment type | Drop Down List | AC;HP; |  | Equal | HP |  |  |  |  | Must be HP | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 40
1 | SWHC039 | 4 | Smart Thermostat, Residential | E | Any | Any |  | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Building type. For upstream or midstream measures where building type is not available, the “Res” building type shall be assumed. Climate zone Existing HVAC system type In any event, data collection shall fully comply with both general and device eligibility requirements. | Yes | Existing Equipment Type | Existing air conditioning equipment type | Drop Down List | AC;HP; |  | Equal | AC |  |  |  |  | Must be AC | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 40
1 | SWHC039 | 4 | Smart Thermostat, Residential | F | Any | Any |  | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Building type. For upstream or midstream measures where building type is not available, the “Res” building type shall be assumed. Climate zone Existing HVAC system type In any event, data collection shall fully comply with both general and device eligibility requirements. | Yes | Existing Equipment Type | Existing air conditioning equipment type | Drop Down List | AC;HP; |  | Equal | HP |  |  |  |  | Must be HP | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 40
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | DnDeemDI |  | EECP | 40 | Per Impact Evaluation of Smart Thermostats. Residential Sector - Program Year 2019 guidance, direct install projects already equipped with smart thermostat technology and/or included the installation of smart thermostat technology shall not be bundled with (or include the installation of) fan control technology to avoid potential double counting of energy savings attributions from both technologies. R1587 (Table 6-1) Program exclusions are expected to be re-evaluated since future impact evaluations will include savings attributions from bundled measures. | Yes | Fan Delay | Does the customer already have a smart thermostat or fan delay controller installed? | Drop Down List | Yes;No; |  | Equal | No |  |  |  |  | Must be No | QA Checklist | Use the EECP double dip report to check for previously installed smart thermostat and fan delay controller measures; also check in the installation report to determine if the report mentions a fan delay controller | There must not be an existing smart thermostat at the property; there must not be a fan delay controller already installed or bundled with this measure. | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-06-10 | Kenny Liljestrom |  |  | 85
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | UpDeemed |  | EECP | 190 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value |  |  |  |  | General |  |  | 0 |  | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 8
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | UpDeemed |  | EECP | 195 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 15
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | Any |  | QA Checklist | 205 | The program administrator (PA) shall employ QA/QC procedures to ensure that the thermostat is installed in an eligible home and is attached to the type of HVAC equipment that is being incentivized, whether it is for natural gas or electricity savings. | Yes | - | The program administrator (PA) shall employ QA/QC procedures to ensure that the thermostat is installed in an eligible home and is attached to the type of HVAC equipment that is being incentivized, whether it is for natural gas or electricity savings. | None | [9 empty] | QA Checklist | Check the home to ensure it is eligible to receive a rebate and ensure the measure is being applied to the correct piece of heating equipment (Gas Furnace or Heat Pump) | The home should not be flagged in EECP as a double dipper for smart thermostats and meet all program eligibility requirements and the HVAC type should match with the measure description | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 251
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | Any |  | QA Checklist | 210 | The PA shall confirm that the customer has a newly purchased smart thermostat. At minimum, the PA shall obtain a copy of the thermostat sales receipt and the PA shall confirm the purchase date is on or after the program start date | Yes | - | The PA shall confirm that the customer has a newly purchased smart thermostat. At minimum, the PA shall obtain a copy of the thermostat sales receipt and the PA shall confirm the purchase date is on or after the program start date. | None | [9 empty] | QA Checklist | Check the enrollment uploads to determine if the sales receipt lists the Smart Thermostat | Confirm the invoice or sales receipt for the thermostats is included with the enrollments and has a line item for Smart Thermostats | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 231
1 | SWHC039 | 4 | Smart Thermostat, Residential | Any | Any | Any |  | QA Checklist | 215 | The PA shall determine customer eligibility prior to rebate payment. Upon request, all data associated with determining eligibility shall be provided to Energy Division of the California Public Utilities Commission (CPUC). All PAs shall extend this requirement to all third-party vendors that assist PAs with determining customer eligibility. To the extent that they are used to determine eligibility, data regarding dates of purchase, location of home, customer HVAC equipment type, pre-installation HVAC energy use, etc. shall be made available. | Yes | - | The PA shall determine customer eligibility prior to rebate payment. Upon request, all data associated with determining eligibility shall be provided to Energy Division of the California Public Utilities Commission (CPUC). All PAs shall extend this requirement to all third-party vendors that assist PAs with determining customer eligibility. To the extent that they are used to determine eligibility, data regarding dates of purchase, location of home, customer HVAC equipment type, pre-installation HVAC energy use, etc. shall be made available. | None | [9 empty] | QA Checklist | Verify customer eligibility | The PA shall determine customer eligibility prior to rebate payment. Upon request, all data associated with determining eligibility shall be provided to Energy Division of the California Public Utilities Commission (CPUC). All PAs shall extend this requirement to all third-party vendors that assist PAs with determining customer eligibility. To the extent that they are used to determine eligibility, data regarding dates of purchase, location of home, customer HVAC equipment type, pre-installation HVAC energy use, etc. shall be made available. | - | - | - |  | 2022-06-10 | Kenny Liljestrom |  |  | 547
0 | SWHC041 | 1 | Software-Controlled Switch Reluctance Motor | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-05-28 | Kenny Liljestrom |  | Add | 12
0 | SWHC041 | 1 | Software-Controlled Switch Reluctance Motor | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-05-28 | Kenny Liljestrom |  | Add | 5
0 | SWHC041 | 1 | Software-Controlled Switch Reluctance Motor | Any | Any | Any |  | EECP | 3 | This measure is not eligible for supply fan motors rated < 1 hp and > 3 hp (nominal). This measure is not eligible for other fans, such as the return fan or outdoor air fan of a packaged HVAC unit. | Yes | Supply Fan Replacement | Was the motor installed to replace a supply fan (not a return fan or outdoor air fan) of a packaged HVAC unit? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-05-28 | Kenny Liljestrom |  | Add | 110
0 | SWHC041 | 1 | Software-Controlled Switch Reluctance Motor | Any | Any | Any |  | EECP | 4 | This measure must replace the existing 1 to 3 hp supply fan motor in a packaged HVAC system. | Yes | Existing Fan Power | Existing packaged HVAC supply fan motor power (hp) | Numeric Value | [8 empty] | Must be >=1 and <=3 | QA Checklist | An installation report should capture the existing conditions and the power (hp) of the existing supply fan motor | The existing motor must be >= 1 and <= 3 hp | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-05-28 | Kenny Liljestrom |  | Add | 50
0 | SWHC041 | 1 | Software-Controlled Switch Reluctance Motor | Any | Any | Any |  | EECP | 5 | The new motor and controls must be UL Listed. | Yes | UL Listed Motor | Are the new motor and controls UL Listed? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Photograph of the motor nameplate and motor casing to look for the 'UL' sticker | A UL sticker or logo should be present on the motor or casing indicating it is a qualified UL listed motor | QA Checklist | Check the motor manufacturer and model number against the UL database of motors or have the implementer provide a screenshot of the manufacturer and model number on the UL database | The motor must be listed as being UL qualified |  | 2021-05-28 | Kenny Liljestrom |  | Add | 41
0 | SWHC041 | 1 | Software-Controlled Switch Reluctance Motor | Any | Any | Any |  | EECP | 6 | The installation of this measure shall meet all applicable regulations, including but not limited to the current California Building Energy Efficiency Standards (Title 24), federal code, and the National Electrical Code® (NEC). | Yes | Codes and Regulations | Does the installation comply with all applicable regulations, including but not limited to the current California Building Energy Efficiency Standards (Title 24), federal code, and the National Electrical Code® (NEC)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | - | - | - | - | - | - |  | 2021-05-28 | Kenny Liljestrom | Removed, implementer must file for permit for measure, not useful to capture unless permit is collected at enrollment | Add | 217
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | UpDeemed |  | EECP | 1 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | UpDeemed |  | EECP | 2 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | Any |  | EECP | 3 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-11 | Kenny Liljestrom |  |  | 12
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | Any |  | EECP | 4 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-11 | Kenny Liljestrom |  |  | 5
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | UpDeemed |  | EECP | 5 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | UpDeemed |  | EECP | 6 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | UpDeemed |  | EECP | 7 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | UpDeemed |  | EECP | 8 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | Any |  | EECP | 9 | This measure is not eligible for supply fan motors rated < 1 hp and > 3 hp (nominal). This measure is not eligible for other fans, such as the return fan or outdoor air fan of a packaged HVAC unit. | Yes | Supply Fan Replacement | Was the motor installed to replace a supply fan (not a return fan or outdoor air fan) of a packaged HVAC unit? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-11-11 | Kenny Liljestrom |  |  | 110
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | Any |  | EECP | 10 | This measure must replace the existing 1 to 3 hp supply fan motor in a packaged HVAC system. | Yes | Existing Fan Power | Existing packaged HVAC supply fan motor power (hp) | Numeric Value | [8 empty] | Must be >=1 and <=3 | QA Checklist | An installation report should capture the existing conditions and the power (hp) of the existing supply fan motor | The existing motor must be >= 1 and <= 3 hp | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-11-11 | Kenny Liljestrom |  |  | 50
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | Any |  | EECP | 11 | The new motor and controls must be UL Listed. | Yes | UL Listed Motor | Are the new motor and controls UL Listed? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Photograph of the motor nameplate and motor casing to look for the 'UL' sticker | A UL sticker or logo should be present on the motor or casing indicating it is a qualified UL listed motor | QA Checklist | Check the motor manufacturer and model number against the UL database of motors or have the implementer provide a screenshot of the manufacturer and model number on the UL database | The motor must be listed as being UL qualified |  | 2021-11-11 | Kenny Liljestrom |  |  | 41
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | Any |  | - | 12 | The installation of this measure shall meet all applicable regulations, including but not limited to the current California Building Energy Efficiency Standards (Title 24), federal code, and the National Electrical Code® (NEC). | No | Codes and Regulations | Does the installation comply with all applicable regulations, including but not limited to the current California Building Energy Efficiency Standards (Title 24), federal code, and the National Electrical Code® (NEC)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | - | - | - | - | - | - |  | 2021-11-11 | Kenny Liljestrom | Program ops request to remove property since contractors are held liable in their contracts to install equipment in accordance with all safety and energy codes |  | 217
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | Any |  | EECP | 13 | In support of the next revision to this workpaper, additional data should to be gathered to determine if motors with horsepower ratings greater than 3 HP can be included as measure offerings. This includes the following: • The application for software-controlled SRMs highlighted by the 2018 ET study is in air conditioning supply fans. Other applications may be studied for suitability. • Based on the initially available set of datasheets, the 5 HP SRM falls below the NEMA Premium® rating of 89.5% for a 4-pole (1800 RPM) induction motor. As additional SRM products become available, efficiency rating tests (following the appropriate standard test procedures identified by the manufacturer) as well as data on full-load VSD losses for the comparable baseline equipment should be collected. | Yes | SoftwareSRM | Software used to control SRM | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | New property | 2021-11-11 | Kenny Liljestrom |  |  | 28
1 | SWHC041 | 2 | Software-Controlled Switch Reluctance Motor | Any | Any | Any |  | EECP | 14 | In support of the next revision to this workpaper, additional data should to be gathered to determine if motors with horsepower ratings greater than 3 HP can be included as measure offerings. This includes the following: • The application for software-controlled SRMs highlighted by the 2018 ET study is in air conditioning supply fans. Other applications may be studied for suitability. • Based on the initially available set of datasheets, the 5 HP SRM falls below the NEMA Premium® rating of 89.5% for a 4-pole (1800 RPM) induction motor. As additional SRM products become available, efficiency rating tests (following the appropriate standard test procedures identified by the manufacturer) as well as data on full-load VSD losses for the comparable baseline equipment should be collected. | Yes | Total hp | Total hp that can benefit from this measure above the max power rating offered by the measure (>3hp) | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | New property | 2021-11-11 | Kenny Liljestrom |  |  | 100
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 12
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 5
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any |  | EECP | 3 | This measure is applicable for the nonresidential buildings served by unitary direct expansion (DX) systems listed below. This measure applies to existing building vintages. Assembly Asm Community College ECC University EUn Grocery Gro Hospital Hsp Nursing Home Nrs Hotel Htl Bio/Tech Manufacturing MBT Light Industrial Manufacturing MLI Large Office OfL Small Office OfS Sit-Down Restaurant RSD Fast-Food Restaurant RFF Department Store Rt3 Big Box Retail RtL Small Retail RtS Conditioned Storage SCn Refrigerated Warehouse WRf | Yes |  | Building type | Drop Down List | Assembly (Asm);Community College (ECC);University (EUn);Grocery (Gro);Hospital (Hsp);Nursing Home (Nrs);Hotel (Htl);Bio/Tech Manufacturing (MBT);Light Industrial Manufacturing (MLI);Large Office (OfL);Small Office (OfS);Sit-Down Restaurant (RSD);Fast-Food Restaurant (RFF);Department Store (Rt3);Big Box Retail (RtL);Small Retail (RtS);Conditioned Storage (SCn);Refrigerated Warehouse (WRf); | [8 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use an installation report to determine the building type | The building type should match what is listed in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 13
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any |  | EECP | 4 | This measure is applicable only in Climate Zones 12, 13, and 15. | Yes |  | Climate Zone | Drop Down List | CZ12;CZ13;CZ15; | [8 empty] | QA Checklist | Use an installation report or invoice to determine the zip code or climate zone where the equipment was purchased or installed | The installation address must reside in CZ12, CZ13, or CZ15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Property can be configured at the enrollment level if the zip code is being captured and converted to CA CZ | 2021-12-29 | Kenny Liljestrom |  |  | 12
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any |  | EECP | 5 | The HVAC packaged units and the evaporative pre-cooler system and controls must meet the following requirements: • Host packaged unit must have a cooling capacity at least 20 tons • For the Add-on Equipment (AOE) measure, the existing packaged unit on which the evaporative pre-cooler system will be installed must be less than 10 years old • A water treatment system must be used in conjunction with the evaporative pre-cooler system to maintain water quality and performance • Real time monitoring of the evaporative pre-cooler system must be implemented to ensure the system is working properly • As a standard procedure, the contractor must perform condenser coil cleaning prior to installation of the pre-cooler system. | Yes |  | Cooling Capacity (tons) | Numeric Value | [8 empty] | Must be >= 20 | Inspections | Photograph the nameplate of the HVAC unit to capture the make, model, and cooling capacity (tons or Btu/hr) | The cooling capacity must be greater than 240,000 Btu/hr or 20 tons | QA Checklist | Using the make and model of the existing HVAC equipment, or the cooling capacity in tons or Btu/hr, to determine the cooling capacity of the HVAC system | The cooling capacity must be greater than 240,000 Btu/hr or 20 tons | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 23
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any |  | EECP | 6 | The HVAC packaged units and the evaporative pre-cooler system and controls must meet the following requirements: • Host packaged unit must have a cooling capacity at least 20 tons • For the Add-on Equipment (AOE) measure, the existing packaged unit on which the evaporative pre-cooler system will be installed must be less than 10 years old • A water treatment system must be used in conjunction with the evaporative pre-cooler system to maintain water quality and performance • Real time monitoring of the evaporative pre-cooler system must be implemented to ensure the system is working properly • As a standard procedure, the contractor must perform condenser coil cleaning prior to installation of the pre-cooler system. | Yes |  | Existing equipment manufacture date | Date | [8 empty] | Date must be <= 10 Years from Today | QA Checklist | Using the serial number of the HVAC equipment, determine the date the system was manufactured (or a photo of the equipment nameplate showing the manufacture date) | The equipment must be less than 10 years old to qualify | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 35
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any |  | EECP | 7 | The HVAC packaged units and the evaporative pre-cooler system and controls must meet the following requirements: • Host packaged unit must have a cooling capacity at least 20 tons • For the Add-on Equipment (AOE) measure, the existing packaged unit on which the evaporative pre-cooler system will be installed must be less than 10 years old • A water treatment system must be used in conjunction with the evaporative pre-cooler system to maintain water quality and performance • Real time monitoring of the evaporative pre-cooler system must be implemented to ensure the system is working properly • As a standard procedure, the contractor must perform condenser coil cleaning prior to installation of the pre-cooler system. | Yes |  | Is a water treatment system used with the evaporative pre-cooler system? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use an installation report or invoice to determine if a water treatment system was installed or in use with the evaporative pre-cooler | A water treatment system must be used to treat the water before entering the evaporative pre-cooler | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 72
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any |  | EECP | 8 | The HVAC packaged units and the evaporative pre-cooler system and controls must meet the following requirements: • Host packaged unit must have a cooling capacity at least 20 tons • For the Add-on Equipment (AOE) measure, the existing packaged unit on which the evaporative pre-cooler system will be installed must be less than 10 years old • A water treatment system must be used in conjunction with the evaporative pre-cooler system to maintain water quality and performance • Real time monitoring of the evaporative pre-cooler system must be implemented to ensure the system is working properly • As a standard procedure, the contractor must perform condenser coil cleaning prior to installation of the pre-cooler system. | Yes |  | Has real time monitoring been implemented to ensure proper operation of the system? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use an installation report or invoice to determine if a real time monitoring system was installed or used with the evaporative pre-cooler | A real time monitoring system must have been installed or in use with the evaporative pre-cooler | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 83
0 | SWHC042 | 2 | Evaporative Pre-Cooler System and Controls for Packaged HVAC Unit, Commercial | Any | Any | Any |  | EECP | 9 | The HVAC packaged units and the evaporative pre-cooler system and controls must meet the following requirements: • Host packaged unit must have a cooling capacity at least 20 tons • For the Add-on Equipment (AOE) measure, the existing packaged unit on which the evaporative pre-cooler system will be installed must be less than 10 years old • A water treatment system must be used in conjunction with the evaporative pre-cooler system to maintain water quality and performance • Real time monitoring of the evaporative pre-cooler system must be implemented to ensure the system is working properly • As a standard procedure, the contractor must perform condenser coil cleaning prior to installation of the pre-cooler system. | Yes |  | Has the contractor performed condenser coil cleaning prior to installation of the pre-cooler system? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Newly adopted measure package in rev 2 | 2021-12-29 | Kenny Liljestrom |  |  | 100
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | Any |  | EECP | 1 | 1 Asm Assembly 2 Com Commercial 3 ECC Education - Community College 4 EPr Education - Primary School 5 ERC Education - Relocatable Classroom 6 ESe Education - Secondary School 7 EUn Education - University 8 Gro Grocery 9 Hsp Health/Medical - Hospital 10 Htl Lodging - Hotel 11 MBT Manufacturing Biotech 12 MLI Manufacturing Light Industrial 13 Mtl Lodging - Motel 14 Nrs Health/Medical - Nursing Home 15 OfL Office - Large 16 OfS Office - Small 17 RFF Restaurant - Fast-Food 18 RSD Restaurant - Sit-Down 19 Rt3 Retail - Multistory Large 20 RtL Retail - Single-Story Large 21 RtS Retail - Small 22 SCn Storage - Conditioned 23 WRf Refrigerated Warehouse | Yes | - | Building Type | Drop Down List | Asm;Com;ECC;EPr;ERC;EUn;Gro;Hsp;Htl;MBT;MLI;Mtl;Nrs;OfL;OfS;RFF;RSD;Rt3;RtL;RtS;SCn;WRf; | [8 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report to determine the building type of the customer | The building type should match what is listed in EECP | Property can be configured at the enrollment level | 2022-02-09 | Kenny Liljestrom |  |  | 13
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed |  | EECP | 2 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed |  | EECP | 3 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed |  | EECP | 4 | E-5152 Data Collection Requirements | Yes | Measure Size Category | Measure Size Category | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | Any |  | EECP | 5 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The manufacturer listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2022-02-09 | Kenny Liljestrom |  |  | 12
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | Any |  | EECP | 6 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The model number listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the model number | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2022-02-09 | Kenny Liljestrom |  |  | 5
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed |  | EECP | 7 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 13
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed |  | EECP | 8 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 21
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed |  | EECP | 9 | Required for UpDeemed Programs | No | Refrigerant Type | Refrigerant Type | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the refrigerant type | The listed refrigerant in EECP should match the nameplate | QA Checklist | Use the make and model number to locate the refrigerant type | The refrigerant type should be listed on the manufacturer specfication sheet or can be validated with nameplate data | New Property added | 2022-05-13 | Kenny Liljestrom |  |  | 16
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed |  | EECP | 10 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 12
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed |  | EECP | 11 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 8
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | UpDeemed |  | EECP | 12 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 15
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | Any |  | EECP | 13 | E-5152 Data Collection Requirements | Yes | Capacity | Cooling Capacity (kBtu/hr) | Numeric Value | [9 empty] | Inspections | Photograph the equipment nameplate to capture the cooling capacity (tons or Btu/hr) | The Cooling Capacity on the nameplate, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) | QA Checklist | Use the submitted invoice or installation report to validate the cooling capacity (btu/hr or tons) | The Cooling Capacity on the specification sheet, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) |  | 2022-02-09 | Kenny Liljestrom |  |  | 26
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | Any |  | EECP | 14 | For units from 65,000 Btu/h to less than 135,000 Btu/h rated capacity: • ≥12.0 EER • ≥19.0 IEER | Yes | EER | EER | Numeric Value | [8 empty] | Must be >= 12 | Inspections | Photograph the equipment nameplate to capture the EER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the EER | The EER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 3
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | A | Any | Any |  | EECP | 15 | For units from 65,000 Btu/h to less than 135,000 Btu/h rated capacity: • ≥12.0 EER • ≥19.0 IEER | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 19 | Inspections | Photograph the equipment nameplate to capture the EER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | B | Any | Any |  | EECP | 16 | For units from 135,000 Btu/h to less than 240,000 Btu/h rated capacity: • ≥12.0 EER • ≥17.5 IEER | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 17.5 | Inspections | Photograph the equipment nameplate to capture the EER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | Any |  | EECP | 17 | For both size categories: • Must contain advanced compressor capacity control (either a variable speed compressor, tandem compressors on a single refrigeration circuit, or multiple-step compressors) • Must contain a multi-speed (three steps or greater) indoor fan • Gas-furnace heating section (no requirements on thermal efficiency) • Must be a commercial unitary air conditioner subject to 10 CFR §431.97 | Yes | CompressorControl | Compressor(s) control type | Drop Down List | Variable speed compressor(s);Multiple-step compressor(s);Multiple compressors operating on a single refrigeration circuit (tandem compressors); | [8 empty] | QA Checklist | Use the manufacturer specification sheet to determine the type of cooling compressor type and control strategy | The compressor type and control strategy listed in the specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 26
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | Any |  | EECP | 18 | For both size categories: • Must contain advanced compressor capacity control (either a variable speed compressor, tandem compressors on a single refrigeration circuit, or multiple-step compressors) • Must contain a multi-speed (three steps or greater) indoor fan • Gas-furnace heating section (no requirements on thermal efficiency) • Must be a commercial unitary air conditioner subject to 10 CFR §431.97 | Yes | MultiSpeed | Unit has multi-speed indoor fan and gas furnace heating? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the manufacturer specification sheet to determine the type of indoor fan control strategy and if the unit has a gas furnace heating coil or section | The indoor fan must have variable or multi-speed controls and the unit must be heated by a gas furnace | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 56
1 | SWHC043 | 2 | Multiple Capacity Unitary Air-Cooled Air Conditioners between 65 and 240 kBtu/hr, Commercial | Any | Any | Any |  | EECP | 19 | Central chilled water hydronic systems and domestic hot water systems are not eligible. | Yes | ChilledWater | System is served by chilled water or serves domestic hot water? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 63
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Heat Pump Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2022-02-09 | Kenny Liljestrom |  |  | 22
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Heat Pump Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2022-02-09 | Kenny Liljestrom |  |  | 15
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed |  | EECP | 3 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes |  | Building type | Drop Down List | Single Family Home;Mobile Home;Multifamily Dwelling; | [8 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report to determine the customer building type | The building type should match what is listed in EECP | This property is acceptable to configure at the enrollment level | 2022-02-09 | Kenny Liljestrom |  |  | 13
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI |  | EECP | 4 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes |  | Building type | Drop Down List | Single Family Home;Mobile Home;Multifamily Dwelling; | [8 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report to determine the customer building type | The building type should match what is listed in EECP | This property is acceptable to configure at the enrollment level | 2022-02-09 | Kenny Liljestrom |  |  | 13
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | Any |  | EECP | 5 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single family, multi-family or mobile homes), and cooling and heating efficiency. | Yes |  | Rated equipment capacity (kBtu/hr) | Numeric Value | [9 empty] | Inspections | Photograph the equipment nameplate to capture the cooling capacity (tons or Btu/hr) | The Cooling Capacity on the nameplate, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) | QA Checklist | Use the submitted invoice or installation report to validate the cooling capacity (btu/hr or tons) | The Cooling Capacity on the specification sheet, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) the calculated value should align with the measure case description |  | 2022-02-09 | Kenny Liljestrom |  |  | 34
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | A | Any | Any |  | EECP | 6 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [8 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | A | Any | Any |  | EECP | 7 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | B | Any | Any |  | EECP | 8 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [8 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | B | Any | Any |  | EECP | 9 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | C | Any | Any |  | EECP | 10 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [8 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | C | Any | Any |  | EECP | 11 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | D | Any | Any |  | EECP | 12 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [8 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | D | Any | Any |  | EECP | 13 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | E | Any | Any |  | EECP | 14 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [8 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | E | Any | Any |  | EECP | 15 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | F | Any | Any |  | EECP | 16 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [8 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | F | Any | Any |  | EECP | 17 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | G | Any | Any |  | EECP | 18 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [8 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | G | Any | Any |  | EECP | 19 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | H | Any | Any |  | EECP | 20 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [8 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | H | Any | Any |  | EECP | 21 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | I | Any | Any |  | EECP | 22 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [8 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | I | Any | Any |  | EECP | 23 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | J | Any | Any |  | EECP | 24 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [8 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | J | Any | Any |  | EECP | 25 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | K | Any | Any |  | EECP | 26 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [8 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | K | Any | Any |  | EECP | 27 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | L | Any | Any |  | EECP | 28 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [8 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | L | Any | Any |  | EECP | 29 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | M | Any | Any |  | EECP | 30 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [8 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | M | Any | Any |  | EECP | 31 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | N | Any | Any |  | EECP | 32 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [8 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | N | Any | Any |  | EECP | 33 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | O | Any | Any |  | EECP | 34 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [8 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | O | Any | Any |  | EECP | 35 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | P | Any | Any |  | EECP | 36 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | SEER | Numeric Value | [8 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | P | Any | Any |  | EECP | 37 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed |  | EECP | 38 | For midstream delivery the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions, and the program administrator shall adjust claimed savings based upon these survey results. | Yes |  | Customer existing baseline fuel type | Drop Down List | Gas;Electric; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 36
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed |  | EECP | 39 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single family, multi-family or mobile homes), and cooling and heating efficiency. | Yes |  | Retailor or distributor zip code | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | This property can be neglected if the zip code is captured at the enrollment level and it is translated into a CZ | 2022-02-09 | Kenny Liljestrom |  |  | 32
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed |  | EECP | 40 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes |  | List other electrification measures installed | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 45
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed |  | QA Checklist | 41 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes |  | Itemized invoices submitted with upgrade costs for additional electrification measures? | Drop Down List | Yes;N/A; | [8 empty] | QA Checklist | Review the submitted files in EECP or the installation report for an itemized invoice showing any additional electrical infrastructure costs | If any electrification measures are listed, ensure an itemized invoice of the costs is submitted as well | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 87
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed |  | QA Checklist | 42 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes |  | Photograph(s) of existing cooling and heating equipment submitted? | Drop Down List | Yes; | [8 empty] | QA Checklist | Review EECP for photographs of the existing cooling and heating equipment | Check the measure case description to see if photographs of the cooling and heating equipment (if applicable) have been submitted | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 66
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI |  | EECP | 43 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes |  | List other electrification measures installed | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 45
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI |  | QA Checklist | 44 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes |  | Itemized invoices submitted with upgrade costs for additional electrification measures? | Drop Down List | Yes;N/A; | [8 empty] | QA Checklist | Review the submitted files in EECP or the installation report for an itemized invoice showing any additional electrical infrastructure costs | If any electrification measures are listed, ensure an itemized invoice of the costs is submitted as well | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 87
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI |  | QA Checklist | 45 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). • For measure case without existing cooling load, verify for the existing condition there is only space heating furnace equipment (excluding any type of cooling equipment) serving the home. | Yes |  | Photograph of existing heating equipment submitted? | Drop Down List | Yes; | [8 empty] | QA Checklist | Review EECP for photographs of the existing cooling and heating equipment | Check the measure case description to see if photographs of the cooling and heating equipment (if applicable) have been submitted | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 51
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | Any |  | EECP | 46 | The mini-split heat pump unit must meet or exceed the minimum efficiency requirements set forth in the measure. The existing furnace and air conditioning equipment must be removed and disposed of rather than refurbished and sold. Existing gas line(s) serving removed gas equipment must be capped off and removed refrigerant must be handled and disposed in accordance with all state and local regulations including but not limited to CA Energy Standards, CA Building Code, CA Pluming Code, and NEC. | Yes |  | Existing equipment removed and disposed of rather than refurbished and sold? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 76
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | Any |  | QA Checklist | 47 | This measure is not eligible when there is no natural gas to electricity fuel substitution for heating and/or when the measures include a non-regulated fuel. New construction measures are only eligible under certain conditions listed in the above section. Ground up constructions are not eligible. | Yes |  | This measure is not eligible when there is no natural gas to electricity fuel substitution for heating and/or when the measures include a non-regulated fuel. New construction measures are only eligible under certain conditions listed in the above section. Ground up constructions are not eligible. | Text Box | [9 empty] | QA Checklist | Use EECP to verify the customer has an active natural gas account | The customer must have a natural gas account to prove they are not using a non-regulated fuel (propane) as the base case equipment | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 298
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed |  | EECP | 48 | Per CPUC Decision 19-08-009 , building infrastructure costs which include panel upgrades or gas line installations/upgrades required to facilitate these fuel substitution measures shall be collected for 10% of each downstream and direct install measures. | Yes |  | Building infrastructure costs (i.e. panel upgrades or gas installation/upgrades) | Numeric Value | [9 empty] | QA Checklist | Use the submitted invoice or installation report to locate any infrastructure upgrade costs | The infrastructure costs should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 80
0 | SWHC044 | 2 | Ductless HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI |  | EECP | 49 | Per CPUC Decision 19-08-009 , building infrastructure costs which include panel upgrades or gas line installations/upgrades required to facilitate these fuel substitution measures shall be collected for 10% of each downstream and direct install measures. | Yes |  | Building infrastructure costs (i.e. panel upgrades or gas installation/upgrades) | Numeric Value | [9 empty] | QA Checklist | Use the submitted invoice or installation report to locate any infrastructure upgrade costs | The infrastructure costs should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 80
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed |  | EECP | 1 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | - | Building Type | Drop Down List | SFm;MFm;DMo; | [8 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report to determine the building type of the customer | The building type should match what is listed in EECP | Property can be configured at the enrollment level | 2022-02-09 | Kenny Liljestrom |  |  | 13
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI |  | EECP | 2 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | - | Building Type | Drop Down List | SFm;MFm;DMo; | [8 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report to determine the building type of the customer | The building type should match what is listed in EECP | Property can be configured at the enrollment level | 2022-02-09 | Kenny Liljestrom |  |  | 13
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | UpDeemed |  | EECP | 3 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | UpDeemed |  | EECP | 4 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | UpDeemed |  | EECP | 5 | E-5152 Data Collection Requirements | Yes | Measure Size Category | Measure Size Category | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | Any |  | EECP | 6 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The manufacturer listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2022-02-09 | Kenny Liljestrom |  |  | 12
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | Any |  | EECP | 7 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The model number listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the model number | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2022-02-09 | Kenny Liljestrom |  |  | 5
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | UpDeemed |  | EECP | 8 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | UpDeemed |  | EECP | 9 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | UpDeemed |  | EECP | 10 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | UpDeemed |  | EECP | 11 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | ZC | Zip Code | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | UpDeemed |  | EECP | 12 |  | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15