1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | Any |  | EECP | 13 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | Capacity | Cooling Capacity (kBtu/hr) | Numeric Value | [9 empty] | Inspections | Photograph the equipment nameplate to capture the cooling capacity (tons or Btu/hr) | The Cooling Capacity on the nameplate, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) | QA Checklist | Use the submitted invoice or installation report to validate the cooling capacity (btu/hr or tons) | The Cooling Capacity on the specification sheet, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) |  | 2022-02-09 | Kenny Liljestrom |  |  | 26
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | A | Any | Any |  | EECP | 14 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | A | Any | Any |  | EECP | 15 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | B | Any | Any |  | EECP | 16 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | B | Any | Any |  | EECP | 17 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | C | Any | Any |  | EECP | 18 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | C | Any | Any |  | EECP | 19 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | D | Any | Any |  | EECP | 20 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | D | Any | Any |  | EECP | 21 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | E | Any | Any |  | EECP | 22 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | E | Any | Any |  | EECP | 23 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | F | Any | Any |  | EECP | 24 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | F | Any | Any |  | EECP | 25 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | G | Any | Any |  | EECP | 26 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | G | Any | Any |  | EECP | 27 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | H | Any | Any |  | EECP | 28 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 4
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | H | Any | Any |  | EECP | 29 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed building type where the product will be installed (single-family, multifamily or mobile homes), and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-09 | Kenny Liljestrom |  |  | 42
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | AR | Any |  | EECP | 30 | In addition, preponderance of evidence (POE) must be documented for accelerated replacement measure application types. Notably, programs shall document if the existing equipment (AR) was replaced as a direct result of information, recommendations, and support provided by the program administrator (PA), and programs shall require the collection and submission of documentation to ensure proper conformance with eligibility and implementation requirements. The following are the types of information that will be required for all projects: Customer/site information Specifications of existing equipment Proof that the existing air conditioner and gas furnace are still operating as intended Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life Replacement central heat pump information | Yes |  | Has all the preponderance of evidence required by the measure package been uploaded in EECP? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Check EECP for any POE related documents | Preponderance of evidence (POE) must be documented including: • Customer/site information • Specifications of existing equipment • Proof that the existing air conditioner and gas furnace are still operating as intended • Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life • Replacement central heat pump information | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 92
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed |  | EECP | 31 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Customer existing baseline fuel type | Drop Down List | Gas;Electric; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 36
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed |  | EECP | 32 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | List other electrification measures installed | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 45
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed |  | QA Checklist | 33 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Itemized invoices submitted with upgrade costs for additional electrification measures? | Drop Down List | Yes;N/A; | [8 empty] | QA Checklist | Review the submitted files in EECP or the installation report for an itemized invoice showing any additional electrical infrastructure costs | If any electrification measures are listed, ensure an itemized invoice of the costs is submitted as well | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 87
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed |  | QA Checklist | 34 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Photograph(s) of existing cooling and heating equipment submitted? | Drop Down List | Yes; | [8 empty] | QA Checklist | Review EECP for photographs of the existing cooling and heating equipment | Check the measure case description to see if photographs of the cooling and heating equipment (if applicable) have been submitted | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 66
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed |  | EECP | 35 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Building infrastructure costs (i.e. panel upgrades or gas installation/upgrades) | Numeric Value | [9 empty] | QA Checklist | Use the submitted invoice or installation report to locate any infrastructure upgrade costs | The infrastructure costs should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 80
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI |  | EECP | 36 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Customer existing baseline fuel type | Drop Down List | Gas;Electric; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 36
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI |  | EECP | 37 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | List other electrification measures installed | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-09 | Kenny Liljestrom |  |  | 45
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI |  | QA Checklist | 38 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Itemized invoices submitted with upgrade costs for additional electrification measures? | Drop Down List | Yes;N/A; | [8 empty] | QA Checklist | Review the submitted files in EECP or the installation report for an itemized invoice showing any additional electrical infrastructure costs | If any electrification measures are listed, ensure an itemized invoice of the costs is submitted as well | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 87
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI |  | QA Checklist | 39 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Photograph(s) of existing cooling and heating equipment submitted? | Drop Down List | Yes; | [8 empty] | QA Checklist | Review EECP for photographs of the existing cooling and heating equipment | Check the measure case description to see if photographs of the cooling and heating equipment (if applicable) have been submitted | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 66
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI |  | EECP | 40 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Building infrastructure costs (i.e. panel upgrades or gas installation/upgrades) | Numeric Value | [9 empty] | QA Checklist | Use the submitted invoice or installation report to locate any infrastructure upgrade costs | The infrastructure costs should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 80
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | Any |  | - | 41 | This measure involves fuel substitution and the implementer must replace an existing central air conditioner and a natural gas furnace. Care must be taken that the existing gas lines are capped off and meet the local code requirements. | No |  | - | None | - | [7 empty] | - | - | - | - | - | - | - | No property required, written in 3PI contracts | 2022-02-09 | Kenny Liljestrom |  |  | 1
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemed |  | EECP | 42 | This measure is not applicable for new construction installations. However new services, as defined in Fuel Substitution Technical Guidance for Energy Efficiency, are eligible. R1087 (Page 3) New service measures are only eligible for downstream and direct install delivery types when: Measures are installed in new areas of an existing building, Measures are installed in a major renovation of an existing building, or Measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. | Yes |  | Installation is part of a new service defined in Fuel Substitution Technical Guidance for EE? | Text Box | Yes;No; | [8 empty] | QA Checklist | If this answer is 'Yes' the 3PI needs to meet certain criteria and provide proof of the following: • Measures are installed in new areas of an existing building, • Measures are installed in a major renovation of an existing building, or • Measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. | A photograph or other type of proof can be submitted to prove one of the three scenarios when a new service measure is eligible | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 93
1 | SWHC045 | 1 | Heat Pump HVAC, Fuel Substitution, Residential | Any | Any | DnDeemDI |  | EECP | 43 | This measure is not applicable for new construction installations. However new services, as defined in Fuel Substitution Technical Guidance for Energy Efficiency, are eligible. R1087 (Page 3) New service measures are only eligible for downstream and direct install delivery types when: Measures are installed in new areas of an existing building, Measures are installed in a major renovation of an existing building, or Measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. | Yes |  | Installation is part of a new service defined in Fuel Substitution Technical Guidance for EE? | Text Box | Yes;No; | [8 empty] | QA Checklist | If this answer is 'Yes' the 3PI needs to meet certain criteria and provide proof of the following: • Measures are installed in new areas of an existing building, • Measures are installed in a major renovation of an existing building, or • Measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. | A photograph or other type of proof can be submitted to prove one of the three scenarios when a new service measure is eligible | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-09 | Kenny Liljestrom |  |  | 93
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed |  | EECP | 1 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed |  | EECP | 2 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | Any |  | EECP | 3 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The manufacturer listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2022-02-10 | Kenny Liljestrom |  |  | 12
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | Any |  | EECP | 4 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The model number listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the model number | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2022-02-10 | Kenny Liljestrom |  |  | 5
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed |  | EECP | 5 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed |  | EECP | 6 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed |  | EECP | 7 | E-5152 Data Collection Requirements | Yes | Measure Size Category | Measure Size Category | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed |  | EECP | 8 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed |  | EECP | 9 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed |  | EECP | 10 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | Any |  | EECP | 11 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | Capacity | Cooling Capacity (kBtu/hr) | Numeric Value | [9 empty] | Inspections | Photograph the equipment nameplate to capture the cooling capacity (tons or Btu/hr) | The Cooling Capacity on the nameplate, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) | QA Checklist | Use the submitted invoice or installation report to validate the cooling capacity (btu/hr or tons) | The Cooling Capacity on the specification sheet, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) |  | 2022-02-10 | Kenny Liljestrom |  |  | 26
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | A | Any | Any |  | EECP | 12 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | A | Any | Any |  | EECP | 13 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.2 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | O | Any | Any |  | EECP | 14 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | O | Any | Any |  | EECP | 15 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.2 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AC | Any | Any |  | EECP | 16 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AC | Any | Any |  | EECP | 17 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.2 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | B | Any | Any |  | EECP | 18 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | B | Any | Any |  | EECP | 19 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.2 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | P | Any | Any |  | EECP | 20 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | P | Any | Any |  | EECP | 21 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.2 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AD | Any | Any |  | EECP | 22 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AD | Any | Any |  | EECP | 23 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.2 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | C | Any | Any |  | EECP | 24 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | C | Any | Any |  | EECP | 25 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.5 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Q | Any | Any |  | EECP | 26 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Q | Any | Any |  | EECP | 27 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.5 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AE | Any | Any |  | EECP | 28 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AE | Any | Any |  | EECP | 29 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.5 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | D | Any | Any |  | EECP | 30 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | D | Any | Any |  | EECP | 31 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | R | Any | Any |  | EECP | 32 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | R | Any | Any |  | EECP | 33 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AF | Any | Any |  | EECP | 34 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AF | Any | Any |  | EECP | 35 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | E | Any | Any |  | EECP | 36 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | E | Any | Any |  | EECP | 37 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | S | Any | Any |  | EECP | 38 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | S | Any | Any |  | EECP | 39 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AG | Any | Any |  | EECP | 40 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 15 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AG | Any | Any |  | EECP | 41 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | F | Any | Any |  | EECP | 42 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | F | Any | Any |  | EECP | 43 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | T | Any | Any |  | EECP | 44 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | T | Any | Any |  | EECP | 45 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AH | Any | Any |  | EECP | 46 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 16 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AH | Any | Any |  | EECP | 47 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | G | Any | Any |  | EECP | 48 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | G | Any | Any |  | EECP | 49 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | U | Any | Any |  | EECP | 50 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | U | Any | Any |  | EECP | 51 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AI | Any | Any |  | EECP | 52 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 17 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AI | Any | Any |  | EECP | 53 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.4 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | H | Any | Any |  | EECP | 54 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | H | Any | Any |  | EECP | 55 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | V | Any | Any |  | EECP | 56 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | V | Any | Any |  | EECP | 57 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AJ | Any | Any |  | EECP | 58 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | SEER | SEER | Numeric Value | [8 empty] | Must be >= 18 | Inspections | Photograph the equipment nameplate to capture the SEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the SEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the SEER | The SEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AJ | Any | Any |  | EECP | 59 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | HSPF | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.7 | Inspections | Photograph the equipment nameplate to capture the Heating Seasonal Performance Factor (HSPF) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the HSPF on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Heating Seasonal Performance Factor (HSPF) | The HSPF listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 42
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | I | Any | Any |  | EECP | 60 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 14.4 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | I | Any | Any |  | EECP | 61 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | W | Any | Any |  | EECP | 62 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 14.4 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | W | Any | Any |  | EECP | 63 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AK | Any | Any |  | EECP | 64 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 14.4 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AK | Any | Any |  | EECP | 65 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | J | Any | Any |  | EECP | 66 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 15.4 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | J | Any | Any |  | EECP | 67 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | X | Any | Any |  | EECP | 68 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 15.4 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | X | Any | Any |  | EECP | 69 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AL | Any | Any |  | EECP | 70 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 15.4 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AL | Any | Any |  | EECP | 71 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | K | Any | Any |  | EECP | 72 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 12.3 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | K | Any | Any |  | EECP | 73 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Y | Any | Any |  | EECP | 74 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 12.3 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Y | Any | Any |  | EECP | 75 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AM | Any | Any |  | EECP | 76 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 12.3 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AM | Any | Any |  | EECP | 77 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | L | Any | Any |  | EECP | 78 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 12.8 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | L | Any | Any |  | EECP | 79 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Z | Any | Any |  | EECP | 80 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 12.8 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Z | Any | Any |  | EECP | 81 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AN | Any | Any |  | EECP | 82 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 12.8 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AN | Any | Any |  | EECP | 83 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.2 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | M | Any | Any |  | EECP | 84 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 14.1 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | M | Any | Any |  | EECP | 85 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.4 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AA | Any | Any |  | EECP | 86 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 14.1 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AA | Any | Any |  | EECP | 87 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.4 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AO | Any | Any |  | EECP | 88 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 14.1 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AO | Any | Any |  | EECP | 89 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.4 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | N | Any | Any |  | EECP | 90 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 14.8 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | N | Any | Any |  | EECP | 91 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.4 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AB | Any | Any |  | EECP | 92 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 14.8 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AB | Any | Any |  | EECP | 93 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.4 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AP | Any | Any |  | EECP | 94 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | IEER | IEER | Numeric Value | [8 empty] | Must be >= 14.8 | Inspections | Photograph the equipment nameplate to capture the IEER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IEER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the IEER | The IEER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 4
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | AP | Any | Any |  | EECP | 95 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | COP | Coefficient of Performance (COP) | Numeric Value | [8 empty] | Must be >= 3.4 | Inspections | Photograph the equipment nameplate to capture the Coefficient of Performance (COP) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the COP on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Coefficient of Performance (COP) | The COP listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | UpDeemed |  | EECP | 96 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | No | - | Retailor or distributor zip code | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | This property can be neglected if the zip code is captured at the enrollment level and it is translated into a CZ | 2022-02-10 | Kenny Liljestrom | Property removed in leiu of CZ field |  | 32
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | Any |  | EECP | 97 | Required Documentation for Normal Replacement in Upstream and Mid-Stream Delivery: For upstream/mid-stream delivery method, the participant baselines are unknown and the spillover effects are unknown. The manufacturer or distributor doesn’t know whether the purchased measure is replacing a gas or an electric baseline appliance. Claimed savings for these delivery types will be adjusted using the ratio of baseline gas appliance to total baseline appliances. For Midstream delivery, the implementer shall survey 10% of the mid-stream baseline existing conditions and fuel type to determine actual gas/electric baseline proportions and the program administrator shall adjust claimed savings based upon these survey results. For upstream delivery, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, proposed commercial building type or space where the product will be installed, and cooling and heating efficiency. | Yes | - | Building Type | Drop Down List | Asm;Com;ECC;EPr;ERC;ESe;EUn;Gro;HGR;Hsp;Htl;MBT;MLI;Mtl;Nrs;OfL;OfS;RFF;RSD;Rt3;RtL;RtS;SCn;SUn;WRf; | [8 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report to determine the building type of the customer | The building type should match what is listed in EECP | Property can be configured at the enrollment level | 2022-02-10 | Kenny Liljestrom |  |  | 13
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | AR | Any |  | EECP | 98 | Preponderance of evidence (POE) must be documented. Notably, programs shall document if measure was replaced as a direct result of information, recommendations, and support provided by the Program Administrator, and programs shall require the collection and submission of documentation to ensure proper conformance to eligibility and implementation requirements. The following are the types of information that will be required for all projects: − Customer/site information − Specifications of existing equipment − Proof that the existing air conditioner and gas furnace are still operating as intended − Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life − Replacement central heat pump information To document POE, the provided Preponderance of Evidence (POE) survey12 or similar, should be completed. | Yes |  | Has all the preponderance of evidence required by the measure package been uploaded in EECP? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Check EECP for any POE related documents | Preponderance of evidence (POE) must be documented including: − Customer/site information − Specifications of existing equipment − Proof that the existing air conditioner and gas furnace are still operating as intended − Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life − Replacement central heat pump information | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-10 | Kenny Liljestrom |  |  | 92
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | NC | Any |  | EECP | 99 | Implementer should confirm and provide required documentation to verify that measure implementation meets one of the following conditions: • measures are installed in new areas of an existing building, • measures are installed in a major renovation of an existing building, or • measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. Required documentation can include ONE of the following: • Existing utility bills for the building, • City approved permitting, • City approved Mechanical, or Electrical, or Architecture site drawings, or • Title-24 compliance report | Yes |  | Required NC document(s) submitted as outlined in the measure package? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Check EECP for any New Construction related documents | Implementer should confirm and provide required documentation to verify that measure implementation meets one of the following conditions: • measures are installed in new areas of an existing building, • measures are installed in a major renovation of an existing building, or • measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. Required documentation can include ONE of the following: • Existing utility bills for the building, • City approved permitting, • City approved Mechanical, or Electrical, or Architecture site drawings, or • Title-24 compliance report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-10 | Kenny Liljestrom |  |  | 69
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | DnDeemed |  | EECP | 100 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Customer existing baseline fuel type | Drop Down List | Gas;Electric; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-10 | Kenny Liljestrom |  |  | 36
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | DnDeemed |  | EECP | 101 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | List other electrification measures installed | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-10 | Kenny Liljestrom |  |  | 45
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | DnDeemed |  | QA Checklist | 102 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Itemized invoices submitted with upgrade costs for additional electrification measures? | Drop Down List | Yes;N/A; | [8 empty] | QA Checklist | Review the submitted files in EECP or the installation report for an itemized invoice showing any additional electrical infrastructure costs | If any electrification measures are listed, ensure an itemized invoice of the costs is submitted as well | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-10 | Kenny Liljestrom |  |  | 87
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | DnDeemed |  | QA Checklist | 103 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Photograph(s) of existing cooling and heating equipment submitted? | Drop Down List | Yes; | [8 empty] | QA Checklist | Review EECP for photographs of the existing cooling and heating equipment | Check the measure case description to see if photographs of the cooling and heating equipment (if applicable) have been submitted | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-10 | Kenny Liljestrom |  |  | 66
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | DnDeemDI |  | EECP | 104 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Customer existing baseline fuel type | Drop Down List | Gas;Electric; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-10 | Kenny Liljestrom |  |  | 36
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | DnDeemDI |  | EECP | 105 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | List other electrification measures installed | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-10 | Kenny Liljestrom |  |  | 45
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | DnDeemDI |  | QA Checklist | 106 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Itemized invoices submitted with upgrade costs for additional electrification measures? | Drop Down List | Yes;N/A; | [8 empty] | QA Checklist | Review the submitted files in EECP or the installation report for an itemized invoice showing any additional electrical infrastructure costs | If any electrification measures are listed, ensure an itemized invoice of the costs is submitted as well | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-10 | Kenny Liljestrom |  |  | 87
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | DnDeemDI |  | QA Checklist | 107 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: • What is the existing fuel type for space heating? • Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. • Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes |  | Photograph(s) of existing cooling and heating equipment submitted? | Drop Down List | Yes; | [8 empty] | QA Checklist | Review EECP for photographs of the existing cooling and heating equipment | Check the measure case description to see if photographs of the cooling and heating equipment (if applicable) have been submitted | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-10 | Kenny Liljestrom |  |  | 66
0 | SWHC046 | 1 | Heat Pump, Unitary Air-Cooled HVAC, Fuel Substitution, Commercial | Any | Any | Any |  | EECP | 108 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must to be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | InfraCosts | Building infrastructure costs (i.e. panel upgrades or gas installation/upgrades) | Numeric Value | [9 empty] | QA Checklist | Use the submitted invoice or installation report to locate any infrastructure upgrade costs | The infrastructure costs should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-02-10 | Kenny Liljestrom |  |  | 80
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | Any |  | EECP | 1 | This measure requires the installation of an air-to-water RTU air conditioner unit for a fast food restaurant that is capable of utilizing waste heat to preheat incoming water from the main. See Measure Case Description. | Yes | - | Building is a fast food restaurant (RFF)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report to determine the building type of the customer | The building type should match what is listed in EECP | This property can be configured at the enrollment level | 2022-02-10 | Kenny Liljestrom |  |  | 41
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | UpDeemed |  | EECP | 2 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | UpDeemed |  | EECP | 3 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | UpDeemed |  | EECP | 4 | E-5152 Data Collection Requirements | Yes | Measure Size Category | Measure Size Category | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | Any |  | EECP | 5 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The manufacturer listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2022-02-10 | Kenny Liljestrom |  |  | 12
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | Any |  | EECP | 6 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The model number listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the model number | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2022-02-10 | Kenny Liljestrom |  |  | 5
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | UpDeemed |  | EECP | 7 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | UpDeemed |  | EECP | 8 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | UpDeemed |  | EECP | 9 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | UpDeemed |  | EECP | 10 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | UpDeemed |  | EECP | 11 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
1 | SWHC048 | 2 | Packaged Air Conditioner Heat Recovery, Commercial | Any | Any | Any |  | EECP | 12 | This measure requires the installation of an air-to-water RTU air conditioner unit for a fast food restaurant that is capable of utilizing waste heat to preheat incoming water from the main. See Measure Case Description. | Yes | HeatUse | Heat used to preheat service hot water (not domestic hot water)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-10 | Kenny Liljestrom |  |  | 64
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-08-17 | Kenny Liljestrom |  | Add | 12
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-08-17 | Kenny Liljestrom |  | Add | 5
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | Any |  | EECP | 3 | Only those air conditioning and heat pump systems covered by AHRI 210/240 2008 are eligible. Efficiency values must be certified by Air-conditioning Heating and Refrigeration Institute (AHRI) as verified by the AHRI certification number. | Yes |  | AHRI certification number | Text Box | [9 empty] | QA Checklist | Use the submitted AHRI number from EECP to cross-check the AHRI database | The AHRI database should be able to match the certification number to the make and model above | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-18 | Kenny Liljestrom |  | Add | 25
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | Any |  | EECP | 4 | - | Yes | Building vintage | Building Vintage | Drop Down List | Existing;New Construction; | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | Can be removed; data in measure description | 2021-08-17 | Kenny Liljestrom |  | Add | 16
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | Any |  | EECP | 5 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Building type | Drop Down List | Single Family;Multifamily;Mobile home; | [8 empty] | Inspections | Document the type of residence the unit was installed in (Single Family Home, Multifamily, or Mobile Home) | The building type listed in EECP should match the building type during the inspection | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP | Not configured in original upload | 2021-08-18 | Kenny Liljestrom |  | Add | 13
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | UpDeemed |  | EECP | 6 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes | ZC | Zip Code | Numeric Value | [9 empty] | QA Checklist | Evaluate the zip code in EECP for accuracy | Ensure zip code is real and locatable | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-17 | Kenny Liljestrom |  | Add | 8
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | UpDeemed |  | EECP | 7 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | Lookup formula based on Zip Code | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-08-17 | Kenny Liljestrom |  | Add | 15
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | AR | Any |  | EECP | 8 | Preponderance of evidence (POE) must be documented. Notably, programs shall document if measure was replaced as a direct result of information, recommendations, and support provided by the Program Administrator, and programs shall require the collection and submission of documentation to ensure proper conformance to eligibility and implementation requirements. The following are the types of information that will be required for all projects: Customer/site information Specifications of existing equipment Proof that the existing air conditioner and gas furnace are still operating as intended Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life Replacement central heat pump information To document POE, the provided Preponderance of evidence (POE) survey, or similar, should be completed | Yes |  | Has all POE documentation been submitted as defined in the workpaper? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Check the EECP documentation for any Preponderance of Evidence (POE) | Preponderance of evidence (POE) must be documented. Notably, programs shall document if measure was replaced as a direct result of information, recommendations, and support provided by the Program Administrator, and programs shall require the collection and submission of documentation to ensure proper conformance to eligibility and implementation requirements. The following are the types of information that will be required for all projects: Customer/site information Specifications of existing equipment Proof that the existing air conditioner and gas furnace are still operating as intended Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life Replacement central heat pump information To document POE, the provided Preponderance of evidence (POE) survey, or similar, should be completed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 69
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | Any |  | EECP | 9 | For split systems the certification will specify an evaporator coil model and may specify additional components. In some cases, a furnace is specified in the certificate. In this case since the furnace is specified as part of the AC system it will not be eligible for a separate incentive. | Yes |  | Does the split system have a furnace in the AHRI certification that has already received a rebate? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | QA Checklist | Use the EECP double dip report to check for previously installed measures; also check in the installation report to determine if the report mentions a furnace rebate | For split systems the certification will specify an evaporator coil model and may specify additional components. In some cases, a furnace is specified in the certificate. In this case since the furnace is specified as part of the AC system it will not be eligible for a separate incentive. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 98
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Any | Any | Any |  | EECP | 10 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Cooling Capacity (kBtuh) | Numeric Value | [9 empty] | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the capacity (Btu/hr or kBtu/hr) is listed | The capacity (Btu/hr) in EECP must match what is listed in the spec sheet or installation report; if the value is listed in Btu/hr use the following formula to match EECP: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 24
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | A | Any | Any |  | EECP | 11 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | B | Any | Any |  | EECP | 12 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | C | Any | Any |  | EECP | 13 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | D | Any | Any |  | EECP | 14 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | E | Any | Any |  | EECP | 15 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | F | Any | Any |  | EECP | 16 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | G | Any | Any |  | EECP | 17 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | H | Any | Any |  | EECP | 18 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | I | Any | Any |  | EECP | 19 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | J | Any | Any |  | EECP | 20 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | K | Any | Any |  | EECP | 21 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | L | Any | Any |  | EECP | 22 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | M | Any | Any |  | EECP | 23 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | N | Any | Any |  | EECP | 24 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | O | Any | Any |  | EECP | 25 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | O | Any | Any |  | EECP | 26 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 8.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | P | Any | Any |  | EECP | 27 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | P | Any | Any |  | EECP | 28 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Q | Any | Any |  | EECP | 29 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Q | Any | Any |  | EECP | 30 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | R | Any | Any |  | EECP | 31 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | R | Any | Any |  | EECP | 32 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | S | Any | Any |  | EECP | 33 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | T | Any | Any |  | EECP | 34 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | U | Any | Any |  | EECP | 35 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | V | Any | Any |  | EECP | 36 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | W | Any | Any |  | EECP | 37 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | X | Any | Any |  | EECP | 38 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Y | Any | Any |  | EECP | 39 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | Z | Any | Any |  | EECP | 40 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AA | Any | Any |  | EECP | 41 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AB | Any | Any |  | EECP | 42 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AC | Any | Any |  | EECP | 43 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AD | Any | Any |  | EECP | 44 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AE | Any | Any |  | EECP | 45 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AF | Any | Any |  | EECP | 46 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AG | Any | Any |  | EECP | 47 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AG | Any | Any |  | EECP | 48 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 8.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AH | Any | Any |  | EECP | 49 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AH | Any | Any |  | EECP | 50 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AI | Any | Any |  | EECP | 51 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AI | Any | Any |  | EECP | 52 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AJ | Any | Any |  | EECP | 53 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AJ | Any | Any |  | EECP | 54 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AK | Any | Any |  | EECP | 55 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AL | Any | Any |  | EECP | 56 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AM | Any | Any |  | EECP | 57 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AN | Any | Any |  | EECP | 58 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AO | Any | Any |  | EECP | 59 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AP | Any | Any |  | EECP | 60 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AQ | Any | Any |  | EECP | 61 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AR | Any | Any |  | EECP | 62 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AS | Any | Any |  | EECP | 63 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AT | Any | Any |  | EECP | 64 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AU | Any | Any |  | EECP | 65 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AV | Any | Any |  | EECP | 66 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AW | Any | Any |  | EECP | 67 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AX | Any | Any |  | EECP | 68 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AY | Any | Any |  | EECP | 69 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AY | Any | Any |  | EECP | 70 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 8.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AZ | Any | Any |  | EECP | 71 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | AZ | Any | Any |  | EECP | 72 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | BA | Any | Any |  | EECP | 73 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | BA | Any | Any |  | EECP | 74 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | BB | Any | Any |  | EECP | 75 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 39
0 | SWHC049 | 1 | SEER Rated AC and HP equipment, Residential | BB | Any | Any |  | EECP | 76 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-17 | Kenny Liljestrom |  | Add | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-23 | Kenny Liljestrom |  |  | 12
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-23 | Kenny Liljestrom |  |  | 5
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | Any |  | EECP | 3 | Only those air conditioning and heat pump systems covered by AHRI 210/240 2008 are eligible. Efficiency values must be certified by Air-conditioning Heating and Refrigeration Institute (AHRI) as verified by the AHRI certification number. | Yes |  | AHRI certification number | Text Box | [9 empty] | QA Checklist | Use the submitted AHRI number from EECP to cross-check the AHRI database | The AHRI database should be able to match the certification number to the make and model above | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 25
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | Any |  | EECP | 4 | - | Yes | Building vintage | Building Vintage | Drop Down List | Existing;New Construction; | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | Can be removed; data in measure description | 2021-11-23 | Kenny Liljestrom |  |  | 16
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | Any |  | EECP | 5 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Building type | Drop Down List | Single Family;Multifamily;Mobile home; | [8 empty] | Inspections | Document the type of residence the unit was installed in (Single Family Home, Multifamily, or Mobile Home) | The building type listed in EECP should match the building type during the inspection | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 13
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | UpDeemed |  | EECP | 6 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes | ZC | Zip Code | Numeric Value | [9 empty] | QA Checklist | Evaluate the zip code in EECP for accuracy | Ensure zip code is real and locatable | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 8
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | UpDeemed |  | EECP | 7 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes | ClimateZone | CA Climate Zone | Formula | [8 empty] | Lookup formula based on Zip Code | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 15
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | AR | Any |  | EECP | 8 | Preponderance of evidence (POE) must be documented. Notably, programs shall document if measure was replaced as a direct result of information, recommendations, and support provided by the Program Administrator, and programs shall require the collection and submission of documentation to ensure proper conformance to eligibility and implementation requirements. The following are the types of information that will be required for all projects: Customer/site information Specifications of existing equipment Proof that the existing air conditioner and gas furnace are still operating as intended Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life Replacement central heat pump information To document POE, the provided Preponderance of evidence (POE) survey, or similar, should be completed | Yes |  | Has all POE documentation been submitted as defined in the workpaper? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Check the EECP documentation for any Preponderance of Evidence (POE) | Preponderance of evidence (POE) must be documented. Notably, programs shall document if measure was replaced as a direct result of information, recommendations, and support provided by the Program Administrator, and programs shall require the collection and submission of documentation to ensure proper conformance to eligibility and implementation requirements. The following are the types of information that will be required for all projects: Customer/site information Specifications of existing equipment Proof that the existing air conditioner and gas furnace are still operating as intended Existing air conditioner and gas furnace nameplate data with manufacturer date to confirm remaining useful life Replacement central heat pump information To document POE, the provided Preponderance of evidence (POE) survey, or similar, should be completed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 69
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | Any |  | EECP | 9 | For split systems the certification will specify an evaporator coil model and may specify additional components. In some cases, a furnace is specified in the certificate. In this case since the furnace is specified as part of the AC system it will not be eligible for a separate incentive. | Yes |  | Does the split system have a furnace in the AHRI certification that has already received a rebate? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | QA Checklist | Use the EECP double dip report to check for previously installed measures; also check in the installation report to determine if the report mentions a furnace rebate | For split systems the certification will specify an evaporator coil model and may specify additional components. In some cases, a furnace is specified in the certificate. In this case since the furnace is specified as part of the AC system it will not be eligible for a separate incentive. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 98
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Any | Any | Any |  | EECP | 10 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Cooling Capacity (kBtuh) | Numeric Value | [9 empty] | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the capacity (Btu/hr or kBtu/hr) is listed | The capacity (Btu/hr) in EECP must match what is listed in the spec sheet or installation report; if the value is listed in Btu/hr use the following formula to match EECP: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 24
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | A | Any | Any |  | EECP | 11 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | B | Any | Any |  | EECP | 12 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | C | Any | Any |  | EECP | 13 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | D | Any | Any |  | EECP | 14 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | E | Any | Any |  | EECP | 15 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | F | Any | Any |  | EECP | 16 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | G | Any | Any |  | EECP | 17 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | H | Any | Any |  | EECP | 18 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | I | Any | Any |  | EECP | 19 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | J | Any | Any |  | EECP | 20 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | K | Any | Any |  | EECP | 21 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | L | Any | Any |  | EECP | 22 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | M | Any | Any |  | EECP | 23 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | N | Any | Any |  | EECP | 24 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | O | Any | Any |  | EECP | 25 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | O | Any | Any |  | EECP | 26 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 8.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | P | Any | Any |  | EECP | 27 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | P | Any | Any |  | EECP | 28 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Q | Any | Any |  | EECP | 29 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Q | Any | Any |  | EECP | 30 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | R | Any | Any |  | EECP | 31 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | R | Any | Any |  | EECP | 32 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | S | Any | Any |  | EECP | 33 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | T | Any | Any |  | EECP | 34 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | U | Any | Any |  | EECP | 35 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | V | Any | Any |  | EECP | 36 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | W | Any | Any |  | EECP | 37 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | X | Any | Any |  | EECP | 38 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Y | Any | Any |  | EECP | 39 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | Z | Any | Any |  | EECP | 40 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AA | Any | Any |  | EECP | 41 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AB | Any | Any |  | EECP | 42 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AC | Any | Any |  | EECP | 43 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AD | Any | Any |  | EECP | 44 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AE | Any | Any |  | EECP | 45 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AF | Any | Any |  | EECP | 46 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AG | Any | Any |  | EECP | 47 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AG | Any | Any |  | EECP | 48 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 8.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AH | Any | Any |  | EECP | 49 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AH | Any | Any |  | EECP | 50 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AI | Any | Any |  | EECP | 51 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AI | Any | Any |  | EECP | 52 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AJ | Any | Any |  | EECP | 53 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AJ | Any | Any |  | EECP | 54 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AK | Any | Any |  | EECP | 55 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AL | Any | Any |  | EECP | 56 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AM | Any | Any |  | EECP | 57 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AN | Any | Any |  | EECP | 58 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AO | Any | Any |  | EECP | 59 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AP | Any | Any |  | EECP | 60 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AQ | Any | Any |  | EECP | 61 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AR | Any | Any |  | EECP | 62 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AS | Any | Any |  | EECP | 63 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AT | Any | Any |  | EECP | 64 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AU | Any | Any |  | EECP | 65 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AV | Any | Any |  | EECP | 66 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 19 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 19 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AW | Any | Any |  | EECP | 67 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 20 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 20 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AX | Any | Any |  | EECP | 68 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 21 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 21 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AY | Any | Any |  | EECP | 69 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 15 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 15 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AY | Any | Any |  | EECP | 70 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 8.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 8.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AZ | Any | Any |  | EECP | 71 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 16 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 16 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | AZ | Any | Any |  | EECP | 72 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.0 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | BA | Any | Any |  | EECP | 73 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 17 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 17 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | BA | Any | Any |  | EECP | 74 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.4 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.4 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | BB | Any | Any |  | EECP | 75 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Seasonal Energy Efficiency Ratio (SEER) | Numeric Value | [8 empty] | Must be >= 18 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Seasonal Energy Efficiency Ratio (SEER) is listed | The Seasonal Energy Efficiency Ratio (SEER) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 18 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 39
1 | SWHC049 | 2 | SEER Rated AC and HP equipment, Residential | BB | Any | Any |  | EECP | 76 | For upstream/mid-stream deliveries, the implementer should provide the retailer or distribution location where the product was sold and the product’s rated capacity (e.g., tons) and cooling and heating rated efficiencies (SEER/HSPF). Additionally, the implementer is encouraged to document and track the Residential building type where the product will be installed and submit that information at claims level on CEDARS website | Yes |  | Heating Seasonal Performance Factor (HSPF) | Numeric Value | [8 empty] | Must be >= 9.7 | QA Checklist | Use the submitted invoice, installation report, or spec sheet to validate the Heating Seasonal Performance Factor (HSPF) is listed | The Heating Seasonal Performance Factor (HSPF) listed in EECP should match the value listed in the invoice, installation report, or spec sheet; Value Must be >= 9.7 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-23 | Kenny Liljestrom |  |  | 42
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | Any |  | EECP | 0 | For midstream and upstream delivery types, when possible, the program administrator (PA) shall claim the “specific building type savings” in which the equipment will be installed and submit that information at claims level on CEDARS website. In cases where there is no “building type” information available for a given project, program administrator shall claim the weighted savings of “Com” building type. | No | - | Building Type | Drop Down List | Asm;Com;ECC;EPr;ERC;ESe;EUn;Gro;HGR;Hsp;Htl;MBT;MLI;Mtl;Nrs;OfL;OfS;RFF;RSD;Rt3;RtL;RtS;SCn;SUn;WRf; | [8 empty] | Inspections | Make note of the building type at the inspection site | The building type should match what is listed in EECP | QA Checklist | Use the installation report to determine the building type of the customer | The building type should match what is listed in EECP | Property can be configured at the enrollment level | 2022-02-10 | Kenny Liljestrom |  |  | 13
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | UpDeemed |  | EECP | 0 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 7
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | UpDeemed |  | EECP | 5 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | Any |  | EECP | 10 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The manufacturer listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2022-02-10 | Kenny Liljestrom |  |  | 12
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | Any |  | EECP | 15 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The model number listed in EECP should match the nameplate on the equipment | QA Checklist | Use the submitted invoice or installation report to validate the model number | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2022-02-10 | Kenny Liljestrom |  |  | 5
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | UpDeemed |  | EECP | 20 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number in EECP should match what is listed in the invoice or installation report |  | 2022-05-16 | Kenny Liljestrom |  |  | 13
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | UpDeemed |  | EECP | 25 | E-5152 Data Collection Requirements | Yes | RefNum | AHRI Reference Number | Text Box | [9 empty] | QA Checklist | Review the AHRI database to check for the make and model of the installed equipment | The equipment in EECP should be locatable on the AHRI database as being a certified product and should match the make and model of the equipment | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | UpDeemed |  | EECP | 30 | E-5152 Data Collection Requirements | Yes | Measure Size Category | Measure Size Category | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 21
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | UpDeemed |  | EECP | 35 | E-5152 Data Collection Requirements | Yes | RetailPrice | Retail Price | Numeric Value |  |  |  |  | Currency |  |  | 2 |  | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 12
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | UpDeemed |  | EECP | 190 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value |  |  |  |  | General |  |  | 0 |  | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 8
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | UpDeemed |  | EECP | 195 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-05-16 | Kenny Liljestrom |  |  | 15
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | Any | Any | Any |  | EECP | 40 | The energy and demand impacts of this measure are applicable only to commercial building applications with chiller equipment serving space conditioning. Chiller serving non-space comfort and/or processes and/or industrial applications is not eligible. | Yes | ChillerPurpose | Chiller used for space conditioning, not for processes or industrial applications? | Drop Down List | Yes;No; |  | Equal | Yes |  |  |  |  | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-02-10 | Kenny Liljestrom |  |  | 82
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | A | Any | Any |  | EECP | 45 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | Capacity (Tons) | Cooling Capacity (tons) | Numeric Value |  |  |  |  | General | 0 | 149 | 0 | Must be < 150 | Inspections | Photograph the equipment nameplate to capture the cooling capacity (tons or Btu/hr) | The Cooling Capacity on the nameplate, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to tons use the following formula: Cooling Capacity (Btu/hr) / 3,413 (Btu/ton) = Cooling Capacity (tons) | QA Checklist | Use the submitted invoice or installation report to validate the cooling capacity (btu/hr or tons) | The Cooling Capacity on the specification sheet, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) |  | 2022-02-10 | Kenny Liljestrom |  |  | 23
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | B | Any | Any |  | EECP | 45 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | Capacity (Tons) | Cooling Capacity (tons) | Numeric Value |  |  |  |  | General | 0 | 149 | 0 | Must be < 150 | Inspections | Photograph the equipment nameplate to capture the cooling capacity (tons or Btu/hr) | The Cooling Capacity on the nameplate, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to tons use the following formula: Cooling Capacity (Btu/hr) / 3,413 (Btu/ton) = Cooling Capacity (tons) | QA Checklist | Use the submitted invoice or installation report to validate the cooling capacity (btu/hr or tons) | The Cooling Capacity on the specification sheet, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) |  | 2022-02-10 | Kenny Liljestrom |  |  | 23
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | C | Any | Any |  | EECP | 45 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | Capacity (Tons) | Cooling Capacity (tons) | Numeric Value |  |  |  |  | General | 150 |  | 0 | Must be >= 150 | Inspections | Photograph the equipment nameplate to capture the cooling capacity (tons or Btu/hr) | The Cooling Capacity on the nameplate, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to tons use the following formula: Cooling Capacity (Btu/hr) / 3,413 (Btu/ton) = Cooling Capacity (tons) | QA Checklist | Use the submitted invoice or installation report to validate the cooling capacity (btu/hr or tons) | The Cooling Capacity on the specification sheet, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) |  | 2022-02-10 | Kenny Liljestrom |  |  | 23
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | D | Any | Any |  | EECP | 45 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | Capacity (Tons) | Cooling Capacity (tons) | Numeric Value |  |  |  |  | General | 150 |  | 0 | Must be >= 150 | Inspections | Photograph the equipment nameplate to capture the cooling capacity (tons or Btu/hr) | The Cooling Capacity on the nameplate, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to tons use the following formula: Cooling Capacity (Btu/hr) / 3,413 (Btu/ton) = Cooling Capacity (tons) | QA Checklist | Use the submitted invoice or installation report to validate the cooling capacity (btu/hr or tons) | The Cooling Capacity on the specification sheet, usually listed in Btu/hr or tons, can be calculated to match what is listed in EECP; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Cooling Capacity (kBtu/hr) to convert from tons: Cooling Capacity (tons) * 3.413 (kBtu/ton) = Cooling Capacity (kBtu/hr) |  | 2022-02-10 | Kenny Liljestrom |  |  | 23
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | A | Any | Any |  | EECP | 50 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | EER | EER | Numeric Value |  |  |  |  | General | 10.4 |  | 1 | Must be >= 10.4 | Inspections | Photograph the equipment nameplate to capture the EER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the EER | The EER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 3
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | A | Any | Any |  | EECP | 55 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | IPLV | Integrated Part Load Value (IPLV) | Numeric Value |  |  |  |  | General | 17.7 |  | 1 | Must be >= 17.7 | Inspections | Photograph the equipment nameplate to capture the Integrated Part Load Value (IPLV) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IPLV on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Integrated Part Load Value (IPLV) | The IPLV listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 33
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | B | Any | Any |  | EECP | 50 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | EER | EER | Numeric Value |  |  |  |  | General | 10.4 |  | 1 | Must be >= 10.4 | Inspections | Photograph the equipment nameplate to capture the EER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the EER | The EER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 3
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | B | Any | Any |  | EECP | 55 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | IPLV | Integrated Part Load Value (IPLV) | Numeric Value |  |  |  |  | General | 19 |  | 1 | Must be >= 19.0 | Inspections | Photograph the equipment nameplate to capture the Integrated Part Load Value (IPLV) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IPLV on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Integrated Part Load Value (IPLV) | The IPLV listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 33
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | C | Any | Any |  | EECP | 50 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | EER | EER | Numeric Value |  |  |  |  | General | 10.4 |  | 1 | Must be >= 10.4 | Inspections | Photograph the equipment nameplate to capture the EER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the EER | The EER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 3
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | C | Any | Any |  | EECP | 55 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | IPLV | Integrated Part Load Value (IPLV) | Numeric Value |  |  |  |  | General | 18 |  | 1 | Must be >= 18.0 | Inspections | Photograph the equipment nameplate to capture the Integrated Part Load Value (IPLV) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IPLV on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Integrated Part Load Value (IPLV) | The IPLV listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 33
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | D | Any | Any |  | EECP | 50 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | EER | EER | Numeric Value |  |  |  |  | General | 10.4 |  | 1 | Must be >= 10.4 | Inspections | Photograph the equipment nameplate to capture the EER | If the value cannot be located on the nameplate, this data can be verified by the processing team; the EER on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the EER | The EER listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 3
0 | SWHC052 | 2 | Air-Cooled Chiller, Path B | D | Any | Any |  | EECP | 55 | Products are required to meet both full load and integrated part load efficiency requirements specified in the Measure Offering Description. | Yes | IPLV | Integrated Part Load Value (IPLV) | Numeric Value |  |  |  |  | General | 19.3 |  | 1 | Must be >= 19.3 | Inspections | Photograph the equipment nameplate to capture the Integrated Part Load Value (IPLV) | If the value cannot be located on the nameplate, this data can be verified by the processing team; the IPLV on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted installation report or specification sheet to validate the Integrated Part Load Value (IPLV) | The IPLV listed in EECP should match what is listed in installation report or specification sheet |  | 2022-02-10 | Kenny Liljestrom |  |  | 33
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph of the lamp nameplate showing manufacturer | Manufacturer on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-14 | Kenny Liljestrom |  | Add | 12
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | EECP | 2 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph of the lamp nameplate showing model number | Model number on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-14 | Kenny Liljestrom |  | Add | 12
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | EECP | 3 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Existing ballast manufacturer | Existing ballast manufacturer | Text Box | [9 empty] | Inspections | Photograph of the lighting fixture ballast showing the manufacturer and model number; if possible, look for any manufacturing dates on the ballast | Manufacturer on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-14 | Kenny Liljestrom |  | Add | 29
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | EECP | 4 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Existing ballast model number | Existing ballast model number | Text Box | [9 empty] | Inspections | Photograph of the lighting fixture ballast showing the manufacturer and model number | Model number on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-14 | Kenny Liljestrom |  | Add | 29
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | EECP | 5 | Due to testing considerations, only a product that can operate from an electronic instant start ballast is eligible. Re-ballast is not eligible. Replacement lamps designed to operate off of existing magnetic ballasts or off of other types of electronic ballasts are not eligible. | Yes |  | Is the ballast existing and an electronic instant start type? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the Ballast make and model listed in EECP to locate a manufacturer specification sheet; or use the inspection photos from the ballast nameplate to determine the Start Type and if possible, look for any manufacturing dates on the ballast | The ballast should NOT be brand new and have a start type listed as Instant Start on the ballast nameplate or manufacturer spec sheet | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 61
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | EECP | 6 | Title-24 Code Requirements for Lighting Alterations | Yes |  | Code Exemption for: Retrofitting < 10% in an enclosed space or <= 50 total per floor or tenant? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | Count the number of lighting fixtures retrofitted and the total number of fixtures | The total fixtures retrofitted should be less than 50 total or less than 10% of the total fixtures on the premise | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 95
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | AR | Any |  | QA Checklist | 7 | Even though POE is not explicitly required for approval by the California Public Utilities Commission (CPUC), all program administrators and third-party program implementers are required to collect data, as stated in the Date Collection Requirements section, that will satisfy POU requirements. R843 This technology is dependent upon the existing condition baseline, and the data collection requirements are intended to provide sufficient evidence of the disposal method and replacement of the existing products, including verification of the ballast and the compatibility. | Yes |  | Has all Preponderance of Evidence (POE) including existing system controls functionality with replacements, reasons for retrofitting to LED, and future plans without incentives been documented and submitted? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Review the Program Influence documents to ensure all POE requirements are met and adequate | Ensure the POE document includes existing system controls functionality with replacements, reasons for retrofitting to LED, and future plans without incentives | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 207
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | AR | Any |  | EECP | 8 | Good to have | No |  | Who was the party that filled out the POE documentation? | Drop Down List | Tenant;Owner;Owner Representative;Implementer; | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | Not configured in original upload | 2021-10-20 | Kenny Liljestrom | Implementers responsible for POE documentation | Add | 56
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | EECP | 9 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Total number of fixture on site | Pre-Existing Conditions: Total number of fixtures on site | Numeric Value | [9 empty] | Inspections | The total quantity of lamps can be counted In lieu of verifying this field | No need to update data in EECP since this is for Pre-Existing conditions | QA Checklist | An installation report which shows down the total fixtures on site | There are no pass or fail criteria for the property, this is a data collection requirement | Update property label to include "Existing Conditions:" | 2021-06-14 | Kenny Liljestrom |  | Add | 57
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | EECP | 10 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Number of fixtures sampled | Pre-Existing Conditions: Number of Fixtures Sampled | Numeric Value | [9 empty] | Inspections | The total quantity of lamps can be counted In lieu of verifying this field | No need to update data in EECP since this is for Pre-Existing conditions | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Update property label to include "Pre-Existing Conditions:" | 2021-06-14 | Kenny Liljestrom |  | Add | 51
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | EECP | 11 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Number of lamps per fixture | Pre-Existing Conditions: Number of Lamps per Fixture | Numeric Value | [9 empty] | Inspections | The total quantity of lamps can be counted In lieu of verifying this field | No need to update data in EECP since this is for Pre-Existing conditions | QA Checklist | Review the installation report which should shows how many lamps are in each lighting fixture | The value should match what is listed in EECP | Update property label to include "Pre-Existing Conditions:" | 2021-06-14 | Kenny Liljestrom |  | Add | 52
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | EECP | 12 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Number of ballasts per fixture | Pre-Existing Conditions: Number of Ballasts per Fixture | Numeric Value | [9 empty] | Inspections | The total quantity of lamps can be counted In lieu of verifying this field | No need to update data in EECP since this is for Pre-Existing conditions | QA Checklist | An installation report which shows how many ballasts are in each lighting fixture | The value should match what is listed in EECP | Update property label to include "Pre-Existing Conditions:" | 2021-06-14 | Kenny Liljestrom |  | Add | 55
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | EECP | 13 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Existing fluorescent lamp wattage | Pre-Existing Conditions: Fluorescent Lamp Wattage (W) | Numeric Value | [9 empty] | Inspections | Look for any existing fluorescent tubes on site, record or document the existing lamp wattage | The value should match what is listed in EECP | QA Checklist | Installation report should indicate what the existing and proposed lighting wattages are | The value should match what is listed in EECP | Update property label to include "Pre-Existing Conditions:" | 2021-06-14 | Kenny Liljestrom |  | Add | 53
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | EECP | 14 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes | Disposal method of tubes | Disposal method of tube | Drop Down List | Abandoned in Place;Removed and Disposed of Properly;Other; | [7 empty] | Must be 'Removed and Disposed of Properly' | QA Checklist | Contractor or implementer should provide records of the lamps being disposed of | There must be proof of lamp disposal in one of the submitted documents | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-14 | Kenny Liljestrom |  | Add | 23
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | EECP | 15 | De-lamping is not eligible. | Yes |  | Have the fixtures been delamped? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 32
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | QA Checklist | 16 | Mandatory data collection requirements are: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Number of ballasts per fixture • Ballast model number • Ballast manufacturer • Fluorescent lamp wattage • Disposal method of tube • Manufacturer cut sheet showing ballast compatibility | Yes |  | Has the manufacturer cut sheet been submitted? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | Check the submitted documents in EECP for a manufacturer specification sheet | Ensure the manufacturer specification sheet was submitted to EECP | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 46
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | QA Checklist | 17 | The lamp must be listed under the Primary Use Category “Replacement Lamps (“plug and play”) (UL Type A)” or “Dual Mode Internal Driver (UL Type A and Type B)” on the current Design Lights Consortium qualified product list (https://www.designlights.org/search/). | Yes |  | Is the lamp listed on the most recent version of the DesignLights Consortium (DLC) list? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | On the DLC website, use the make and model of the lighting to see if the equipment exists in the database | The make and model from EECP should be present on the DLC database | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 88
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | QA Checklist | 18 | LED tube must be 4-foot and designated as UL Type A or UL Type A+B, but must be configured as a UL Type A. | Yes |  | 4-ft LED Tube Type | Drop Down List | UL Type A;UL Type B;UL Type C;ULType A + B; | [7 empty] | Must be 'UL Type A' or 'UL Type A + B' | QA Checklist | Use the DLC list using the make and model to check the "lamp designation" | The lamp must be listed as being UL Type A or UL Type A + B | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 18
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | QA Checklist | 19 | The lamp must be listed under the Primary Use Category “Replacement Lamps (“plug and play”) (UL Type A)” or “Dual Mode Internal Driver (UL Type A and Type B)” on the current Design Lights Consortium qualified product list (https://www.designlights.org/search/). | Yes |  | Primary Use Category | Drop Down List | Replacement Lamps (“plug and play”) (UL Type A);Dual Mode Internal Driver (UL Type A and Type B);Other; | [7 empty] | Must not be 'Other' | QA Checklist | Use the DLC list using the make and model to check the "Primary Use Category" | The Primary Use Category must be listed as Replacement Lamps (“plug and play”) (UL Type A); Dual Mode Internal Driver (UL Type A and Type B) | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 20
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | QA Checklist | 20 | TLEDs must be on the current DLC qualified products list and have a listed efficacy of 145 LPW or higher. | Yes |  | System Efficacy, Lumens/Watt (LPW) listed on DLC | Numeric Value | [8 empty] | Must be >= 145 | QA Checklist | Use the DLC list using the make and model to check the listed "efficacy" | The listed efficacy must be greater than or equal to 145 | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 48
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | QA Checklist | 21 | Program Requirements for LED T8 Lamps Table | Yes |  | CRI | Numeric Value | [8 empty] | Must be >= 80 | QA Checklist | Use the DLC list using the make and model to check the "CRI" | The CRI must be greater than or equal to 80 | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 3
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | QA Checklist | 22 | Program Requirements for LED T8 Lamps Table | Yes |  | Kelvin Correlated Color Temperature (CCT) | Numeric Value | [8 empty] | Must be >= 2200 and <= 6500 | QA Checklist | Use the DLC list using the make and model to check the "CCT" | Ensure the CCT is between 2200 and 6500 | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 41
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | QA Checklist | 23 | Program Requirements for LED T8 Lamps Table | Yes |  | Power Factor | Numeric Value | [8 empty] | Must be >= 0.90 | QA Checklist | Check the DLC list to ensure the Power Factor is greater than or equal to 0.90 | Check the DLC list to ensure the Power Factor is greater than or equal to 0.90 | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 12
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | QA Checklist | 24 | Program Requirements for LED T8 Lamps Table | Yes |  | Total Harmonic Distortion | Numeric Value | [8 empty] | Must be <= 20% | QA Checklist | Use the DLC list using the make and model to check the "Total Harmonic Distortion" | The Total Harmonic Distortion must be less than or equal to 20% | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 25
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | QA Checklist | 25 | Program Requirements for LED T8 Lamps Table | Yes |  | L70 Lumen Maintenance Hours | Numeric Value | [8 empty] | Must be >= 50000 | QA Checklist | All products listed on the DLC meet this requirement | No need to verify this requirement | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 27
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | QA Checklist | 26 | Program Requirements for LED T8 Lamps Table | Yes |  | Minimum Warranty | Drop Down List | >= 5 Years;< 5 Years; | [7 empty] | Must be >= 5 Years | QA Checklist | All products listed on the DLC meet this requirement | No need to verify this requirement | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 16
1 | SWLG009 | 2 | LED Tube, UL Type A | Any | Any | Any |  | QA Checklist | 27 | The LED T8 Lamp specification sheet must list all of the compatible ballast model numbers to ensure proper operation of the measure. | Yes |  | Does the submitted lamp specification sheet list the installed ballast model number showing it to be compatible with the installed lamp? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the existing ballast make and model listed in EECP and cross check the lamp manufacturer specification sheet | The existing ballast listed by the implementer should be listed on the specification sheet showing compatibility | - | - | - |  | 2021-06-14 | Kenny Liljestrom | Listed on the BES Invoice Checklist | Add | 136
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-08 | Kenny Liljestrom |  | Add | 12
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-08 | Kenny Liljestrom |  | Add | 5
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any |  | EECP | 3 | The measure must replace a lumen equivalent lamp/fixture of higher wattage. (See Measure Case Description). | Yes | Watts | Wattage | Numeric Value | [9 empty] | QA Checklist | Installation report should indicate what the proposed lighting wattages are | The value should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-08 | Kenny Liljestrom |  | Add | 7
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any |  | EECP | 4 | The measure must replace a lumen equivalent lamp/fixture of higher wattage. (See Measure Case Description). | Yes | Replace Higher Wattage | Does this fixture/retrofit kit replace a lumen equivalent lamp/fixture of higher wattage? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | Installation report should indicate what the existing and proposed fixtures wattages are | The existing wattage should be greater than or equal to the proposed wattage | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-08 | Kenny Liljestrom |  | Add | 89
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any |  | QA Checklist | 5 | The measure must be on the DesignLights Consortium (DLC) qualified product list (QPL) (https://www.designlights.org/search/). The product efficacy must meet or exceed the specified “measure case” efficacy based on the “rated” or “measured” efficacy in the DLC database. This requirement is to ensure the efficacy reported by the manufacturer has been confirmed by a third-party entity. | Yes |  | Replacement fixture/retrofit kit on the most recent version of the DLC qualified product list? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | On the DLC website, use the make and model of the lighting to see if the equipment exists in the database | The make and model from EECP should be present on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 94
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any |  | QA Checklist | 6 | Only premium fixtures will qualify for the measure case descriptions | Yes |  | Fixture/retrofit kit listing in the Technical Requirements table (V5) on DLC under Classification | Drop Down List | Standard;Premium;Other | [7 empty] | Must be Premium | QA Checklist | Use the DLC list using the make and model to check the "Classification" | The fixture must be listed as being Premium | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 97
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any |  | QA Checklist | 7 | The LED fixture or retrofit kit must be listed in the Technical Requirements table (V5) by the DLC under the General Category “High Bay” and under the Primary Use Designations as follows: R1300 • High-Bay Aisle Luminaires • High-Bay Luminaires for Commercial and Industrial Buildings • Low-Bay Luminaires for Commercial and Industrial Buildings • Retrofit Kits for High-Bay Luminaires for Commercial and Industrial Buildings • Retrofit Kits for Low-Bay Luminaires for Commercial and Industrial Buildings | Yes |  | Fixture/retrofit kit listing in the Technical Requirements table (V5) on DLC under Primary Use Designations? | Drop Down List | High-Bay Aisle Luminaires;High-Bay Luminaires for Commercial and Industrial Buildings;Low-Bay Luminaires for Commercial and Industrial Buildings;Retrofit Kits for High-Bay Luminaires for Commercial and Industrial Buildings;Retrofit Kits for Low-Bay Luminaires for Commercial and Industrial Buildings;Other; | [7 empty] | Must not be 'Other' | QA Checklist | Use the DLC list using the make and model to check the "Primary Use Designation" | The fixture must be listed as being one of the following options: High-Bay Aisle Luminaires; High-Bay Luminaires for Commercial and Industrial Buildings; Low-Bay Luminaires for Commercial and Industrial Buildings; Retrofit Kits for High-Bay Luminaires for Commercial and Industrial Buildings; Retrofit Kits for Low-Bay Luminaires for Commercial and Industrial Buildings; | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 108
0 | SWLG011 | 3 | LED, High or Low Bay | A | Any | Any |  | QA Checklist | 8 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 4500 and < 5400 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 4500 and < 5400 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | A | Any | Any |  | QA Checklist | 9 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 130 and < 150 | EECP | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | B | Any | Any |  | QA Checklist | 10 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 5400 and < 6500 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 5400 and < 6500 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | B | Any | Any |  | QA Checklist | 11 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | C | Any | Any |  | QA Checklist | 12 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 6500 and < 7800 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 6500 and < 7800 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | C | Any | Any |  | QA Checklist | 13 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | D | Any | Any |  | QA Checklist | 14 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 7800 and < 9400 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 7800 and < 9400 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | D | Any | Any |  | QA Checklist | 15 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | E | Any | Any |  | QA Checklist | 16 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 9400 and < 11800 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 9400 and < 11800 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | E | Any | Any |  | QA Checklist | 17 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | F | Any | Any |  | QA Checklist | 18 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 11800 and < 14800 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 11800 and < 14800 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | F | Any | Any |  | QA Checklist | 19 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | G | Any | Any |  | QA Checklist | 20 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 14800 and < 18500 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 14800 and < 18500 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | G | Any | Any |  | QA Checklist | 21 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | H | Any | Any |  | QA Checklist | 22 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 18500 and < 23100 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 18500 and < 23100 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | H | Any | Any |  | QA Checklist | 23 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | I | Any | Any |  | QA Checklist | 24 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 23100 and < 30000 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 23100 and < 30000 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | I | Any | Any |  | QA Checklist | 25 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | J | Any | Any |  | QA Checklist | 26 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 30000 and < 39000 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 30000 and < 39000 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | J | Any | Any |  | QA Checklist | 27 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | K | Any | Any |  | QA Checklist | 28 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 39000 and < 50700 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 39000 and < 50700 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | K | Any | Any |  | QA Checklist | 29 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | L | Any | Any |  | QA Checklist | 30 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 50700 and < 65900 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 50700 and < 65900 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | L | Any | Any |  | QA Checklist | 31 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | M | Any | Any |  | QA Checklist | 32 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 4500 and < 5400 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 4500 and < 5400 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | M | Any | Any |  | QA Checklist | 33 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | N | Any | Any |  | QA Checklist | 34 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 5400 and < 6500 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 5400 and < 6500 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | N | Any | Any |  | QA Checklist | 35 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 130 and < 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 130 and < 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | O | Any | Any |  | QA Checklist | 36 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 6500 and < 7800 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 6500 and < 7800 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | O | Any | Any |  | QA Checklist | 37 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | P | Any | Any |  | QA Checklist | 38 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 7800 and < 9400 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 7800 and < 9400 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | P | Any | Any |  | QA Checklist | 39 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | Q | Any | Any |  | QA Checklist | 40 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 9400 and < 11800 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 9400 and < 11800 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | Q | Any | Any |  | QA Checklist | 41 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | R | Any | Any |  | QA Checklist | 42 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 11800 and < 14800 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 11800 and < 14800 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | R | Any | Any |  | QA Checklist | 43 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | S | Any | Any |  | QA Checklist | 44 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 14800 and < 18500 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 14800 and < 18500 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | S | Any | Any |  | QA Checklist | 45 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | T | Any | Any |  | QA Checklist | 46 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 18500 and < 23100 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 18500 and < 23100 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | T | Any | Any |  | QA Checklist | 47 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | U | Any | Any |  | QA Checklist | 48 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 23100 and < 30000 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 23100 and < 30000 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | U | Any | Any |  | QA Checklist | 49 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | V | Any | Any |  | QA Checklist | 50 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 30000 and < 39000 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 30000 and < 39000 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | V | Any | Any |  | QA Checklist | 51 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | W | Any | Any |  | QA Checklist | 52 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 39000 and < 50700 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 39000 and < 50700 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | W | Any | Any |  | QA Checklist | 53 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | X | Any | Any |  | QA Checklist | 54 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Lumens | Numeric Value | [8 empty] | must be >= 50700 and < 65900 | QA Checklist | Use the DLC list using the make and model to check the 'Lumens' | The fixture lumens must be >= 50700 and < 65900 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 6
0 | SWLG011 | 3 | LED, High or Low Bay | X | Any | Any |  | QA Checklist | 55 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Efficacy, Lumens/Watt (LPW) | Formula | =Lumens / Wattage | [7 empty] | must be >= 150 | QA Checklist | Use the DLC list using the make and model to check the 'Efficacy, Lumens/Watt (LPW)' | The fixture efficacy must be >= 150 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any |  | QA Checklist | 56 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | Kelvin Correlated Color Temperature (CCT) | Numeric Value | [8 empty] | Must be <= 5700 | QA Checklist | Use the DLC list using the make and model to check the 'CCT' | The fixture CCT must be <= 5700 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 41
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any |  | QA Checklist | 57 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | What is the fixture Color Rendering Index (CRI)? | Numeric Value | [8 empty] | Must be >= 70 | QA Checklist | Use the DLC list using the make and model to check the 'CRI' | The fixture CCT must be >= 70 on the DLC database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 48
0 | SWLG011 | 3 | LED, High or Low Bay | Any | Any | Any |  | QA Checklist | 58 | DLC Standard requirements for the high-bay and low-bay categories include: • 50,000-hour L70 Lumen Maintenance • ≥ 70 Color Rendering Index (CRI) • ≥ 115 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 120 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) • ≤ 5700 Kelvin Correlated Color Temperature (CCT) • ≥ 5,000 lumen light output (10% tolerance) • ≥ 30% of lumen Output in the 20° - 50° zone (higher for Aisle Lighting) Additional Requirements for DLC Premium above the Standard level for the high-bay and low-bay categories include: • 36,000-hour L90 Lumen Maintenance • ≥ 130 lumens/watt (LPW) for low-bay (5,000 – 10,000 lumens) • ≥ 135 lumens/watt (LPW) for high-bay (≥ 10,000 lumens) | Yes |  | L90 Lumen Maintenance Hours | Numeric Value | [8 empty] | Must be >= 36,000 | QA Checklist | All products listed on the DLC meet this requirement | No validation criteria | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-08 | Kenny Liljestrom |  | Add | 27
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph of the lamp nameplate showing manufacturer | Manufacturer on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-08 | Kenny Liljestrom |  | Add | 12
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph of the lamp nameplate showing model number | Model number on the nameplate should match what is listed in EECP | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-08 | Kenny Liljestrom |  | Add | 5
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | EECP | 5 | To ensure that code requirements for lighting power and controls are being met, the following data submission requirements must be met for all delivery types and measure application types. •Documentation showing that the retrofitted space has achieved a lighting power density that is < 80% of allowable Title 24 LPD for that space type. •Title 24 compliance documentation verifying the existence of required automated shut-off controls compliant with 2019 Title 24 §130.1(c)1-8 Auto-Shut-off Control. •Only for AR measures, the customer must confirm that existing automated control functionality remains intact after installation. (See Preponderance of Evidence Requirements below.) | Yes | Code Exemptions | Does this project meet one of the Code Exemptions: Retrofitting < 10% of luminaires in an enclosed space or retrofitting <= 50 total luminaires per floor or tenant space? | Drop Down List | Yes;No; |  | Equal | Yes |  |  |  |  | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-07-08 | Kenny Liljestrom |  | Add | 170
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | AR | Any |  | EECP | 6 | All program administrators and third-party program implementers are required to collect data as stated in the Date Collection Requirements section that will satisfy POE requirements. The data collection requirements are intended to provide establish programmatic evidence and include questions about existing system functionality, reasons for retrofitting to LED, and potential future plans without provided incentives. | Yes | POE Docs Submitted | Has all Preponderance of Evidence (POE) including existing system controls functionality with replacements, reasons for retrofitting to LED, and future plans without incentives been documented and submitted? | Drop Down List | Yes;No; |  | Equal | Yes |  |  |  |  | Must be 'Yes' | QA Checklist | Review the Program Influence documents to ensure all POE requirements are met and adequate | All program administrators and third-party program implementers are required to collect data as stated in the Date Collection Requirements section that will satisfy POE requirements. The data collection requirements are intended to provide establish programmatic evidence and include questions about existing system functionality, reasons for retrofitting to LED, and potential future plans without provided incentives. | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 7/30/20210 | Kenny Liljestrom |  | Add | 207
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | AR | Any |  | EECP | 7 | Good to have | No | POE Contact | Who was the party that filled out the POE documentation? | Drop Down List | Tenant;Owner;Owner Representative;Implementer; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-10-20 | Kenny Liljestrom | Implementers responsible for POE documentation | Add | 56
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | EECP | 8 | Existing lamps and ballasts must be fully demolished and properly disposed. “Abandon-in-place” demolition of existing ballasts is not eligible. | Yes | Disposal Method Tube | Disposal method of tube | Drop Down List | Abandoned in Place;Removed_Disposed of Properly;Other; |  | Equal | Removed_Disposed of Properly |  |  |  |  | Must be 'Removed and Disposed of Properly' | QA Checklist | The implementer should provide documentation or proof of the lamp disposal method | The lamps must be properly disposed of, not abandoned in place | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2021-07-08 | Kenny Liljestrom |  | Add | 23
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | EECP | 9 | The LED tube must be 4-foot and designated as UL Type B, UL Type A+B, or UL Type C. UL Type A+B (dual mode) lamps must be installed in a Type B configuration with the existing ballast removed. | Yes | UL Type Config | If UL Type A + B Configuration, was the existing ballast removed? | Drop Down List | Yes;No;N/A; |  | Not Equal | No |  |  |  |  | Conditional Field If LED Tube Type is 'UL Type A + B', answer must be Yes | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-07-08 | Kenny Liljestrom |  | Add | 65
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | EECP | 10 | The LED tube must be compatible with the installed system lighting controls. For example, if the lighting system includes dimming controls, the new LED tube must be dimmable and compatible with the installed dimming system. | Yes | Compatible with existing controls | Is the new lighting compatible with the existing lighting controls type (i.e. dimming controls with dimmable LED)? | Drop Down List | Yes;No; |  | Equal | Yes |  |  |  |  | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-07-08 | Kenny Liljestrom |  | Add | 114
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | EECP | 11 | De-lamping is not eligible. | Yes | Fixtures Delamped | Have the fixtures been delamped? | Drop Down List | Yes;No; |  | Equal | No |  |  |  |  | Must be 'No' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2021-07-08 | Kenny Liljestrom |  | Add | 32
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | AR | Any |  | EECP | 12 | The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Total number of fixtures on site | Pre-Existing Conditions: Total number of fixtures on site | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | The total quantity of lamps can be counted In lieu of verifying this field | No need to update data in EECP since this is for Pre-Existing conditions | QA Checklist | An installation report which shows down the total fixtures on site | There are no pass or fail criteria for the property, this is a data collection requirement | Update property label to include "Pre-Existing Conditions:" | 2021-07-08 | Kenny Liljestrom |  | Add | 57
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | AR | Any |  | EECP | 13 | The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Number of fixtures sampled | Pre-Existing Conditions: Number of Fixtures Sampled | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | The total quantity of lamps can be counted In lieu of verifying this field | No need to update data in EECP since this is for Pre-Existing conditions | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | Update property label to include "Pre-Existing Conditions:" | 2021-07-08 | Kenny Liljestrom |  | Add | 51
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | AR | Any |  | EECP | 14 | The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Percent Sampled | Pre-Existing Conditions: Percent of Fixtures Sampled | Formula |  |  |  |  | Percentage | 10 | 100 |  | Must be >= 10% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | Update property label to include "Pre-Existing Conditions:" | 2021-07-08 | Kenny Liljestrom |  | Add | 52
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | AR | Any |  | EECP | 15 | The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Number of lamps per fixture | Pre-Existing Conditions: Number of Lamps per Fixture | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | The total quantity of lamps can be counted In lieu of verifying this field | No need to update data in EECP since this is for Pre-Existing conditions | QA Checklist | Review the installation report which should shows how many lamps are in each lighting fixture | The value should match what is listed in EECP | Update property label to include "Pre-Existing Conditions:" | 2021-07-08 | Kenny Liljestrom |  | Add | 52
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | AR | Any |  | EECP | 16 | The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Existing Watts | Pre-Existing Conditions: Fluorescent Lamp Wattage (W) | Numeric Value |  |  |  |  | General |  |  | 2 |  | Inspections | Look for any existing fluorescent tubes on site, record or document the existing lamp wattage | The value should match what is listed in EECP | QA Checklist | Installation report should indicate what the existing and proposed lighting wattages are | The value should match what is listed in EECP | Update property label to include "Pre-Existing Conditions:" | 2021-07-08 | Kenny Liljestrom |  | Add | 53
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | AR | Any |  | EECP | 17 | The following data collection requirements must be met for accelerated replacement measures: The customer must submit responses to the POE questionnaire document associated with these measures. Pre-existing data that must be collected includes: • Total number of fixtures on site • Number of fixtures sampled (must sample at least 10% of the total number of fixtures on site) • Number of lamps per fixture • Fluorescent lamp wattage • Disposal method of tube • Existing automated controls types in the spaces retrofitted | Yes | Auto Control Types | Pre-Existing Conditions: Automated controls type in retrofitted spaces | Drop Down List | Occupancy;Building Automation System (BAS);Time Clock;Other;None; |  | Not Equal | None |  |  |  |  | Must not be 'No Automated Controls' | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - | Update property label to include "Pre-Existing Conditions:" | 2021-07-30 | Kenny Liljestrom | Property updated to add additional drop-down item on 7/30/21 and update the validation criteria to make the property more clear | Add | 70
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | QA Checklist | 18 | Program Requirements for LED T8 Lamps Table | Yes |  | Is the lamp listed on the most recent version of the DesignLights Consortium (DLC) list? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | On the DLC website, use the make and model of the lighting to see if the equipment exists in the database | The make and model from EECP should be present on the DLC database | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 88
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | QA Checklist | 19 | The LED tube must be 4-foot and designated as UL Type B, UL Type A+B, or UL Type C. UL Type A+B (dual mode) lamps must be installed in a Type B configuration with the existing ballast removed. | Yes |  | LED Tube Type | Drop Down List | UL Type A;UL Type B;UL Type C;ULType A + B; | [7 empty] | Must be 'UL Type B', 'UL Type C' or 'UL Type A + B' | QA Checklist | Use the DLC list using the make and model to check the "lamp designation" | The lamp must be listed as being UL Type B, UL Type A + B, or UL Type C | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 13
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | QA Checklist | 20 | The lamp must be listed under the Primary Use Category “Internal Driver/Line Voltage (UL Type B) Lamps”, “Dual Mode Internal Driver (UL Type A and Type B)”, “2-Lamp External Driver (UL Type C) Lamps”, “3-Lamp External Driver (UL Type C) Lamps”, “4-Lamp External Driver (UL Type C) Lamps” on the current Design Lights Consortium qualified product list (https://www.designlights.org/search/). | Yes |  | Primary Use Category | Drop Down List | Internal Driver/Line Voltage (UL Type B) Lamps;Dual Mode Internal Driver (UL Type A and Type B);2-Lamp External Driver (UL Type C) Lamps;3-Lamp External Driver (UL Type C) Lamps;4-Lamp External Driver (UL Type C) Lamps;Other; | [7 empty] | Must not be 'Other' | QA Checklist | Use the DLC list using the make and model to check the "Primary Use Category" | The Primary Use Category must be listed as Internal Driver/Line Voltage (UL Type B) Lamps, Dual Mode Internal Driver (UL Type A and Type B), 2-Lamp External Driver (UL Type C) Lamps, 3-Lamp External Driver (UL Type C) Lamps, or 4-Lamp External Driver (UL Type C) Lamps. | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 20
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | QA Checklist | 21 | Must meet a minimum efficacy requirement stated in the Measure Case Description. | Yes |  | System Efficacy, Lumens/Watt (LPW) as listed on DLC | Numeric Value | [8 empty] | Must be >= 160 | QA Checklist | Use the DLC list using the make and model to check the listed "efficacy" | The listed efficacy must be greater than or equal to 160 | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 51
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | QA Checklist | 22 | Program Requirements for LED T8 Lamps Table | Yes |  | CRI | Numeric Value | [8 empty] | Must be >= 80 | QA Checklist | Use the DLC list using the make and model to check the "CRI" | The CRI must be greater than or equal to 80 | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 3
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | QA Checklist | 23 | Program Requirements for LED T8 Lamps Table | Yes |  | Kelvin Correlated Color Temperature (CCT) | Numeric Value | [8 empty] | Must be >= 2200 and <= 6500 | QA Checklist | Use the DLC list using the make and model to check the "CCT" | Ensure the CCT is between 2200 and 6500 | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 41
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | QA Checklist | 24 | Program Requirements for LED T8 Lamps Table | Yes |  | Power Factor | Numeric Value | [8 empty] | Must be >= 0.90 | QA Checklist | Check the DLC list to ensure the Power Factor is greater than or equal to 0.90 | Check the DLC list to ensure the Power Factor is greater than or equal to 0.90 | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 12
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | QA Checklist | 25 | Program Requirements for LED T8 Lamps Table | Yes |  | Total Harmonic Distortion | Numeric Value | [8 empty] | Must be <= 20% | QA Checklist | Use the DLC list using the make and model to check the "Total Harmonic Distortion" | The Total Harmonic Distortion must be less than or equal to 20% | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 25
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | QA Checklist | 26 | Program Requirements for LED T8 Lamps Table | Yes |  | L70 Lumen Maintenance Hours | Numeric Value | [8 empty] | Must be >= 50000 | QA Checklist | All products listed on the DLC meet this requirement | No need to verify this requirement | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 27
1 | SWLG018 | 1 | LED Tube, UL Type B and Type C | Any | Any | Any |  | QA Checklist | 27 | Program Requirements for LED T8 Lamps Table | Yes |  | Minimum Warranty | Drop Down List | >= 5 Years;< 5 Years; | [7 empty] | Must be >= 5 Years | QA Checklist | All products listed on the DLC meet this requirement | No need to verify this requirement | - | - | - | Not configured in EECP | 2021-07-08 | Kenny Liljestrom |  | Add | 16
0 | SWPR001 | 1 | Ventilation Fan, Agriculture | Any | Any | Any |  | EECP | 1 | - | Pending | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the ventilation fan nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-21 | Kenny Liljestrom |  |  | 12
0 | SWPR001 | 1 | Ventilation Fan, Agriculture | Any | Any | Any |  | EECP | 2 | - | Pending | Model | Model | Text Box | [9 empty] | Inspections | Photograph the ventilation fan nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-21 | Kenny Liljestrom |  |  | 5
0 | SWPR001 | 1 | Ventilation Fan, Agriculture | Any | Any | Any |  | EECP | 3 | The measure is applicable for all existing agriculture facilities of any vintage. | Pending |  | Building type is existing Agricultural facility (any vintage)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | Observe the building type | The building type must be an existing agricultural facility | QA Checklist | Use the submitted installation report to determine the building type | The building type must be an existing agricultural facility | Property may be able to be configured at the enrollment level; if applicable, please configure at enrollment instead of measure level | 2021-09-21 | Kenny Liljestrom |  |  | 62
0 | SWPR001 | 1 | Ventilation Fan, Agriculture | A | Any | Any |  | EECP | 4 | A fan must have been tested by the Bioenvironmental and Structural Systems Laboratory (BESS Lab) ventilation fan testing facility at the University of Illinois to the specifications provided in the Base Case Description, and it must meet the minimum allowable cfm/W. (This value is a tradeoff between trying to encourage the highest practical efficiencies and still allowing most manufacturers to have at least one offering within the accepted range.) | Pending |  | Fan cfm/watt | Numeric Value | [8 empty] | Must be >= 14.0 | QA Checklist | Use the submitted manufacturer spec sheet (or make and model) to determine the fan efficiency (cfm/watt) | The fan efficiency should be >= 14 cfm/watt. This calculation can be completed by taking the flow rate (cfm) and dividing by the total input power (Watts) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 12
0 | SWPR001 | 1 | Ventilation Fan, Agriculture | B | Any | Any |  | EECP | 5 | A fan must have been tested by the Bioenvironmental and Structural Systems Laboratory (BESS Lab) ventilation fan testing facility at the University of Illinois to the specifications provided in the Base Case Description, and it must meet the minimum allowable cfm/W. (This value is a tradeoff between trying to encourage the highest practical efficiencies and still allowing most manufacturers to have at least one offering within the accepted range.) | Pending |  | Fan cfm/watt | Numeric Value | [8 empty] | Must be >= 20.4 | QA Checklist | Use the submitted manufacturer spec sheet (or make and model) to determine the fan efficiency (cfm/watt) | The fan efficiency should be >= 20.4 cfm/watt. This calculation can be completed by taking the flow rate (cfm) and dividing by the total input power (Watts) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 12
0 | SWPR001 | 1 | Ventilation Fan, Agriculture | C | Any | Any |  | EECP | 6 | A fan must have been tested by the Bioenvironmental and Structural Systems Laboratory (BESS Lab) ventilation fan testing facility at the University of Illinois to the specifications provided in the Base Case Description, and it must meet the minimum allowable cfm/W. (This value is a tradeoff between trying to encourage the highest practical efficiencies and still allowing most manufacturers to have at least one offering within the accepted range.) | Pending |  | Fan cfm/watt | Numeric Value | [8 empty] | Must be >= 21.9 | QA Checklist | Use the submitted manufacturer spec sheet (or make and model) to determine the fan efficiency (cfm/watt) | The fan efficiency should be >= 21.9 cfm/watt. This calculation can be completed by taking the flow rate (cfm) and dividing by the total input power (Watts) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 12
1 | SWPR002 | 1 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any |  | EECP | 1 | - | Pending | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the VFD Controls equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the VFD manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-17 | Kenny Liljestrom |  |  | 12
1 | SWPR002 | 1 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any |  | EECP | 2 | - | Pending | Model | Model | Text Box | [9 empty] | Inspections | Photograph the VFD Controls equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the VFD model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-17 | Kenny Liljestrom |  |  | 5
1 | SWPR002 | 1 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any |  | EECP | 3 | This measure is only applicable to the winery industry for process end-use applications. | Pending |  | Measure is installed for wine processing? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | Observe the building type | The building type must be a winery; or the pump must be serving a chilled wine loop | QA Checklist | Use the EEECP building type validation or installation report to determine the building type | The building type must be a winery; or the pump must be serving a chilled wine loop | This property can be configured at the enrollment level if Winery is a building type selection; if not, please configure at the measure level | 2021-09-17 | Kenny Liljestrom |  |  | 41
1 | SWPR002 | 1 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any |  | EECP | 4 | This measure involves the installation of a variable frequency drive (VFD) on an existing glycol pump motor. Chilled fluid, other than glycol, can be considered only if the unit energy savings (UES) is equal to or exceeds the UES of this measure. | Pending |  | Does the pump serve a glycol loop? | Drop Down List | Yes;No; | [8 empty] | QA Checklist | The installation report should indicate the type of loop the pump is serving | The pump can serve a glycol or non-glycol loop; if it is a non-glycol loop, the following property must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-17 | Kenny Liljestrom |  |  | 34
1 | SWPR002 | 1 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any |  | EECP | 5 | This measure involves the installation of a variable frequency drive (VFD) on an existing glycol pump motor. Chilled fluid, other than glycol, can be considered only if the unit energy savings (UES) is equal to or exceeds the UES of this measure. | Pending |  | If not a glycol loop, do the unit energy savings exceed the measure case savings? | Drop Down List | Yes;No;N/A; | [7 empty] | Must be 'Yes' or 'N/A' | QA Checklist | If the pump does not serve a glycol loop, the implementer/customer must provide proof the energy savings exceeds the savings from the workpaper; this may be present in the installation report or via a calculation file | The implementer/customer must provide proof the energy savings exceeds the savings from the workpaper | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-17 | Kenny Liljestrom |  |  | 81
1 | SWPR002 | 1 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any |  | EECP | 6 | Application of this measure is for the addition of a VFD on an existing glycol pump motor. The existing glycol pump(s) must operate at constant speed. | Pending |  | VFD installed on an existing constant speed pump motor? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | The implementer or customer should provide proof the existing pump motors are fixed/constant speed | Use the installation report or photographs to prove the motor is existing and operates at a constant speed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-17 | Kenny Liljestrom |  |  | 55
1 | SWPR002 | 1 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any |  | EECP | 7 | The VFD must have automated controls based on pressure feedback, fluid temperature feedback, and/or flow rate feedback. | Pending |  | VFD is automated by pressure, fluid temperature, or flow rate feedback? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the installation report to determine how the VFD will communicate with the pump motor | The VFD must operate based on feedback from the fluid pressure, temperature, or flow rate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-17 | Kenny Liljestrom |  |  | 71
1 | SWPR002 | 1 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any |  | EECP | 8 | The customer must provide documentation that the VFD is not installed on a back-up pump or redundant pump. | Pending |  | Documentation submitted showing VFD is not for backup pump? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the installation report to validate the VFD is not configured as a backup pump; the pump must be a primary | Implementer or customer should provide documentation showing the VFD is not acting as a backup pump | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-17 | Kenny Liljestrom |  |  | 59
0 | SWPR002 | 2 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the VFD Controls equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the VFD manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-23 | Kenny Liljestrom |  |  | 12
0 | SWPR002 | 2 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the VFD Controls equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the VFD model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-23 | Kenny Liljestrom |  |  | 5
0 | SWPR002 | 2 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any |  | EECP | 3 | This measure is only applicable to the winery industry for process end-use applications. | Yes |  | Measure is installed for wine processing? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | Observe the building type | The building type must be a winery; or the pump must be serving a chilled wine loop | QA Checklist | Use the EEECP building type validation or installation report to determine the building type | The building type must be a winery; or the pump must be serving a chilled wine loop | This property can be configured at the enrollment level if Winery is a building type selection; if not, please configure at the measure level | 2021-11-23 | Kenny Liljestrom |  |  | 41
0 | SWPR002 | 2 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any |  | EECP | 4 | This measure involves the installation of a variable frequency drive (VFD) on an existing glycol pump motor. Chilled fluid, other than glycol, can be considered only if the unit energy savings (UES) is equal to or exceeds the UES of this measure. | Yes |  | Does the pump serve a glycol loop? | Drop Down List | Yes;No; | [8 empty] | QA Checklist | The installation report should indicate the type of loop the pump is serving | The pump can serve a glycol or non-glycol loop; if it is a non-glycol loop, the following property must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 34
0 | SWPR002 | 2 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any |  | EECP | 5 | This measure involves the installation of a variable frequency drive (VFD) on an existing glycol pump motor. Chilled fluid, other than glycol, can be considered only if the unit energy savings (UES) is equal to or exceeds the UES of this measure. | Yes |  | If not a glycol loop, do the unit energy savings exceed the measure case savings? | Drop Down List | Yes;No;N/A; | [7 empty] | Must be 'Yes' or 'N/A' | QA Checklist | If the pump does not serve a glycol loop, the implementer/customer must provide proof the energy savings exceeds the savings from the workpaper; this may be present in the installation report or via a calculation file | The implementer/customer must provide proof the energy savings exceeds the savings from the workpaper | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 81
0 | SWPR002 | 2 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any |  | EECP | 6 | Application of this measure is for the addition of a VFD on an existing glycol pump motor. The existing glycol pump(s) must operate at constant speed. | Yes |  | VFD installed on an existing constant speed pump motor? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | The implementer or customer should provide proof the existing pump motors are fixed/constant speed | Use the installation report or photographs to prove the motor is existing and operates at a constant speed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 55
0 | SWPR002 | 2 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any |  | EECP | 7 | The VFD must have automated controls based on pressure feedback, fluid temperature feedback, and/or flow rate feedback. | Yes |  | VFD is automated by pressure, fluid temperature, or flow rate feedback? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the installation report to determine how the VFD will communicate with the pump motor | The VFD must operate based on feedback from the fluid pressure, temperature, or flow rate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 71
0 | SWPR002 | 2 | VFD for Glycol Pump Motor, Agriculture | Any | Any | Any |  | EECP | 8 | The customer must provide documentation that the VFD is not installed on a back-up pump or redundant pump. | Yes |  | Documentation submitted showing VFD is not for backup pump? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use the installation report to validate the VFD is not configured as a backup pump; the pump must be a primary | Implementer or customer should provide documentation showing the VFD is not acting as a backup pump | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 59
1 | SWPR004 | 1 | Circulating Block Heater | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-08 | Kenny Liljestrom |  | Add | 12
1 | SWPR004 | 1 | Circulating Block Heater | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-08 | Kenny Liljestrom |  | Add | 5
1 | SWPR004 | 1 | Circulating Block Heater | Any | NR | Any |  | EECP | 3 | For a normal replacement (NR) installation, the existing backup generator is eligible if it is not currently fitted with a circulating block heater or device utilizing similar electro-mechanical system to heat and circulate generator block pre-warming fluid. | Yes | Electro-Mechanical system | Before installation of the measure was the existing backup generator fitted with a circulating block heater or device utilizing similar electro-mechanical system to heat and circulate generator block pre-warming fluid? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Review the installation report to determine if the existing conditions are documented and whether or not the existing generator is fitted with a circulating block heater or electro-mechanical system to pre-warm the fluid | For a normal replacement (NR) installation, the existing backup generator is eligible if it is not currently fitted with a circulating block heater or device utilizing similar electro-mechanical system to heat and circulate generator block pre-warming fluid. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-08 | Kenny Liljestrom |  | Add | 218
1 | SWPR004 | 1 | Circulating Block Heater | Any | NC | Any |  | EECP | 4 | A new generator installation (i.e., new construction, NC), for which the base design prescribes a pre-heating device (e.g., thermosiphon heater) other than a circulating block heater or similar device is eligible to upgrade from base design to efficient design including a circulating block heater. | Yes |  | Does the base design prescribe a pre-heating device other than a circulating block heater? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Review the installation report to determine if the base design or code conditions are documented and whether or not the base design generator is fitted with a circulating block heater | A new generator installation (i.e., new construction, NC), for which the base design prescribes a pre-heating device (e.g., thermosiphon heater) other than a circulating block heater or similar device is eligible to upgrade from base design to efficient design including a circulating block heater. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-25 | Kenny Liljestrom |  | Add | 90
1 | SWPR004 | 1 | Circulating Block Heater | Any | Any | Any |  | EECP | 5 | Additional eligibility requirements regarding the installation include: • Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician). • Installer should follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. • Installation shall meet all applicable regulations including but not limited to latest NFPA Code 110 for Emergency Power Systems and NEC. | Yes | Qualified Tech | Was the installation of the circulating block heater performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician)? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-07-08 | Kenny Liljestrom |  | Add | 162
1 | SWPR004 | 1 | Circulating Block Heater | Any | Any | Any |  | EECP | 6 | Additional eligibility requirements regarding the installation include: • Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician). • Installer should follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. • Installation shall meet all applicable regulations including but not limited to latest NFPA Code 110 for Emergency Power Systems and NEC. | Yes | Installation Requirements | Did the Installer follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the circulating block heater to function at optimal energy efficiency? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-07-08 | Kenny Liljestrom |  | Add | 248
1 | SWPR004 | 1 | Circulating Block Heater | Any | Any | Any |  | EECP | 7 | Additional eligibility requirements regarding the installation include: • Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician). • Installer should follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. • Installation shall meet all applicable regulations including but not limited to latest NFPA Code 110 for Emergency Power Systems and NEC. | Yes |  | Installation meets latest NFPA Code 110 for Emergency Power Systems and NEC installation guidelines? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-08-25 | Kenny Liljestrom |  | Add | 100
1 | SWPR004 | 1 | Circulating Block Heater | Any | Any | Any |  | EECP | 8 | This measure is applicable to the following non-residential building types, of any vintage: Assembly; Manufacturing - Bio/Tech; Education - Community College; Manufacturing - Light Industrial; Education - Primary School; Office - Large; Education - Relocatable Classroom; Office - Small; Education - Secondary School; Restaurant - Fast-Food; Education - University; Restaurant - Sit-Down; Grocery; Retail - Multistory Large; Health/Medical - Hospital; Retail - Single-Story Large; Health/Medical - Nursing Home; Retail - Small; Lodging - Guest Rooms; Storage - Conditioned; Lodging - Hotel; Storage - Unconditioned; Lodging - Motel; Warehouse - Refrigerated | Yes |  | Building type | Drop Down List | Assembly;Manufacturing - Bio/ - Community College;Manufacturing - Light Industrial;Education - Primary School;Office - Large;Education - Relocatable Classroom;Office - Small;Education - Secondary School;Restaurant - Fast-Food;Education - University;Restaurant - Sit-Down;Grocery;Retail - Multistory Large;Health/Medical - Hospital;Retail - Single-Story Large;Health/Medical - Nursing Home;Retail - Small;Lodging - Guest Rooms;Storage - Conditioned;Lodging - Hotel;Storage - Unconditioned;Lodging - Motel;Warehouse - Refrigerated | [8 empty] | Inspections | While on site, observe and make note of the building type | The building type needs to be one of the following: Assembly, Manufacturing - Bio/Tech, Education - Community College, Manufacturing - Light Industrial, Education - Primary School, Office - Large, Education - Relocatable Classroom, Office - Small, Education - Secondary School, Restaurant - Fast-Food, Education - University, Restaurant - Sit-Down, Grocery, Retail - Multistory Large, Health/Medical - Hospital, Retail - Single-Story Large, Health/Medical - Nursing Home, Retail - Small, Lodging - Guest Rooms, Storage - Conditioned, Lodging - Hotel, Storage - Unconditioned, Lodging - Motel, Warehouse - Refrigerated | QA Checklist | Use the installation report or EECP to determine the building type | The building type needs to be one of the following: Assembly, Manufacturing - Bio/Tech, Education - Community College, Manufacturing - Light Industrial, Education - Primary School, Office - Large, Education - Relocatable Classroom, Office - Small, Education - Secondary School, Restaurant - Fast-Food, Education - University, Restaurant - Sit-Down, Grocery, Retail - Multistory Large, Health/Medical - Hospital, Retail - Single-Story Large, Health/Medical - Nursing Home, Retail - Small, Lodging - Guest Rooms, Storage - Conditioned, Lodging - Hotel, Storage - Unconditioned, Lodging - Motel, Warehouse - Refrigerated | Not configured in original upload | 2021-08-25 | Kenny Liljestrom |  | Add | 13
0 | SWPR004 | 2 | Circulating Block Heater | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-11-11 | Kenny Liljestrom |  |  | 12
0 | SWPR004 | 2 | Circulating Block Heater | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-11 | Kenny Liljestrom |  |  | 5
0 | SWPR004 | 2 | Circulating Block Heater | Any | Any | Any |  | EECP | 3 |  | Yes | Size | Back-up generator size (kW) | Numeric Value | [9 empty] | Inspections | Photograph the nameplate showing the capacity (kW) of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Review the make and model and locate the size (kW) of the backup generator | The generator size/power (kW) must algin with the measure case description |  | 2021-11-11 | Kenny Liljestrom |  |  | 27
0 | SWPR004 | 2 | Circulating Block Heater | Any | NR | Any |  | EECP | 4 | For a normal replacement (NR) installation, the existing backup generator is eligible if it is not currently fitted with a circulating block heater or device utilizing similar electro-mechanical system to heat and circulate generator block pre-warming fluid. | Yes | Electro-Mechanical system | Before installation of the measure was the existing backup generator fitted with a circulating block heater or device utilizing similar electro-mechanical system to heat and circulate generator block pre-warming fluid? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Review the installation report to determine if the existing conditions are documented and whether or not the existing generator is fitted with a circulating block heater or electro-mechanical system to pre-warm the fluid | For a normal replacement (NR) installation, the existing backup generator is eligible if it is not currently fitted with a circulating block heater or device utilizing similar electro-mechanical system to heat and circulate generator block pre-warming fluid. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-11 | Kenny Liljestrom |  |  | 218
0 | SWPR004 | 2 | Circulating Block Heater | Any | NC | Any |  | EECP | 5 | A new generator installation (i.e., new construction, NC), for which the base design prescribes a pre-heating device (e.g., thermosiphon heater) other than a circulating block heater or similar device is eligible to upgrade from base design to efficient design including a circulating block heater. | Yes |  | Does the base design prescribe a pre-heating device other than a circulating block heater? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Review the installation report to determine if the base design or code conditions are documented and whether or not the base design generator is fitted with a circulating block heater | A new generator installation (i.e., new construction, NC), for which the base design prescribes a pre-heating device (e.g., thermosiphon heater) other than a circulating block heater or similar device is eligible to upgrade from base design to efficient design including a circulating block heater. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-11-11 | Kenny Liljestrom |  |  | 90
0 | SWPR004 | 2 | Circulating Block Heater | Any | Any | Any |  | EECP | 6 | Additional eligibility requirements regarding the installation include: • Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician). • Installer should follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. • Installation shall meet all applicable regulations including but not limited to latest NFPA Code 110 for Emergency Power Systems and NEC. | Yes | Qualified Tech | Was the installation of the circulating block heater performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician)? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-11 | Kenny Liljestrom |  |  | 162
0 | SWPR004 | 2 | Circulating Block Heater | Any | Any | Any |  | EECP | 7 | Additional eligibility requirements regarding the installation include: • Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician). • Installer should follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. • Installation shall meet all applicable regulations including but not limited to latest NFPA Code 110 for Emergency Power Systems and NEC. | Yes | Installation Requirements | Did the Installer follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the circulating block heater to function at optimal energy efficiency? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-11 | Kenny Liljestrom |  |  | 248
0 | SWPR004 | 2 | Circulating Block Heater | Any | Any | Any |  | - | 7 | Additional eligibility requirements regarding the installation include: • Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician). • Installer should follow manufacturer’s installation requirements and assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. • Installation shall meet all applicable regulations including but not limited to latest NFPA Code 110 for Emergency Power Systems and NEC. | No | NFPA Code | Installation meets latest NFPA Code 110 for Emergency Power Systems and NEC installation guidelines? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-01-05 | Kenny Liljestrom | Program ops request to remove property since contractors are held liable in their contracts to install equipment in accordance with all safety and energy codes |  | 100
0 | SWPR004 | 2 | Circulating Block Heater | Any | Any | Any |  | EECP | 8 | This measure is applicable to the following non-residential building types, of any vintage: Assembly; Manufacturing - Bio/ - Community College; Manufacturing - Light Industrial; Education - Primary School; Office - Large; Education - Relocatable Classroom; Office - Small; Education - Secondary School; Restaurant - Fast-Food; Education - University; Restaurant - Sit-Down; Grocery; Retail - Multistory Large; Health/Medical - Hospital; Retail - Single-Story Large; Health/Medical - Nursing Home; Retail - Small; Lodging - Guest Rooms; Storage - Conditioned; Lodging - Hotel; Storage - Unconditioned; Lodging - Motel; Warehouse - Refrigerated | Yes |  | Building type | Drop Down List | Assembly;Manufacturing - Bio/ - Community College;Manufacturing - Light Industrial;Education - Primary School;Office - Large;Education - Relocatable Classroom;Office - Small;Education - Secondary School;Restaurant - Fast-Food;Education - University;Restaurant - Sit-Down;Grocery;Retail - Multistory Large;Health/Medical - Hospital;Retail - Single-Story Large;Health/Medical - Nursing Home;Retail - Small;Lodging - Guest Rooms;Storage - Conditioned;Lodging - Hotel;Storage - Unconditioned;Lodging - Motel;Warehouse - Refrigerated | [8 empty] | Inspections | While on site, observe and make note of the building type | The building type needs to be one of the following: Assembly, Manufacturing - Bio/Tech, Education - Community College, Manufacturing - Light Industrial, Education - Primary School, Office - Large, Education - Relocatable Classroom, Office - Small, Education - Secondary School, Restaurant - Fast-Food, Education - University, Restaurant - Sit-Down, Grocery, Retail - Multistory Large, Health/Medical - Hospital, Retail - Single-Story Large, Health/Medical - Nursing Home, Retail - Small, Lodging - Guest Rooms, Storage - Conditioned, Lodging - Hotel, Storage - Unconditioned, Lodging - Motel, Warehouse - Refrigerated | QA Checklist | Use the installation report or EECP to determine the building type | The building type needs to be one of the following: Assembly, Manufacturing - Bio/Tech, Education - Community College, Manufacturing - Light Industrial, Education - Primary School, Office - Large, Education - Relocatable Classroom, Office - Small, Education - Secondary School, Restaurant - Fast-Food, Education - University, Restaurant - Sit-Down, Grocery, Retail - Multistory Large, Health/Medical - Hospital, Retail - Single-Story Large, Health/Medical - Nursing Home, Retail - Small, Lodging - Guest Rooms, Storage - Conditioned, Lodging - Hotel, Storage - Unconditioned, Lodging - Motel, Warehouse - Refrigerated | Not configured in original upload | 2021-11-11 | Kenny Liljestrom |  |  | 13
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any |  | EECP | 1 | - | Pending | Manufacturer | VSD Manufacturer | Text Box | [9 empty] | Inspections | Photograph the ventilation fan nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-21 | Kenny Liljestrom |  |  | 16
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any |  | EECP | 2 | - | Pending | Model | VSD Model | Text Box | [9 empty] | Inspections | Photograph the ventilation fan nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-21 | Kenny Liljestrom |  |  | 9
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any |  | EECP | 3 | - | Pending |  | Motor Manufacturer | Text Box | [9 empty] | Inspections | Photograph the ventilation fan nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-21 | Kenny Liljestrom |  |  | 18
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any |  | EECP | 4 | - | Pending |  | Motor Model | Text Box | [9 empty] | Inspections | Photograph the ventilation fan nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-21 | Kenny Liljestrom |  |  | 11
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any |  | QA Checklist | 5 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending | Fan Power Rating | The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. | None | - | [7 empty] | - | QA Checklist | Use the manufacturer spec sheet (or make and model) to find the size of the fan motor(s) | The fan power (hp) must meet the measure case description; if there is any deviation from the measure case, the motor must not be < 10 or > 150 | - | - | - |  | 2021-09-21 | Kenny Liljestrom |  |  | 89
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | A | Any | Any |  | EECP | 6 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [8 empty] | Inspections | Observe the building type | The building/facility must be either an industrial or an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be either an industrial or an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | B | Any | Any |  | EECP | 7 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [8 empty] | Inspections | Observe the building type | The building/facility must be either an industrial or an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be either an industrial or an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | C | Any | Any |  | EECP | 8 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [8 empty] | Inspections | Observe the building type | The building/facility must be either an industrial or an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be either an industrial or an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | D | Any | Any |  | EECP | 9 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [8 empty] | Inspections | Observe the building type | The building/facility must be either an industrial or an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be either an industrial or an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | E | Any | Any |  | EECP | 10 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [8 empty] | Inspections | Observe the building type | The building/facility must be either an industrial or an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be either an industrial or an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | F | Any | Any |  | EECP | 11 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [8 empty] | Inspections | Observe the building type | The building/facility must be either an industrial or an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be either an industrial or an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | G | Any | Any |  | EECP | 12 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [8 empty] | Inspections | Observe the building type | The building/facility must be either an industrial or an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be either an industrial or an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | H | Any | Any |  | EECP | 13 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [7 empty] | Must be 'Agricultural' | Inspections | Observe the building type | The building/facility must be an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | I | Any | Any |  | EECP | 14 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [7 empty] | Must be 'Agricultural' | Inspections | Observe the building type | The building/facility must be an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | J | Any | Any |  | EECP | 15 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [7 empty] | Must be 'Agricultural' | Inspections | Observe the building type | The building/facility must be an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | K | Any | Any |  | EECP | 16 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [7 empty] | Must be 'Agricultural' | Inspections | Observe the building type | The building/facility must be an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | L | Any | Any |  | EECP | 17 | Both agricultural and industrial sectors are applicable for fan motors 50 hp or smaller, whereas fan motors larger than 50 hp are limited to the agricultural sector. The minimum fan size must be 10 hp to 150 hp, as defined in the Measure Case Description. For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 | Pending |  | Facility sector | Drop Down List | Industrial;Agricultural; | [7 empty] | Must be 'Agricultural' | Inspections | Observe the building type | The building/facility must be an agricultural site | QA Checklist | Use the installation report or EECP to determine the building type | The building/facility must be an agricultural site For customers with dust collection systems between 5 hp to 50 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 211120 to 213115 311000 to 339999 For customers with dust collection systems between 60 hp to 150 hp, the business/facility must have a NAICS Code as follows: 111000 to 112990 311000 to 311999 |  | 2021-09-21 | Kenny Liljestrom |  |  | 15
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any |  | EECP | 18 | The customer must have an existing electrically operated fixed-speed fan installed on site or plans to install a new electrically operated fixed-speed fan. The existing baghouse, fan, and motor must be in proper operating condition. The baghouse fan motor must be compatible with a variable speed drive (VSD).1 | Pending |  | Customer has (or plans to have) existing, operational, and VSD compatible fixed speed fan? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Use an installation report or photographs of the fan motor to prove the existing and proposed systems which show proof of the motor not being changed out during the project | The existing fan motor must be already installed (or planned to be installed for new construction applications), operational (working), and compatible with a VSD; the fan motor should not be changed out to be compatible with a VSD, photographs of the motor before and after the installation will prove the motor was not replaced during the project | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 90
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any |  | EECP | 19 | There must be no previous VSD or failed VSD installed on the baghouse existing fan motor. This measure cannot be used for the following fan applications: • HVAC fan • An individual fan motor rated less than 10 hp or higher than 150 hp • A two-speed fan motor • A fan motor with an existing VSD | Pending |  | Did existing fans (not HVAC related) previously have VSD controls? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | QA Checklist | Use an installation report or photographs of the fan motor showing there are currently no controls in place to vary the speed of the motor | The existing fan motor must not have a VSD installed; photographs of the motor before and after the installation will prove the motor did not have VSD controls already installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 66
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any |  | EECP | 20 | The installed VSD must be controlled based on static pressure, airflow rate (cfm), or velocity at the lowest required rate to keep particulates suspended in the air stream. The VSD is recommended to meet requirements as specified by IEEE Standard 519-2014.2. | Pending |  | VSD controlled by static pressure, airflow, or duct velocity and meets IEEE 519-2014.2 requirements? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | An installation report should indicate the method of control for the VSD feedback | The VSD must be controlled by static pressure, airflow, or duct velocity and the installation report should indicate which method of control is being used | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 100
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | H | Any | Any |  | EECP | 21 | The fan/blower must not be a designed high-pressure blower. High pressure blowers have designed capacities of less than 150 cfm per rated horsepower. (Applicable only to fan motors larger than 50 hp.) | Pending |  | Is the fan/blower a designed high-pressure blower (design capacity <= 150 cfm/hp)? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet (or make and model) to determine the type of fan/blower being used | The fan/blower must not be a 'high-pressure blower' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 82
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | I | Any | Any |  | EECP | 22 | The fan/blower must not be a designed high-pressure blower. High pressure blowers have designed capacities of less than 150 cfm per rated horsepower. (Applicable only to fan motors larger than 50 hp.) | Pending |  | Is the fan/blower a designed high-pressure blower (design capacity <= 150 cfm/hp)? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet (or make and model) to determine the type of fan/blower being used | The fan/blower must not be a 'high-pressure blower' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 82
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | J | Any | Any |  | EECP | 23 | The fan/blower must not be a designed high-pressure blower. High pressure blowers have designed capacities of less than 150 cfm per rated horsepower. (Applicable only to fan motors larger than 50 hp.) | Pending |  | Is the fan/blower a designed high-pressure blower (design capacity <= 150 cfm/hp)? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet (or make and model) to determine the type of fan/blower being used | The fan/blower must not be a 'high-pressure blower' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 82
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | K | Any | Any |  | EECP | 24 | The fan/blower must not be a designed high-pressure blower. High pressure blowers have designed capacities of less than 150 cfm per rated horsepower. (Applicable only to fan motors larger than 50 hp.) | Pending |  | Is the fan/blower a designed high-pressure blower (design capacity <= 150 cfm/hp)? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet (or make and model) to determine the type of fan/blower being used | The fan/blower must not be a 'high-pressure blower' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 82
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | L | Any | Any |  | EECP | 25 | The fan/blower must not be a designed high-pressure blower. High pressure blowers have designed capacities of less than 150 cfm per rated horsepower. (Applicable only to fan motors larger than 50 hp.) | Pending |  | Is the fan/blower a designed high-pressure blower (design capacity <= 150 cfm/hp)? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | QA Checklist | Use the manufacturer spec sheet (or make and model) to determine the type of fan/blower being used | The fan/blower must not be a 'high-pressure blower' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 82
1 | SWPR005 | 2 | Dust Collection Fan VSD, Industrial and Agriculture | Any | Any | Any |  | QA Checklist | 26 | This measure cannot be used for the following fan applications: • HVAC fan • An individual fan motor rated less than 10 hp or higher than 150 hp • A two-speed fan motor • A fan motor with an existing VSD | Pending |  | Is this measure for an HVAC fan? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | QA Checklist | Use photographs of the equipment the fan is serving | The equipment should not be HVAC related | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-21 | Kenny Liljestrom |  |  | 32
0 | SWPR007 | 1 | Steam Boiler Economizer, Industrial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Steam boiler manufacturer | Text Box | [9 empty] | Inspections | Photograph the Steam Boiler nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the Steam Boiler manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | Update property label to 'Steam boiler manufacturer' | 2021-09-17 | Kenny Liljestrom |  |  | 25
0 | SWPR007 | 1 | Steam Boiler Economizer, Industrial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Steam boiler model | Text Box | [9 empty] | Inspections | Photograph the Steam Boiler nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the Steam Boiler model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | Update property label to 'Steam boiler model' | 2021-09-17 | Kenny Liljestrom |  |  | 18
0 | SWPR007 | 1 | Steam Boiler Economizer, Industrial | Any | Any | Any |  | EECP | 3 | This measure is applicable to steam boilers only. The steam boiler must have an input rating ≤ 20 million Btu/hr. Hot water boilers are not eligible. | Pending |  | Steam boiler input rating (MMBtu/hr) | Numeric Value | [8 empty] | Must be <= 20 | Inspections | Photograph the steam boiler nameplate to capture the make, model, and input rating (MMBtu/hr) | The input rating (MMBtu/hr) must be <= 20 and match what is listed in EECP | QA Checklist | Use the installation report or photographs which show the steam boiler input rating | The steam boiler input rating must be <= 20 MMBtu/hr If the units on the nameplate are listed in Btu/hr, divide the number by 1,000,000 to convert to MMBtu/hr |  | 2021-09-17 | Kenny Liljestrom |  |  | 36
0 | SWPR007 | 1 | Steam Boiler Economizer, Industrial | Any | Any | Any |  | EECP | 4 | The boiler manufacturer, model, and spec sheet should be submitted for verification. | Pending |  | Steam boiler spec sheet submitted? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Review the documentation in EECP to determine if the boiler spec sheet was submitted | A spec sheet for the boiler must be submitted with the project files in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-17 | Kenny Liljestrom |  |  | 34
0 | SWPR007 | 1 | Steam Boiler Economizer, Industrial | Any | Any | Any |  | EECP | 5 | For a dual-stage economizer: • The disposal of combustion condensate must meet local codes regarding sanitary drain or storm sewer. • Some applications may require a neutralizer for the acidic combustion condensate. | Pending |  | Dual stage economizer: condensate meets sanitary and acidic neutralization of combustion codes? | Drop Down List | Yes;No;N/A; | [7 empty] | Must be 'Yes' or 'N/A' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-09-17 | Kenny Liljestrom |  |  | 95
0 | SWPR007 | 1 | Steam Boiler Economizer, Industrial | Any | Any | Any |  | EECP | 6 | - | Pending |  | Economizer manufacturer | Text Box | [9 empty] | Inspections | If accessible, photograph the economizer nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the economizer manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-09-17 | Kenny Liljestrom |  |  | 23
0 | SWPR007 | 1 | Steam Boiler Economizer, Industrial | Any | Any | Any |  | EECP | 7 | - | Pending |  | Economizer model | Text Box | [9 empty] | Inspections | If accessible, photograph the economizer nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the economizer model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-09-17 | Kenny Liljestrom |  |  | 16
0 | SWPR007 | 1 | Steam Boiler Economizer, Industrial | Any | Any | Any |  | EECP | 8 | There are no boiler efficiency eligibility requirements for the measure, for both single stage and two stage economizers. The efficiency gains were averaged from past custom projects and meeting these efficiencies (estimated improvement at 2% and 8% for single and dual stage economizer, respectively) is not a requirement for rebate. Good to have | Pending |  | Economizer efficiency / effectiveness (%) | Numeric Value | [9 empty] | QA Checklist | Use the make and model for the economizer (or spec sheet if submitted) to validate the economizer efficiency | There are no validation criteria for this property; the value should match between EECP and the spec sheet (if not easily available, this property can be ignored) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-09-17 | Kenny Liljestrom |  |  | 41
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted spec sheet or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the spec sheet or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-09 | Kenny Liljestrom |  | Add | 12
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted spec sheet or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the spec sheet or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-09 | Kenny Liljestrom |  | Add | 5
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any |  | EECP | 3 | Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Natural Gas Heated | Is the pool heated with natural gas? | Drop Down List | Yes;No | [7 empty] | Must be Yes | Inspections | Locate the water heater for the pool; photograph the nameplate of the pool water heater to capture the make, model, and input rating (Btu/hr) | The nameplate should indicate the input rating in Btu/hr or the unit should be easily identifiable as a gas fired unit; the pool water heater must be gas fired to qualify | QA Checklist | Use photographs or the installation report for the pool water heater to determine the fuel type (electric or gas) | The pool water heater must be fueled by natural gas to qualify |  | 2021-07-09 | Kenny Liljestrom |  | Add | 36
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any |  | EECP | 4 | Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Pool Area SF | What is area in square footage of the pool area | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Is this property the same as the quantity field? | 2021-07-09 | Kenny Liljestrom |  | Add | 47
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any |  | EECP | 5 | Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | R Value | R value (ft2-hr-F/Btu) | Numeric Value | [8 empty] | Must be >= 0.5 | QA Checklist | Use the manufacturer spec sheet to validate the R value (ft2-hr-F/Btu) is listed | The R value must be >= 0.5 ft2-hr-F/Btu | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-09 | Kenny Liljestrom |  | Add | 22
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any |  | EECP | 6 | This measure applies to outdoor and indoor heated swimming pools that do not already have pool cover. Energy efficiency programs are to target pools without existing pool covers. | Yes | Existing Pool Cover | Is there an existing pool cover in use? | Drop Down List | Yes;No | [7 empty] | Must be No | Inspections | During the site pre-inspection, determine if an existing cover is in use or if there are signs a pool cover was in use | An existing pool cover must not be in use to qualify for this measure | QA Checklist | The implementer should provide proof that an existing pool cover is not in use via photographs of the pool area and equipment storage locations | An existing pool cover must not be in use to qualify for this measure |  | 2021-07-09 | Kenny Liljestrom |  | Add | 39
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any |  | EECP | 7 | Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Pool Cover Requirements | Does the installed cover have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard)? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Use the manufacturer spec sheet to validate thickness, material, and thermal conductivity is listed | The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-09 | Kenny Liljestrom |  | Add | 174
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any |  | EECP | 8 | Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Pool Cover Size | How much of the pool does the new pool cover encompass? (%) | Numeric Value | [8 empty] | Must be >= 95% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-07-09 | Kenny Liljestrom |  | Add | 59
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any |  | EECP | 9 | Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Olympic Size_Storage Reel System | If the pool is Olympic sized, is there a storage reel system? | Drop Down List | N/A;Yes;No | [7 empty] | Must be 'Yes' or 'N/A' | Inspections | If the pool is Olympic sized (50 meters in length) determine if there is a storage reel system installed | Storage reels are required for Olympic sized pools to qualify | QA Checklist | If the pool is Olympic sized (50 meters in length) determine if there is a storage reel system installed via an installation report or photographs | Storage reels are required for Olympic sized pools to qualify | Update property values ("N/A") and add validation criteria | 2021-07-09 | Kenny Liljestrom |  | Add | 61
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any |  | EECP | 10 | Eligibility requirements include: • The pool must be heated with natural gas. • The cover must have 1/8" thick (L), high-density polyethylene foam of thermal conductivity (K) Factor 0.25 Btu/ ft2-Hr-°F/inch (based upon the ASTM D2326 standard, withdrawn). • The new pool cover must cover at least 95% of the pool. • The new pool cover must have a minimum R-value of 0.5 ft2-hr-F/Btu (R=L/K). R-value of 0.5 is the thermal resistance of the cover itself. • 100% post inspection. • Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies). • Proof of cover thickness and K factor (found on the manufacturer specification sheet). • Olympic size pools must have a storage reel system either manual or automatic winding and are subject to inspection. • Rebate is applicable to installed pool cover, per pool only. • Rebate is based on the square footage of the pool area. | Yes | Pool Cover Warranty | Does the pool cover come with a minimum 5 year warranty? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Use the manufacturer spec sheet or extended warranty documentation (if applicable) to determine if there is a minimum 5-year warranty on the pool cover | Proof of minimum five-year warranty (any combination of manufacturers and/or extended applies) is required at enrollment | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update validation criteria | 2021-07-09 | Kenny Liljestrom |  | Add | 56
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any |  | QA Checklist | 11 | The primary target building types for this measure are existing schools/colleges (educational institutions), city (municipal) recreational centers, home owner associations (e.g., condominiums with common pools), private/health clubs, and multifamily residences (apartment buildings). | Yes |  | Is the primary target building type for this measure an existing schools/colleges (educational institutions), city (municipal) recreational centers, home owner associations (e.g., condominiums with common pools), private/health clubs, and multifamily residences (apartment buildings)? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | Review the submitted documentation in EECP to determine the building type where the cover is being installed | The primary target building types for this measure are existing schools/colleges (educational institutions), city (municipal) recreational centers, home owner associations (e.g., condominiums with common pools), private/health clubs, and multifamily residences (apartment buildings). | - | - | - |  | 2021-07-12 | Kenny Liljestrom |  | Add | 284
1 | SWRE001 | 1 | Pool Cover, Commercial | Any | Any | Any |  | QA Checklist | 12 | New construction installations are not eligible. | Yes |  | New Construction | Drop Down List | Yes;No; | [7 empty] | Must be No | QA Checklist | Review the submitted documentation in EECP to determine the building vintage (Existing or New Construction) | New construction projects do not qualify for a rebate | - | - | - |  | 2021-07-12 | Kenny Liljestrom |  | Add | 16
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate of the pump to capture the manufacturer | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate of the pump to capture the model number | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any |  | EECP | 3 | Only main filtration pumps are eligible. | Yes | Installed on Main Pump | Was the measure installed on a main filtration pump? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Photograph the pool pumping system (all pumps visible), check to see if there are multiple VSD pumps running at one time or only one | There should only be a single VSD pump operating at a time | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 52
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any |  | EECP | 4 | Only one-for-one pump replacements are eligible. | Yes | Replacement | Is the measure a one-for-one pump replacement? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 46
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any |  | EECP | 5 | Both base case and measure case pool pumps must be between 1 hp and 3 hp, with horsepower referring to the (rated) nameplate horsepower before service factor is applied. | Yes | Size | base case and measure case pool pumps? (hp) | Numeric Value | [8 empty] | Must be >= 1 and <=3 | Inspections | Photograph the pump nameplate to capture the motor horsepower | The horsepower should match what is listed in EECP and be between 1 and 3hp | QA Checklist | Use the submitted invoice or installation report to show the existing and proposed conditions for the motor power (hp); or a manufacturer specification sheet showing the motor power (hp) | The motor power (hp) listed in EECP should match the installation report or spec sheet and must be >= 1 and <= 3 |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any |  | EECP | 6 | The variable speed drive (VSD) pump must replace an existing single- or two-speed pool pump and meet base case and measure case requirements, as specified in the Base Case Description and Measure Case Description, respectively. | Yes | VSD Replace | Did the installed variable speed drive (VSD) pump replace an existing single- or two-speed pool pump? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 101
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any |  | EECP | 7 | Nominal capacity of the new VSD pump should match the capacity of the pump being replaced (recommended). | Yes | VSD Capacity Match | Does the nominal capacity of the new VSD pump match the capacity of the pump being replaced? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 92
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any |  | EECP | 8 | The VSD pump must be configured to meet program pump configuration requirements. | Yes | VSD Configuration | Was the VSD pump configured to meet program pump configuration requirements? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 76
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any |  | EECP | 9 | For models that require an automatic control system capable of controlling both high and low speeds, a controller must be installed. | Yes | Controller Installed | For models that require an automatic control system capable of controlling both high and low speeds, was a controller installed? | Drop Down List | Yes;No;N/A | [7 empty] | Must be 'Yes' or 'N/A' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 128
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any |  | EECP | 10 | Measure implementation must be completed with both the customer and the installation contractor acknowledgement of energy savings settings. | Yes | Customer_Contractor | Did both the customer and the installation contractor acknowledge the energy savings setting of the installed measure? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 118
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any |  | EECP | 11 | The installation contractor shall follow all manufacturer installation requirements and comply with all applicable regulations. The installation shall meet all applicable standards and regulations including (but not limited to) NEC and the California Title 24 and Title 20 regulations (see Code Requirements). | Yes | Contractor Instructions | Did the installation contractor follow all manufacturer installation requirements and comply with all applicable standards and regulations including (but not limited to) NEC and the California Title 24 and Title 20 regulations (see Code Requirements).? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 252
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any |  | EECP | 13 | Pumps being replaced must be disposed of rather than refurbished and sold. | Yes | Disposal | Was the pump being replaced disposed of rather than refurbished and/or sold? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 76
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any |  | EECP | 14 | Equipment and materials must meet or exceed all applicable local, state and federal standards. | Yes | Equipment Standards | Did equipment and materials meet or exceed all applicable local, state and federal standards? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 93
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any |  | EECP | 15 | The installation must be completed by a utility-approved contractor or a contractor with the appropriate license and training. All direct installation with downstream delivery installations must be completed by a utility-approved contractor. Utility-approved contractors will complete both technical and program-related training to ensure proper installation. Each approved contractor will be trained such that they can properly collect and submit the correct (and corresponding) information for both accelerated replacement (AR) and normal replacement (NR) measures. | Yes | Approved Contractor | Was the installation of the measure completed by a utility-approved contractor? | Drop Down List | Yes;No | [7 empty] | If No - enable "Self-Install" | QA Checklist | Check the contractor listed as performing the work against the trade professional database | The contractor who performed the installation should be listed in the trade pro database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 79
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | B | Any | Any |  | EECP | 16 | Self-Installed Measures: Measure B shall be specified on applications for which the client installs their own variable speed pump, or if no certified contractor is used to install the equipment. | No |  | Only eligible for Single Family Homes, did the customer perform self-installation of the new pump? | Drop Down List | Yes;No | [7 empty] | Enable if Approved Contractor is 'No' Must be 'Yes' | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 98
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any |  | EECP | 17 | The variable speed pool pump or motor must be a new | Yes | New Equipment | Was the installed equipment new? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Contractor should provide evidence of proof of purchase or invoice showing the purchase date of the pump | The invoice should list the pump as being new or not used in the description | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 32
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | Any | Any |  | EECP | 18 | Program Exclusions: New parts installed in existing units and Motor-only replacements | No |  | Was the equipment fully replaced (i.e. not a part swap or motor only replacement)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 82
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | AR | Any |  | EECP | 19 | For accelerated replacement application types, the customer must be approached by a direct install implementer. | No |  | Was the customer approached directly by a direct installation implementer? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 74
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | AR | Any |  | EECP | 20 | Preponderance of evidence (POE) will be assessed at the program-level based on the direction outlined in the “Accelerated Replacement Using Preponderance of Evidence” of the T1 Working Group Report prepared for the California Public Utilities Commission (CPUC). Additional information and documentation to ensure conformance to eligibility and implementation requirements, include (but are not limited to) the following: Customer/site information Existing equipment Replacement equipment Permits and associated documentation Pump commissioning information | No |  | Has all Preponderance of Evidence (POE) been presented including: Customer site information, Make/model of pre-existing equipment, Make/model of replacement equipment, Permits and associated documentation, and Pump commissioning information? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 242
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | AR | Any |  | EECP | 21 | Risk mitigation | No |  | Who was the party that filled out the POE documentation? | Drop Down List | Customer;Customer Representative;Program Advisor;Implementer; | [7 empty] | Must be 'Yes' | - | - | - | - | - | - | Not configured in original upload | 2021-10-20 | Kenny Liljestrom | Implementers responsible for POE documentation | Add | 56
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | Any | AR | Any |  | EECP | 22 | All accelerated replacement measures require third-party baseline verification and data gathering in full compliance with the established POE requirements. | No |  | Was third-party baseline verification and data gathering in full compliance with the established POE requirements performed? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 124
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | A | Any | Any |  | EECP | 23 | Program Exclusions: Pool Pumps installed in a spa or jacuzzi at a single-family residence. | No |  | Was a pool pump installed in a spa or jacuzzi? | Drop Down List | Yes;No | [7 empty] | Must be No | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 46
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | B | Any | Any |  | EECP | 24 | Program Exclusions: Pool Pumps installed in a spa or jacuzzi at a single-family residence. | No |  | Was a pool pump installed in a spa or jacuzzi? | Drop Down List | Yes;No | [7 empty] | Must be No | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 46
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | C | Any | Any |  | EECP | 25 | Program Exclusions: Pool Pumps installed in a spa or jacuzzi at a single-family residence. | No |  | Was a pool pump installed in a spa or jacuzzi? | Drop Down List | Yes;No | [7 empty] | Must be No | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 46
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | H | Any | Any |  | EECP | 26 | Program Exclusions: Pool Pumps installed in a spa or jacuzzi at a single-family residence. | No |  | Was a pool pump installed in a spa or jacuzzi? | Drop Down List | Yes;No | [7 empty] | Must be No | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 46
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | I | Any | Any |  | EECP | 27 | Program Exclusions: Pool Pumps installed in a spa or jacuzzi at a single-family residence. | No |  | Was a pool pump installed in a spa or jacuzzi? | Drop Down List | Yes;No | [7 empty] | Must be No | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 46
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | A | Any | Any |  | EECP | 28 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | B | Any | Any |  | EECP | 29 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | C | Any | Any |  | EECP | 30 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any |  | EECP | 31 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any |  | EECP | 32 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any |  | EECP | 33 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any |  | EECP | 34 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any |  | EECP | 35 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any |  | EECP | 36 | Program Exclusions: Rented or leased products | Yes | Equipment Rented_Leased | Is the installed equipment rented or leased? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not a rented or leased piece of equipment | The pump needs to be shown as fully purchased with no terms of a rental period or lease agreement | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 44
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | A | Any | Any |  | EECP | 37 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [7 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | B | Any | Any |  | EECP | 38 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [7 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | C | Any | Any |  | EECP | 39 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [7 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any |  | EECP | 40 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [7 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any |  | EECP | 41 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [7 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any |  | EECP | 42 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [7 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any |  | EECP | 43 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [7 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any |  | EECP | 44 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [7 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any |  | EECP | 45 | Program Exclusions: Booster pumps solely used for an added spa jet circulation or secondary pumps used for cleaning purposes | Yes | Booster Pump | Is the installed equipment a booster pump solely used for an added spa jet circulation or secondary pumps used for cleaning purposes? | Drop Down List | Yes;No | [7 empty] | Must be No | Inspections | Look at the piping system coming from the VSD pump, the piping system connected to the pump should only be connected to the pool filtration system | The VSD pump should only be connected to the pool, not a spa or jacuzzi | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | A | Any | Any |  | EECP | 46 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | B | Any | Any |  | EECP | 47 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | C | Any | Any |  | EECP | 48 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any |  | EECP | 49 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any |  | EECP | 50 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any |  | EECP | 51 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any |  | EECP | 52 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any |  | EECP | 53 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any |  | EECP | 54 | Program Exclusions: Products won as prizes | Yes | Equipment Prize | Was the installed equipment won as a prize? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Purchase invoice should show the pump as being a purchase, not won as a prize | A purchase invoice will show the amount paid for the pump, there shouldn't be any rebates or discounts indicating the customer paid little to no cost for the unit | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 43
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | A | Any | Any |  | EECP | 55 | Only one variable-speed pool pump and motor rebate per residence. | No |  | Has only one variable-speed pool pump and motor been installed at the residence? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 80
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | B | Any | Any |  | EECP | 56 | Only one variable-speed pool pump and motor rebate per residence. | No |  | Has only one variable-speed pool pump and motor been installed at the residence? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 80
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | C | Any | Any |  | EECP | 57 | Only one variable-speed pool pump and motor rebate per residence. | No |  | Has only one variable-speed pool pump and motor been installed at the residence? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 80
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | A | Any | Any |  | EECP | 58 | Filtration settings must be configured to operate outside peak hours, as defined by the utility. | No |  | Have the filtration settings been configured to operate outside peak hours, as defined by the utility? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 102
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | B | Any | Any |  | EECP | 59 | Filtration settings must be configured to operate outside peak hours, as defined by the utility. | No |  | Have the filtration settings been configured to operate outside peak hours, as defined by the utility? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 102
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | C | Any | Any |  | EECP | 60 | Filtration settings must be configured to operate outside peak hours, as defined by the utility. | No |  | Have the filtration settings been configured to operate outside peak hours, as defined by the utility? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 102
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | A | Any | Any |  | EECP | 61 | • Customers must acknowledge and confirm operation on application form in order to be eligible for rebate. | No |  | Has the customer confirmed the operation of the replacement equipment on the application form? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 94
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | B | Any | Any |  | EECP | 62 | • Customers must acknowledge and confirm operation on application form in order to be eligible for rebate. | No |  | Has the customer confirmed the operation of the replacement equipment on the application form? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 94
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | C | Any | Any |  | EECP | 63 | • Customers must acknowledge and confirm operation on application form in order to be eligible for rebate. | No |  | Has the customer confirmed the operation of the replacement equipment on the application form? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 94
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any |  | EECP | 64 | Only one rebate is allowed per spa OR wading pool pump. | No |  | Has only one rebate been applied per spa or wading pool? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 56
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any |  | EECP | 65 | Only one rebate is allowed per spa OR wading pool pump. | No |  | Has only one rebate been applied per spa or wading pool? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 56
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any |  | EECP | 66 | Only one rebate is allowed per spa OR wading pool pump. | No |  | Has only one rebate been applied per spa or wading pool? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 56
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any |  | EECP | 67 | Only one rebate is allowed per spa OR wading pool pump. | No |  | Has only one rebate been applied per spa or wading pool? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 56
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any |  | EECP | 68 | A maximum of three rebates are allowed per customer property/site for main filtration pump(s). Incentive applications for more than one main filtration pump require supporting documentation verifying existing condition per Authority Having Jurisdiction. | No |  | Has the customer received less than or equal to the three maximum rebates per property/site for the main filtration pumps (includes pools, spas, and wading pools)? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 163
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any |  | EECP | 69 | A maximum of three rebates are allowed per customer property/site for main filtration pump(s). Incentive applications for more than one main filtration pump require supporting documentation verifying existing condition per Authority Having Jurisdiction. | No |  | Has the customer received less than or equal to the three maximum rebates per property/site for the main filtration pumps (includes pools, spas, and wading pools)? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 163
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any |  | EECP | 70 | A maximum of three rebates are allowed per customer property/site for main filtration pump(s). Incentive applications for more than one main filtration pump require supporting documentation verifying existing condition per Authority Having Jurisdiction. | No |  | Has the customer received less than or equal to the three maximum rebates per property/site for the main filtration pumps (includes pools, spas, and wading pools)? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 163
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any |  | EECP | 71 | A maximum of three rebates are allowed per customer property/site for main filtration pump(s). Incentive applications for more than one main filtration pump require supporting documentation verifying existing condition per Authority Having Jurisdiction. | No |  | Has the customer received less than or equal to the three maximum rebates per property/site for the main filtration pumps (includes pools, spas, and wading pools)? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 163
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any |  | EECP | 72 | A maximum of three rebates are allowed per customer property/site for main filtration pump(s). Incentive applications for more than one main filtration pump require supporting documentation verifying existing condition per Authority Having Jurisdiction. | No |  | Has the customer received less than or equal to the three maximum rebates per property/site for the main filtration pumps (includes pools, spas, and wading pools)? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 163
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any |  | EECP | 73 | A maximum of three rebates are allowed per customer property/site for main filtration pump(s). Incentive applications for more than one main filtration pump require supporting documentation verifying existing condition per Authority Having Jurisdiction. | No |  | Has the customer received less than or equal to the three maximum rebates per property/site for the main filtration pumps (includes pools, spas, and wading pools)? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-08-06 | Kenny Liljestrom |  | Add | 163
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any |  | EECP | 74 | During pool operating hours, the VSD setting must be “right sized” to meet turn-over requirements as specified by the 2019 Title 24 standards, Chapter 31B “Public Swimming Pools,” Section 3124B. (See Code Requirements). | Yes | VSD Setting | During pool operating hours, was the VSD setting “right sized”? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 63
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any |  | EECP | 75 | During pool operating hours, the VSD setting must be “right sized” to meet turn-over requirements as specified by the 2019 Title 24 standards, Chapter 31B “Public Swimming Pools,” Section 3124B. (See Code Requirements). | Yes | VSD Setting | During pool operating hours, was the VSD setting “right sized”? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 63
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any |  | EECP | 76 | During pool operating hours, the VSD setting must be “right sized” to meet turn-over requirements as specified by the 2019 Title 24 standards, Chapter 31B “Public Swimming Pools,” Section 3124B. (See Code Requirements). | Yes | VSD Setting | During pool operating hours, was the VSD setting “right sized”? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 63
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any |  | EECP | 77 | During pool operating hours, the VSD setting must be “right sized” to meet turn-over requirements as specified by the 2019 Title 24 standards, Chapter 31B “Public Swimming Pools,” Section 3124B. (See Code Requirements). | Yes | VSD Setting | During pool operating hours, was the VSD setting “right sized”? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 63
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any |  | EECP | 78 | During pool operating hours, the VSD setting must be “right sized” to meet turn-over requirements as specified by the 2019 Title 24 standards, Chapter 31B “Public Swimming Pools,” Section 3124B. (See Code Requirements). | Yes | VSD Setting | During pool operating hours, was the VSD setting “right sized”? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 63
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any |  | EECP | 79 | During pool operating hours, the VSD setting must be “right sized” to meet turn-over requirements as specified by the 2019 Title 24 standards, Chapter 31B “Public Swimming Pools,” Section 3124B. (See Code Requirements). | Yes | VSD Setting | During pool operating hours, was the VSD setting “right sized”? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 63
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | H | Any | Any |  | EECP | 80 | During Pool Operating Hours: Variable speed drive setting must be “right sized” to meet turnover requirements as specified by California Code of Regulations, Title 24, Building Standards Code (2016): Chapter 31B “Public Swimming Pools,” Section 3124B. | Yes | VSD Setting | During pool operating hours, was the VSD setting “right sized”? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 63
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | I | Any | Any |  | EECP | 81 | During Pool Operating Hours: Variable speed drive setting must be “right sized” to meet turnover requirements as specified by California Code of Regulations, Title 24, Building Standards Code (2016): Chapter 31B “Public Swimming Pools,” Section 3124B. | Yes | VSD Setting | During pool operating hours, was the VSD setting “right sized”? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 63
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any |  | EECP | 82 | During pool non-operating hours, the VSD setting must be configured to at least 50% of full-speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting | VSD setting percentage during non-operating hours | Numeric Value | [8 empty] | Must be <=50% | Inspections | Photograph the motor display panel showing the scheduled operating conditions for the pool pump | The setting must be less than or equal to 50% speed during nighttime hours | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any |  | EECP | 83 | During pool non-operating hours, the VSD setting must be configured to at least 50% of full-speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting | VSD setting percentage during non-operating hours | Numeric Value | [8 empty] | Must be <=50% | Inspections | Photograph the motor display panel showing the scheduled operating conditions for the pool pump | The setting must be less than or equal to 50% speed during nighttime hours | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any |  | EECP | 84 | During pool non-operating hours, the VSD setting must be configured to at least 50% of full-speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting | VSD setting percentage during non-operating hours | Numeric Value | [8 empty] | Must be <=50% | Inspections | Photograph the motor display panel showing the scheduled operating conditions for the pool pump | The setting must be less than or equal to 50% speed during nighttime hours | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any |  | EECP | 85 | During pool non-operating hours, the VSD setting must be configured to at least 50% of full-speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting | VSD setting percentage during non-operating hours | Numeric Value | [8 empty] | Must be <=50% | Inspections | Photograph the motor display panel showing the scheduled operating conditions for the pool pump | The setting must be less than or equal to 50% speed during nighttime hours | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any |  | EECP | 86 | During pool non-operating hours, the VSD setting must be configured to at least 50% of full-speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting | VSD setting percentage during non-operating hours | Numeric Value | [8 empty] | Must be <=50% | Inspections | Photograph the motor display panel showing the scheduled operating conditions for the pool pump | The setting must be less than or equal to 50% speed during nighttime hours | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any |  | EECP | 87 | During pool non-operating hours, the VSD setting must be configured to at least 50% of full-speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting | VSD setting percentage during non-operating hours | Numeric Value | [8 empty] | Must be <=50% | Inspections | Photograph the motor display panel showing the scheduled operating conditions for the pool pump | The setting must be less than or equal to 50% speed during nighttime hours | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | H | Any | Any |  | EECP | 88 | During Pool Non-Operating Hours: Variable speed drive setting must be configured to at least 50% of full speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting | VSD setting percentage during non-operating hours | Numeric Value | [8 empty] | Must be <=50% | Inspections | Photograph the motor display panel showing the scheduled operating conditions for the pool pump | The setting must be less than or equal to 50% speed during nighttime hours | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | I | Any | Any |  | EECP | 89 | During Pool Non-Operating Hours: Variable speed drive setting must be configured to at least 50% of full speed operation to achieve energy savings. Running the pump at half speed will theoretically reduce power draw to 1/8 of full power, but actual power draw will likely be higher due to lower motor efficiencies at part load. | Yes | VSD Non_Op setting | VSD setting percentage during non-operating hours | Numeric Value | [8 empty] | Must be <=50% | Inspections | Photograph the motor display panel showing the scheduled operating conditions for the pool pump | The setting must be less than or equal to 50% speed during nighttime hours | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any |  | EECP | 90 | Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit | Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | Drop Down List | Yes;No;N/A | [7 empty] | Must be Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 134
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any |  | EECP | 91 | Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit | Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | Drop Down List | Yes;No;N/A | [7 empty] | Must be Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 134
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any |  | EECP | 92 | Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit | Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | Drop Down List | Yes;No;N/A | [7 empty] | Must be Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 134
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any |  | EECP | 93 | Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit | Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | Drop Down List | Yes;No;N/A | [7 empty] | Must be Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 134
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any |  | EECP | 94 | Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit | Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | Drop Down List | Yes;No;N/A | [7 empty] | Must be Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 134
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any |  | EECP | 95 | Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit | Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | Drop Down List | Yes;No;N/A | [7 empty] | Must be Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 134
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | H | Any | Any |  | EECP | 96 | Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit | Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | Drop Down List | Yes;No;N/A | [7 empty] | Must be Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 134
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | I | Any | Any |  | EECP | 97 | Must obtain and submit a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction; if applicable. | Yes | Permit | Was a permit from the governing Environmental Health & Safety Department (i.e. County or City) of jurisdiction obtained and submitted? | Drop Down List | Yes;No;N/A | [7 empty] | Must be Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 134
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any |  | EECP | 98 | Health code requirements and inspections must be passed successfully. | Yes | Health Inspection | Were all health code requirements and inspections passed successfully? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 70
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any |  | EECP | 99 | Health code requirements and inspections must be passed successfully. | Yes | Health Inspection | Were all health code requirements and inspections passed successfully? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 70
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any |  | EECP | 100 | Health code requirements and inspections must be passed successfully. | Yes | Health Inspection | Were all health code requirements and inspections passed successfully? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 70
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any |  | EECP | 101 | Health code requirements and inspections must be passed successfully. | Yes | Health Inspection | Were all health code requirements and inspections passed successfully? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 70
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any |  | EECP | 102 | Health code requirements and inspections must be passed successfully. | Yes | Health Inspection | Were all health code requirements and inspections passed successfully? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 70
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any |  | EECP | 103 | Health code requirements and inspections must be passed successfully. | Yes | Health Inspection | Were all health code requirements and inspections passed successfully? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 70
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | H | Any | Any |  | EECP | 104 | Health code requirements and inspections must be passed successfully. | Yes | Health Inspection | Were all health code requirements and inspections passed successfully? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 70
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | I | Any | Any |  | EECP | 105 | Health code requirements and inspections must be passed successfully. | Yes | Health Inspection | Were all health code requirements and inspections passed successfully? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 70
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | D | Any | Any |  | EECP | 106 | EH&S Department approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved | Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | F | Any | Any |  | EECP | 107 | EH&S Department approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved | Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | G | Any | Any |  | EECP | 108 | EH&S Department approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved | Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | J | Any | Any |  | EECP | 109 | EH&S Department approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved | Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | K | Any | Any |  | EECP | 110 | EH&S Department approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved | Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | L | Any | Any |  | EECP | 111 | EH&S Department approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved | Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | H | Any | Any |  | EECP | 112 | EH&S approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved | Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | I | Any | Any |  | EECP | 113 | EH&S Department approves size and model of pump for installation, as well as, the required minimum and maximum flow rates based on specific site conditions. | Yes | EHS Approved | Did EH&S Department approve the size and model of pump for installation? As well as the required minimum and maximum flow rates based on specific site conditions? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 162
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | H | Any | Any |  | EECP | 114 | The customer, as part of the incentive application process shall acknowledge that the replacement pool pump VSD has been configured to achieve energy savings and agreed to have the pump filtration settings programmed for reduced flow during pool non-operating hours. | No |  | Has the customer, as part of the incentive application process, acknowledged that the replacement pool pump VSD has been configured to achieve energy savings and agreed to have the pump filtration settings programmed for reduced flow during pool non-operating hours? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-05-28 | Kenny Liljestrom | Removed, trust on part of implementer to inform customer of savings for measure. Also no way to verify | Add | 266
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | I | Any | Any |  | EECP | 115 | The customer, as part of the incentive application process shall acknowledge that the replacement pool pump VSD has been configured to achieve energy savings and agreed to have the pump filtration settings programmed for reduced flow during pool non-operating hours. | No |  | Has the customer, as part of the incentive application process, acknowledged that the replacement pool pump VSD has been configured to achieve energy savings and agreed to have the pump filtration settings programmed for reduced flow during pool non-operating hours? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-05-28 | Kenny Liljestrom | Removed, trust on part of implementer to inform customer of savings for measure. Also no way to verify | Add | 266
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | H | Any | Any |  | EECP | 116 | The customer shall agree not to modify and/or alter in any way programmed settings on the pump VSD to ensure persistence of the measure savings. | No |  | Has the customer agreed not to modify and/or alter, in any way, programmed settings on the pump VSD to ensure persistence of the measure savings? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-05-28 | Kenny Liljestrom | Removed, trust on part of implementer to inform customer of savings for measure. Also no way to verify | Add | 145
0 | SWRE002 | 1 | VSD for Pool & Spa Pump | I | Any | Any |  | EECP | 117 | The customer shall agree not to modify and/or alter in any way programmed settings on the pump VSD to ensure persistence of the measure savings. | No |  | Has the customer agreed not to modify and/or alter, in any way, programmed settings on the pump VSD to ensure persistence of the measure savings? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-05-28 | Kenny Liljestrom | Removed, trust on part of implementer to inform customer of savings for measure. Also no way to verify | Add | 145
1 | SWRE003 | 1 | Heater for Pool or Spa, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-12 | Kenny Liljestrom |  | Add | 12
1 | SWRE003 | 1 | Heater for Pool or Spa, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-12 | Kenny Liljestrom |  | Add | 5
1 | SWRE003 | 1 | Heater for Pool or Spa, Commercial | Any | Any | Any |  | EECP | 3 | This measure is available for swimming pool heating and the unit must replace pre-existing pool heater. | Yes | Existing Heater | Did the installed heater replace an existing pool heater? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Review the submitted documentation in EECP (either photographs or an installation report) to determine if there is an existing pool heater installed | The implementer needs to provide proof there is an existing heater on site | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 57
1 | SWRE003 | 1 | Heater for Pool or Spa, Commercial | Any | Any | Any |  | EECP | 4 | The commercial pool heater must be certified to meet the following requirements: • The heater must have TE ≥ 84% • The heater must have an ON/OFF switch and no pilot light | Yes | EFFICIENCY | Thermal efficiency of installed heater (%) | Numeric Value | [8 empty] | Must be > 84% | Inspections | Photograph the nameplate showing the efficiency (%) of the unit | The efficiency listed in EECP should match what is listed on the nameplate; the efficiency needs to be > 84% | QA Checklist | Use the manufacturer spec sheet to validate the equipment efficiency (%) | The efficiency listed in EECP should match what is listed in the spec sheet; the efficiency needs to be > 84% |  | 2021-07-12 | Kenny Liljestrom |  | Add | 42
1 | SWRE003 | 1 | Heater for Pool or Spa, Commercial | Any | Any | Any |  | EECP | 5 | The commercial pool heater must be certified to meet the following requirements: • The heater must have TE ≥ 84% • The heater must have an ON/OFF switch and no pilot light | Yes | ON_OFF Switch | Does the installed heater have an ON/OFF switch and no pilot light? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Use the manufacturer spec sheet to determine if the unit has an On/Off switch and no pilot light | The heater must be an On/Off type heater with no pilot light | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 67
1 | SWRE003 | 1 | Heater for Pool or Spa, Commercial | Any | Any | Any |  | QA Checklist | 6 | This measure is applicable to all heated pools installed in commercial facilities, such as schools, colleges, universities, YMCA/YWCA, public facilities, hotels/motels, health clubs, and spas. This measure is also applicable for multifamily properties, such as homeowner associations and other multifamily complexes. | Yes |  | Is the building type: commercial facilities, such as schools, colleges, universities, YMCA/YWCA, public facilities, hotels/motels, health clubs, and spas. This measure is also applicable for multifamily properties, such as homeowner associations and other multifamily complexes? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Review the documentation in EECP to determine the building type | The building type must be one of the following: commercial facilities, such as schools, colleges, universities, YMCA/YWCA, public facilities, hotels/motels, health clubs, and spas. This measure is also applicable for multifamily properties, such as homeowner associations and other multifamily complexes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-12 | Kenny Liljestrom |  | Add | 278
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | An installation report should indicate the work performed and show Duct Seal and testing specifications for the HVAC system including existing and proposed leakage rates | The manufacturer may be listed as the implementer or contractor who performed the work or the product used to perform the sealing | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | An installation report should indicate the work performed and show Duct Seal and testing specifications for the HVAC system including existing and proposed leakage rates | The model number may be listed as the implementer or contractor who performed the work or the product used to perform the sealing | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any |  | EECP | 3 | This measure is applicable for any existing single family, multifamily with two or more units, or mobile home that uses air-cooled, direct expansion (DX) cooling and gas heating, heat pump, or gas heating with no cooling. | Yes |  | What type of HVAC system does the customer have? | Drop Down List | Air-cooled direct expansion (DX) cooling and gas heating;Heat pump;Gas heating with no cooling;Other; | [7 empty] | Must not be 'Other' | QA Checklist | An installation report should indicate the type of HVAC system the customer has | HVAC system type should match EECP and be one of the following: Air-cooled direct expansion (DX) cooling and gas heating, Heat pump, or Gas heating with no cooling | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 48
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any |  | EECP | 4 | Up to two duct tests must be conducted: the first or “test-in” is a system check to determine whether the duct system tightness meets the California Title 24 specifications. | Yes |  | Test-in Duct Leakage Rate (%) | Numeric Value | [9 empty] | QA Checklist | An installation report should indicate the test-in leakage rate | the test-in leakage rate should be greater than or equal to the measure case leakage rate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 29
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any |  | EECP | 5 | If the Test-in shows that duct leakage exceeds minimum tightness specifications, and the technicians correct the situation, then a second test or “test-out” must be conducted to verify proper duct tightness was achieved. | Yes |  | Test-out Duct Leakage Rate (%) | Numeric Value | [9 empty] | QA Checklist | An installation report should indicate the test-out leakage rate | the test-out leakage rate should be less than or equal to the measure case leakage rate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 30
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any |  | EECP | 6 | If some or all of the existing ductwork is beyond repair and sections must be replaced, the sections that must be replaced must be less than 40 linear feet in total per Section 150.2(b) of the 2019 California Building Energy Efficiency Standards (Title 24) | Yes |  | Length of ductwork replaced (linear feet) | Numeric Value | [9 empty] | Inspections | Photograph of the ductwork showing repairs or replacements in the ducting system | Using your best judgement, determine if more than 40-linear feet of duct work was added or replaced as part of the project; the replacement ductwork must be < 40-feet to be eligible | QA Checklist | An installation report should indicate, if any, the length of the duct work replaced as part of the project | If some or all of the existing ductwork is beyond repair and sections must be replaced, the sections that must be replaced must be less than 40 linear feet in total per Section 150.2(b) of the 2019 California Building Energy Efficiency Standards (Title 24) | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 41
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any |  | EECP | 7 | ...or the replaced ductwork must be installed and tested in accordance with the applicable requirements in 2019 Title 24 Section 150.2(b)1D | Yes |  | Ductwork length > 40-ft been installed and tested in accordance to 2019 Title 24 Section 150.2(b)1D? | Drop Down List | Yes;No;N/A; | [7 empty] | Must be 'Yes' or 'N/A' | QA Checklist | If the length of ductwork replaced is greater than 40-linear feet, the implementer should supply the Title-24 compliance sheets as part of the documentation | Photograph of the ductwork showing repairs or replacements in the ducting system | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 100
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any |  | EECP | 8 | To identify these measures as part of an existing HVAC system, the program implementer must record existing duct leakage through comprehensive field testing. The testing can be performed while the system is pressurized using a duct blower fan to ensure the target leakage thresholds are achieved. Duct sealing shall be performed on the unpressurized system. After installation, testing shall be performed to ensure the target leakage thresholds are achieved. Photos and test results can serve as documentation that the work was performed on an existing HVAC system. | Yes |  | Has photographic evidence or documentation of the test-in and test-out procedures been uploaded? | Drop Down List | Yes;No; | [7 empty] | Must be ''Yes' | QA Checklist | Review the submitted documentation in EECP to look for photographic evidence or documentation of the test-in and test-out procedures | An installation report with photographs of the test-in and test-out leakage rates should be included in the submitted documentation | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 96
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any |  | EECP | 9 | Programs often bundle Quality Maintenance (QM) measures. The following prerequisites must be met before the QM treatments, such as airflow adjustments, can be implemented to ensure an HVAC system is running optimally. | Yes |  | Additional QM measures (i.e. airflow adjustments) being installed in conjunction with this measure? | Drop Down List | Yes;No; | [8 empty] | QA Checklist | If implementer answers 'Yes', check the measures installed as part of the enrollment and via double-dip report | If the implementer answers yes to this question, they must meet the following criteria to be eligible | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 99
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any |  | EECP | 10 | • The unit must be drawing power. | Yes |  | Is the unit drawing power? | Drop Down List | Yes;No; | [7 empty] | If 'QM Eligibility' is Yes then Must be ''Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, review the submitted documentation in EECP | Ensure the installation report shows the HVAC system as being functional prior to any work being performed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 26
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any |  | EECP | 11 | • The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted. | Yes |  | Refrigerant charge adjustments, unit has been tested to deliver supply air of at least 350 cfm/ton? | Drop Down List | Yes;No;N/A; | [7 empty] | If 'QM Eligibility' is Yes then Refrigerant Check must be 'Yes' or 'N/A' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, review the submitted documentation in EECP | Ensure the installation report shows the HVAC system having a tested airflow supply rate of greater than or equal to 350 cfm/ton 350 * tonnage of HVAC system = airflow rate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 99
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any |  | EECP | 12 | • The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees. | Yes |  | Does the unit have a condenser over ambient temperature (COAT) of at least 3 degrees F? | Drop Down List | Yes;No; | [7 empty] | If 'QM Eligibility' is Yes then Must be 'Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, review the submitted documentation in EECP | Ensure the installation report shows the COAT is greater than or equal to 3 degrees | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 87
0 | SWSV001 | 2 | Duct Seal, Residential | Any | Any | Any |  | EECP | 13 | • An assessment and report are required in accordance with Air Conditioning Contractors of America (ACCA) Standard 48 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations. | Yes |  | Report been submitted in accordance with ACCA Standard 4 prior to any treatments being applied? | Drop Down List | Yes;No; | [7 empty] | If 'QM Eligibility' is Yes then Must be 'Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, review the submitted documentation in EECP | Ensure the installation report or other documentation clearly indicates the HVAC system is functional and not in need of any major repairs prior to the measures being installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 96
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | An installation report should indicate the work performed and show Duct Seal and testing specifications for the HVAC system including existing and proposed leakage rates | The manufacturer may be listed as the implementer or contractor who performed the work or the product used to perform the sealing | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | An installation report should indicate the work performed and show Duct Seal and testing specifications for the HVAC system including existing and proposed leakage rates | The model number may be listed as the implementer or contractor who performed the work or the product used to perform the sealing | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 3 | This measure is applicable for any existing single family, multifamily with two or more units, or mobile home that uses air-cooled, direct expansion (DX) cooling and gas heating, heat pump, or gas heating with no cooling. To confirm that the correct vintage savings are being used, the building age should be verified. See below for details on DEER 2020 vintage years for Old and Median (Existing) vintage buildings : | Yes |  | Building Vintage (construction year) | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | New measure property | 2021-06-21 | Kenny Liljestrom |  | Add | 36
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 4 | This measure is applicable for any existing single family, multifamily with two or more units, or mobile home that uses air-cooled, direct expansion (DX) cooling and gas heating, heat pump, or gas heating with no cooling. | Yes |  | What type of HVAC system does the customer have? | Drop Down List | Air-cooled direct expansion (DX) cooling and gas heating;Heat pump;Gas heating with no cooling;Other; | [7 empty] | Must not be 'Other' | QA Checklist | An installation report should indicate the type of HVAC system the customer has | HVAC system type should match EECP and be one of the following: Air-cooled direct expansion (DX) cooling and gas heating, Heat pump, or Gas heating with no cooling | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-06-21 | Kenny Liljestrom |  | Add | 48
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 5 | In order to verify compliance with measure requirements and the correct measure selection, the following information must be collected for each installation: • Building information such as: building type, vintage (year), and climate zone • HVAC System type, capacity in tons (for systems with cooling) or kBtuh (for systems with no heating), make and model number • Duct testing information include: o Type of duct test conducted o Pre and post install duct leakage rate percentages o Duct sealing material used | Yes |  | HVAC System Cooling Capacity (tons) | Numeric Value | [9 empty] | Inspections | Photograph the condenser unit (outdoor unit) nameplate to capture the make, model, and cooling capacity (Btu/hr or tons) | The value listed in EECP should match the cooling capacity listed on the nameplate; to convert from Btu/hr to tons use the following formula: Cooling Capacity (Btu/hr) / 12,000 (Btu/ton) = Tons of cooling | QA Checklist | Use photographs or an installation report to determine the cooling capacity of the HVAC system; this can be done by using the make and model to locate the manufacturer spec sheet or the information may be present in an installation report | The value listed in EECP should match the cooling capacity (Btu/hr or tons) listed on the nameplate or in the spec sheet; to convert from Btu/hr to tons use the following formula: Cooling Capacity (Btu/hr) / 12,000 (Btu/ton) = Tons of cooling | New measure property | 2021-06-21 | Kenny Liljestrom |  | Add | 35
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 6 | In order to verify compliance with measure requirements and the correct measure selection, the following information must be collected for each installation: • Building information such as: building type, vintage (year), and climate zone • HVAC System type, capacity in tons (for systems with cooling) or kBtuh (for systems with no heating), make and model number • Duct testing information include: o Type of duct test conducted o Pre and post install duct leakage rate percentages o Duct sealing material used | Yes |  | Heating System Capacity (kBtuh) | Numeric Value | [9 empty] | QA Checklist | Photograph the heating unit nameplate to capture the make, model, and heating capacity (Btu/hr or kBtu/hr) | The value listed in EECP should match the heating capacity listed on the nameplate; to convert from Btu/hr to kBtu/hr use the following formula: Heating Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Heating Capacity (kBtu/hr) | QA Checklist | Use photographs or an installation report to determine the heating capacity of the HVAC system; this can be done by using the make and model to locate the manufacturer spec sheet or the information may be present in an installation report | The value listed in EECP should match the heating capacity (Btu/hr) listed on the nameplate or in the spec sheet; to convert from Btu/hr to kBtu/hr use the following formula: Cooling Capacity (Btu/hr) / 1,000 (Btu/kBtu) = Heating Capacity (kBtu/hr) | New measure property | 2021-06-21 | Kenny Liljestrom |  | Add | 31
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 7 | Up to two duct tests must be conducted: the first or “test-in” is a system check to determine whether the duct system tightness meets the California Title 24 specifications. | Yes |  | Test-in Duct Leakage Rate (%) | Numeric Value | [9 empty] | QA Checklist | An installation report should indicate the test-in leakage rate | The test-in leakage rate should be greater than or equal to the measure case leakage rate and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 29
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 8 | If the Test-in shows that duct leakage exceeds minimum tightness specifications, and the technicians correct the situation, then a second test or “test-out” must be conducted to verify proper duct tightness was achieved. | Yes |  | Test-out Duct Leakage Rate (%) | Numeric Value | [9 empty] | QA Checklist | An installation report should indicate the test-out leakage rate | The test-out leakage rate should be less than or equal to the measure case leakage rate and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 30
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 9 | If some or all of the existing ductwork is beyond repair and sections must be replaced, the sections that must be replaced must be less than 40 linear feet in total per Section 150.2(b) of the 2019 California Building Energy Efficiency Standards (Title 24) | Yes |  | Length of ductwork replaced (linear feet) | Numeric Value | [9 empty] | Inspections | Photograph of the ductwork showing repairs or replacements in the ducting system | Document or estimate the amount of ductwork replaced | QA Checklist | An installation report should indicate, if any, the length of the duct work replaced as part of the project | The duct work length in the installation report should match what is listed in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 41
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 10 | ...or the replaced ductwork must be installed and tested in accordance with the applicable requirements in 2019 Title 24 Section 150.2(b)1D | Yes |  | Ductwork installed and tested in accordance with requirements in 2019 Title 24 Section 150.2(b)1D? | Drop Down List | Yes;No;N/A; | [7 empty] | Must be 'Yes' or 'N/A' | QA Checklist | If the length of ductwork replaced is greater than 40-linear feet, the implementer should supply the Title-24 compliance sheets as part of the documentation | If the ductwork length is greater than 40 feet, EECP documents need to have Title-24 compliance sheets have been submitted as part of this upload | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 98
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 11 | To identify these measures as part of an existing HVAC system, the program implementer must record existing duct leakage through comprehensive field testing. The testing can be performed while the system is pressurized using a duct blower fan to ensure the target leakage thresholds are achieved. Duct sealing shall be performed on the unpressurized system. After installation, testing shall be performed to ensure the target leakage thresholds are achieved. Photos and test results can serve as documentation that the work was performed on an existing HVAC system. | Yes |  | Has photographic evidence or documentation of the test-in and test-out procedures been uploaded? | Drop Down List | Yes;No; | [7 empty] | Must be ''Yes' | QA Checklist | Check either EECP or an installation report for photographs of the test-in and test-out procedures or results | Photographs of the test-in and test-out leakage rates needs to be included in the submitted documentation | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 96
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 12 | Per Resolution E-5082 “duct connections must not be sealed with duct tape (cloth-backed rubber adhesive tapes). Mastic or aerosol sealant materials are preferred, and butyl tape can be used where mastic or aerosol are impractical.” | Yes |  | Duct sealant material | Drop Down List | Mastic;Aerosol;Butyl tape | [7 empty] | Must be Yes | QA Checklist | Use the manufacturer spec sheet to validate the type of material used for the duct sealant | The material type listed in EECP should match what is listed in the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | New measure property | 2021-06-21 | Kenny Liljestrom |  | Add | 21
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 13 | Programs often bundle Quality Maintenance (QM) measures. The following prerequisites must be met before the QM treatments, such as airflow adjustments, can be implemented to ensure an HVAC system is running optimally. | Yes | QM Eligibility | Are other Quality Maintenance (QM) measures (i.e. airflow adjustments) being installed with this measure? | Drop Down List | Yes;No; | [8 empty] | QA Checklist | If implementer answers 'Yes', check the measures installed as part of the enrollment and via double-dip report | EECP should not indicate the customer has installed QM measures previously | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-05 | Kenny Liljestrom |  | Add | 105
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 14 | • The unit must be drawing power. | Yes |  | QM1: Is the HVAC system drawing power? | Drop Down List | Yes;No;N/A | [7 empty] | If 'QM Eligibility' is Yes then Must be ''Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, ensure the installation report shows the HVAC system as being functional prior to any work being performed | The installation report must show the HVAC system as being functioning prior to any adjustments/measures being installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 38
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 15 | • The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted. | Yes |  | QM2: For refrigerant charge adjustments, does the unit deliver supply air of at least 350 cfm/ton? | Drop Down List | Yes;No;N/A; | [7 empty] | If 'QM Eligibility' is Yes then must be 'Yes' or 'N/A' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, ensure the installation report shows the HVAC system having a tested airflow supply rate of greater than or equal to 350 cfm/ton | Using the equation below, determine if the supply airflow is >= 350 cfm/ton: supply air flow, cfm / tonnage of HVAC system = airflow rate per ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 98
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 16 | • The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees. | Yes |  | QM3: Does the unit have a condenser over ambient temperature (COAT) of at least 3 degrees F? | Drop Down List | Yes;No;N/A | [7 empty] | If 'QM Eligibility' is Yes then Must be 'Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, ensure the installation report shows the condenser over ambient temperature (COAT) | Ensure the COAT is greater than or equal to 3 degrees | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 92
1 | SWSV001 | 3 | Duct Seal, Residential | Any | Any | Any |  | EECP | 17 | • An assessment and report are required in accordance with Air Conditioning Contractors of America (ACCA) Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations. | Yes |  | QM4: Has a report been submitted meeting ACCA Standard 4 prior to any treatments being applied? | Drop Down List | Yes;No;N/A | [7 empty] | If 'QM Eligibility' is Yes then Must be 'Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, ensure the installation report or other documentation shows reference to the steps in the ACCA 4 Standard | ACCA Standard 4 items that need to be Include are: a. Inspect for particulate accumulation on filters b. Inspect air filter housing integrity and air seal c. Inspect grilles, registers, diffusers, and trunk/branch balancing dampers for dirt accumulation d. Inspect all accessible ductwork for areas of moisture accumulation or biological growth e. Inspect integrity of all accessible ductwork insulation f. Inspect integrity of all accessible ductwork including: duct strapping, hangers, sections, joints, and seams | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom |  | Add | 95
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | An installation report should indicate the sealant manufacturer, implementer, or contractor who performed the work | So long as the field is not blank, it is valid | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 12
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | An installation report should indicate the sealant manufacturer, implementer, or contractor who performed the work | So long as the field is not blank, it is valid | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 5
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any |  | EECP | 3 | This measure is applicable for any existing single family, multifamily with two or more units, or mobile home that uses air-cooled, direct expansion (DX) cooling and gas heating, heat pump, or gas heating with no cooling. | Yes |  | Building type | Drop Down List | Single Family;Multifamily;Mobile home; | [8 empty] | Inspections | Document the type of residence the unit was installed in (Single Family Home, Multifamily, or Mobile Home) | The building type listed in EECP should match the building type during the inspection | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 13
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any |  | EECP | 4 | To confirm that the correct vintage savings are being used, the building age should be verified. See below for details on DEER 2020 vintage years for Old and Median (Existing) vintage buildings: • Old: Before 2002 for non-mobile homes, before 1995 for mobile homes • Median (Existing): 2002 to 2016 for non-mobile homes, 1995 to 2005 for mobile homes | Yes |  | Building vintage | Drop Down List | Old: Before 2002 for non-mobile homes, before 1995 for mobile homes;Median: 2002 to 2016 for non-mobile homes, 1995 to 2005 for mobile homes; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | This has only two drop-down options but they are defined differently (very dumb) so we cannot separate the drop-down options | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 16
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any |  | EECP | 5 | This measure is applicable for any existing single family, multifamily with two or more units, or mobile home that uses air-cooled, direct expansion (DX) cooling and gas heating, heat pump, or gas heating with no cooling. | Yes |  | What type of HVAC system does the customer have? | Drop Down List | Air-cooled direct expansion (DX) cooling and gas heating;Heat pump;Gas heating with no cooling; | [8 empty] | Inspections | Photograph the outdoor HVAC system nameplate to capture the manufacturer and model number | The make and model can be compared to the equipment specification sheet to identify the HVAC system type; this can be done by processing | QA Checklist | An installation report should indicate the type of HVAC system the customer has; if data is collected by the inspections team, use the HVAC make and model number to locate a manufacturer specification sheet to determine the HVAC equipment type | The HVAC system type should match what is listed in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 48
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any |  | EECP | 6 | Up to two duct tests must be conducted: the first or “test-in” is a system check to determine whether the duct system tightness meets the California Title 24 specifications. | Yes | Test-In | Test-in Duct Leakage Rate (%) | Numeric Value | [9 empty] | QA Checklist | An installation report should indicate the test-in leakage rate | The test-in leakage rate should be greater than or equal to the measure case leakage rate and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 29
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any |  | EECP | 7 | If the Test-in shows that duct leakage exceeds minimum tightness specifications, and the technicians correct the situation, then a second test or “test-out” must be conducted to verify proper duct tightness was achieved. | Yes | Test-Out | Test-out Duct Leakage Rate (%) | Numeric Value | [9 empty] | QA Checklist | An installation report should indicate the test-out leakage rate | the test-out leakage rate should be less than or equal to the measure case leakage rate and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 30
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any |  | EECP | 8 | If some or all of the existing ductwork is beyond repair and sections must be replaced, the sections that must be replaced must be less than 40 linear feet in total per Section 150.2(b) of the 2019 California Building Energy Efficiency Standards (Title 24) | Yes | Ductwork Length | Length of ductwork replaced (linear feet) | Numeric Value | [9 empty] | Inspections | Photograph of the ductwork showing repairs or replacements in the ducting system | Document or estimate the amount of ductwork replaced | QA Checklist | An installation report should indicate, if any, the length of the duct work replaced as part of the project | The duct work length in the installation report should match what is listed in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 41
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any |  | - | 9 | ...or the replaced ductwork must be installed and tested in accordance with the applicable requirements in 2019 Title 24 Section 150.2(b)1D | No | Ductwork Code Requirement | Ductwork installed and tested in accordance with requirements in 2019 Title 24 Section 150.2(b)1D? | Drop Down List | Yes;No;N/A; | [7 empty] | Must be 'Yes' or 'N/A' | QA Checklist | If the length of ductwork replaced is greater than 40-linear feet, the implementer should supply the Title-24 compliance sheets as part of the documentation | If the ductwork length is greater than 40 feet, EECP documents need to have Title-24 compliance sheets have been submitted as part of this upload | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Property removed since contractors and implementors are required to install within local and state codes | Add | 98
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any |  | EECP | 10 | To identify these measures as part of an existing HVAC system, the program implementer must record existing duct leakage through comprehensive field testing. The testing can be performed while the system is pressurized using a duct blower fan to ensure the target leakage thresholds are achieved. Duct sealing shall be performed on the unpressurized system. After installation, testing shall be performed to ensure the target leakage thresholds are achieved. Photos and test results can serve as documentation that the work was performed on an existing HVAC system. | Yes | Duct Leakage | Has photographic evidence or documentation of the test-in and test-out procedures been uploaded? | Drop Down List | Yes;No; | [7 empty] | Must be ''Yes' | QA Checklist | Check either EECP or an installation report for photographs of the test-in and test-out procedures or results | Photographs of the test-in and test-out leakage rates needs to be included in the submitted documentation | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 96
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any |  | EECP | 11 | Programs often bundle Quality Maintenance (QM) measures. The following prerequisites must be met before the QM treatments, such as airflow adjustments, can be implemented to ensure an HVAC system is running optimally. | Yes | QM Eligibility | Are other Quality Maintenance (QM) measures (i.e. airflow adjustments) being installed with this measure? | Drop Down List | Yes;No; | [8 empty] | QA Checklist | If implementer answers 'Yes', check the measures installed as part of the enrollment and via double-dip report | EECP should not indicate the customer has installed QM measures previously | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 105
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any |  | EECP | 12 | • The unit must be drawing power. | Yes | Power Check | QM1: Is the HVAC system drawing power? | Drop Down List | Yes;No;N/A | [7 empty] | If 'QM Eligibility' is Yes then Must be ''Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, ensure the installation report shows the HVAC system as being functional prior to any work being performed | The installation report must show the HVAC system as being functioning prior to any adjustments/measures being installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 38
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any |  | EECP | 13 | • The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted. | Yes |  | QM2: For refrigerant charge adjustments, does the unit deliver supply air of at least 350 cfm/ton? | Drop Down List | Yes;No;N/A; | [7 empty] | If 'QM Eligibility' is Yes then must be 'Yes' or 'N/A' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, ensure the installation report shows the HVAC system having a tested airflow supply rate of greater than or equal to 350 cfm/ton | Using the equation below, determine if the supply airflow is >= 350 cfm/ton: supply air flow, cfm / tonnage of HVAC system = airflow rate per ton | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 98
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any |  | EECP | 14 | • The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees. | Yes |  | QM3: Does the unit have a condenser over ambient temperature (COAT) of at least 3 degrees F? | Drop Down List | Yes;No;N/A | [7 empty] | If 'QM Eligibility' is Yes then Must be 'Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, ensure the installation report shows the condenser over ambient temperature (COAT) | Ensure the COAT is greater than or equal to 3 degrees | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 92
0 | SWSV001 | 4 | Duct Seal, Residential | Any | Any | Any |  | EECP | 15 | • An assessment and report are required in accordance with Air Conditioning Contractors of America (ACCA) Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations. | Yes |  | QM4: Has a report been submitted meeting ACCA Standard 4 prior to any treatments being applied? | Drop Down List | Yes;No;N/A | [7 empty] | If 'QM Eligibility' is Yes then Must be 'Yes' | QA Checklist | If the implementer answered 'Yes' to other Quality Maintenance Measures being installed, ensure the installation report or other documentation shows reference to the steps in the ACCA 4 Standard | ACCA Standard 4 items that need to be Include are: a. Inspect for particulate accumulation on filters b. Inspect air filter housing integrity and air seal c. Inspect grilles, registers, diffusers, and trunk/branch balancing dampers for dirt accumulation d. Inspect all accessible ductwork for areas of moisture accumulation or biological growth e. Inspect integrity of all accessible ductwork insulation f. Inspect integrity of all accessible ductwork including: duct strapping, hangers, sections, joints, and seams | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-05 | Kenny Liljestrom | Measure active 1/1/2022 | Add | 95
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Make | Make | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 4
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 5
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any |  | EECP | 3 | Legacy property, set to expire 12/31/21 | Yes | Actual QTY | Cap-Tons | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any |  | EECP | 4 | Legacy property, set to expire 12/31/21 | Yes | Base Case Measure Code | Base Case Measure Code | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 22
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any |  | EECP | 5 | Legacy property, set to expire 12/31/21 | Yes | Base Case Measure Description | Base Case Measure Description | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 29
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any |  | EECP | 6 | Legacy property, set to expire 12/31/21 | Yes | Cap-Tons | Cap-Tons | Numeric Value | [9 empty] | Inspections | Photograph the outdoor HVAC system nameplate to capture the manufacturer, model number, and capacity (Btu/hr or tons) | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit | QA Checklist | Use an installation report to determine the capacity of the HVAC system; this can be found using the HVAC make and model and locating the specification sheet | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any |  | EECP | 7 | Legacy property, set to expire 12/31/21 | Yes | End Use | End Use | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 7
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any |  | EECP | 8 | Legacy property, set to expire 12/31/21 | Yes | Location | Location | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any |  | EECP | 12 | Legacy property, set to expire 12/31/21 | Yes | Refrigerant applied | Refrigerant successfully applied and meets manufacturer recommended levels | Drop Down List | Yes¦1;No¦0 | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 74
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any |  | EECP | 13 | Legacy property, set to expire 12/31/21 | Yes | Serial Number | Serial Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 13
1 | SWSV002 | 1 | Refrigerant Charge Adjustment, Commercial | Any | Any | Any |  | EECP | 14 | Legacy property, set to expire 12/31/21 | Yes | Size | Cap-Tons | Numeric Value | [9 empty] | Inspections | Photograph the outdoor HVAC system nameplate to capture the manufacturer, model number, and capacity (Btu/hr or tons) | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit | QA Checklist | Use an installation report to determine the capacity of the HVAC system; this can be found using the HVAC make and model and locating the specification sheet | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Make | Make | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 4
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 5
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 3 | Legacy property, set to expire 12/31/21 | Yes | Actual QTY | Cap-Tons | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 4 | Legacy property, set to expire 12/31/21 | Yes | Base Case Measure Code | Base Case Measure Code | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 22
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 5 | Legacy property, set to expire 12/31/21 | Yes | Base Case Measure Description | Base Case Measure Description | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 29
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 6 | Legacy property, set to expire 12/31/21 | Yes | Cap-Tons | Cap-Tons | Numeric Value | [9 empty] | Inspections | Photograph the outdoor HVAC system nameplate to capture the manufacturer, model number, and capacity (Btu/hr or tons) | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit | QA Checklist | Use an installation report to determine the capacity of the HVAC system; this can be found using the HVAC make and model and locating the specification sheet | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 7 | Legacy property, set to expire 12/31/21 | Yes | End Use | End Use | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 7
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 8 | Legacy property, set to expire 12/31/21 | Yes | Location | Location | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 12 | Legacy property, set to expire 12/31/21 | Yes | Refrigerant applied | Refrigerant successfully applied and meets manufacturer recommended levels | Drop Down List | Yes¦1;No¦0 | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 74
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 13 | Legacy property, set to expire 12/31/21 | Yes | Serial Number | Serial Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 13
0 | SWSV003 | 1 | Evaporator Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 14 | Legacy property, set to expire 12/31/21 | Yes | Size | Cap-Tons | Numeric Value | [9 empty] | Inspections | Photograph the outdoor HVAC system nameplate to capture the manufacturer, model number, and capacity (Btu/hr or tons) | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit | QA Checklist | Use an installation report to determine the capacity of the HVAC system; this can be found using the HVAC make and model and locating the specification sheet | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Make | Make | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 4
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 5
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 3 | Legacy property, set to expire 12/31/21 | Yes | Actual QTY | Cap-Tons | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 4 | Legacy property, set to expire 12/31/21 | Yes | Base Case Measure Code | Base Case Measure Code | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 22
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 5 | Legacy property, set to expire 12/31/21 | Yes | Base Case Measure Description | Base Case Measure Description | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 29
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 6 | Legacy property, set to expire 12/31/21 | Yes | Cap-Tons | Cap-Tons | Numeric Value | [9 empty] | Inspections | Photograph the outdoor HVAC system nameplate to capture the manufacturer, model number, and capacity (Btu/hr or tons) | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit | QA Checklist | Use an installation report to determine the capacity of the HVAC system; this can be found using the HVAC make and model and locating the specification sheet | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 7 | Legacy property, set to expire 12/31/21 | Yes | End Use | End Use | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 7
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 8 | Legacy property, set to expire 12/31/21 | Yes | Location | Location | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 12 | Legacy property, set to expire 12/31/21 | Yes | Refrigerant applied | Refrigerant successfully applied and meets manufacturer recommended levels | Drop Down List | Yes¦1;No¦0 | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 74
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 13 | Legacy property, set to expire 12/31/21 | Yes | Serial Number | Serial Number | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-08-05 | Kenny Liljestrom |  | Add | 13
1 | SWSV004 | 1 | Condenser Coil Cleaning, Commercial | Any | Any | Any |  | EECP | 14 | Legacy property, set to expire 12/31/21 | Yes | Size | Cap-Tons | Numeric Value | [9 empty] | Inspections | Photograph the outdoor HVAC system nameplate to capture the manufacturer, model number, and capacity (Btu/hr or tons) | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit | QA Checklist | Use an installation report to determine the capacity of the HVAC system; this can be found using the HVAC make and model and locating the specification sheet | The make and model can be used to locate the equipment specification sheet to identify the HVAC system capacity; the cap-tons can also be calculated by taking the capacity (Btu/hr) and dividing by 12,000 ex: Capacity 24,000 Btu/hr / 12,000 Btu/ton = 2-ton unit |  | 2021-08-05 | Kenny Liljestrom |  | Add | 8
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | An invoice or installation report should indicate the Refrigerant type, the manufacturer of the refrigerant, or the implementer who performed the work | The manufacturer may be listed as the implementer or contractor who performed the work, the refrigerant type used, or the refrigerant manufacturer | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | An invoice or installation report should indicate the Refrigerant type, the manufacturer of the refrigerant, or the implementer who performed the work | The model number may be listed as the implementer or contractor who performed the work, the refrigerant type used, or the refrigerant manufacturer | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any |  | EECP | 3 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Air Flow Rate | After implementation air flow rate? (cfm/ton) | Numeric Value | [8 empty] | Must be >= 350 | QA Checklist | An installation report should indicate the airflow rate after the refrigerant charge adjustment | The value should be above 350 cfm/ton 350 * tonnage of HVAC system = airflow rate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any |  | EECP | 4 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Operational | Is the unit operational? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Inspect both the outdoor and indoor HVAC systems | Ensure both units are energized and functional | QA Checklist | The installation report should indicate the HVAC system was operational in the existing conditions performance data; i.e. airflows, power draw, etc. should not be zero | An installation report should indicate the airflow rate after the refrigerant charge adjustment |  | 2021-06-21 | Kenny Liljestrom |  | Add | 24
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any |  | EECP | 5 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | COAT | Before implementation condenser over ambient temperature (COAT) ? (degrees) | Numeric Value | [8 empty] | Must be >= 3 | QA Checklist | Review the submitted installation report or documentation in EECP for the condenser over ambient temperature (COAT) | Ensure the installation report shows the COAT is greater than or equal to 3 degrees | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 75
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any |  | EECP | 6 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Assessment_Report | Before implementation of the measure was an assessment and report created in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Review the submitted installation report or documentation in EECP for ACCA Standard 4 requirements being met | The installation report or other documentation should clearly indicates the HVAC system is functional and not in need of any major repairs prior to the measures being installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label to change 'ACCA Standard 43' to 'ACCA Standard 4' | 2021-06-21 | Kenny Liljestrom |  | Add | 228
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any |  | EECP | 7 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | QM Service Agreement | Has Customer agreed to the QM Service Agreement? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | A service agreement or signed contract with the customer should be included in the submitted documentation | The document should indicate the customer has agreed to future quality maintenance performed at their residence (no requirement for the length or number of services performed) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 48
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any |  | EECP | 8 | This measure is applicable for residential single family, multifamily, and double-wide mobile homes that use central air-cooled direct expansion (DX) cooling and gas heating. | Yes | DX Cooling_Gas Heat | Does premise have central air-cooled direct expansion (DX) cooling and gas heating? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the make and model of the HVAC system and furnace to determine the HVAC system type | The system type is limited to Direct Expansion (DX) cooling and gas heating | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 83
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any |  | EECP | 9 | The contractor must provide the amount and percent refrigerant charge added to or removed from the system to verify the applicable measure. | Yes |  | Amount of refrigerant added or removed | Numeric Value | [9 empty] | QA Checklist | Review the installation report to validate the amount of refrigerant added or removed | The installation report should indicate the amount (in lbs) of the refrigerant added or removed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-25 | Kenny Liljestrom |  | Add | 38
0 | SWSV006 | 1 | Refrigerant Charge Adjustment, Residential | Any | Any | Any |  | EECP | 10 | The contractor must provide the amount and percent refrigerant charge added to or removed from the system to verify the applicable measure. | Yes |  | Percent of refrigerant added or removed | Numeric Value | [9 empty] | QA Checklist | Review the installation report to validate the percent of refrigerant added or removed | The installation report should indicate the percent of the refrigerant added or removed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-25 | Kenny Liljestrom |  | Add | 39
1 | SWSV007 | 1 | Condenser Coil Cleaning, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | An installation report should indicate the implementer or contractor who performed the work | The manufacturer may be listed as the implementer or contractor who performed the work | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
1 | SWSV007 | 1 | Condenser Coil Cleaning, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | An installation report should indicate the implementer or contractor who performed the work | The model number may be listed as the implementer or contractor who performed the work | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
1 | SWSV007 | 1 | Condenser Coil Cleaning, Residential | Any | Any | Any |  | EECP | 3 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Air Flow Rate | After implementation air flow rate? (cfm/ton) | Numeric Value | [8 empty] | Must be >= 350 | QA Checklist | An installation report should indicate the airflow rate after the refrigerant charge adjustment | The value should be above 350 cfm/ton 350 * tonnage of HVAC system = airflow rate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
1 | SWSV007 | 1 | Condenser Coil Cleaning, Residential | Any | Any | Any |  | EECP | 4 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Operational | Is the unit operational? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Inspect both the outdoor and indoor HVAC systems | Ensure both units are energized and functional | QA Checklist | The installation report should indicate the HVAC system was operational in the existing conditions performance data; i.e. airflows, power draw, etc. should not be zero | An installation report should indicate the airflow rate after the refrigerant charge adjustment |  | 2021-06-21 | Kenny Liljestrom |  | Add | 24
1 | SWSV007 | 1 | Condenser Coil Cleaning, Residential | Any | Any | Any |  | EECP | 5 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | COAT | Before implementation condenser over ambient temperature (COAT) ? (degrees) | Numeric Value | [8 empty] | Must be >= 3 | QA Checklist | Review the submitted installation report or documentation in EECP for the condenser over ambient temperature (COAT) | Ensure the installation report shows the COAT is greater than or equal to 3 degrees | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 75
1 | SWSV007 | 1 | Condenser Coil Cleaning, Residential | Any | Any | Any |  | EECP | 6 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Assessment_Report | Before implementation of the measure was an assessment and report created in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Review the submitted installation report or documentation in EECP for ACCA Standard 4 requirements being met | The installation report or other documentation should clearly indicates the HVAC system is functional and not in need of any major repairs prior to the measures being installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Update property label to change 'ACCA Standard 43' to 'ACCA Standard 4' | 2021-06-21 | Kenny Liljestrom |  | Add | 228
1 | SWSV007 | 1 | Condenser Coil Cleaning, Residential | Any | Any | Any |  | EECP | 7 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | QM Service Agreement | Has Customer agreed to the QM Service Agreement? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | A service agreement or signed contract with the customer should be included in the submitted documentation | The document should indicate the customer has agreed to future quality maintenance performed at their residence (no requirement for the length or number of services performed) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 48
1 | SWSV007 | 1 | Condenser Coil Cleaning, Residential | Any | Any | Any |  | EECP | 8 | This measure is applicable for residential single family, multifamily, and double-wide mobile homes that use central air-cooled direct expansion (DX) cooling and gas heating. | Yes | DX Cooling_Gas Heat | Does premise have central air-cooled direct expansion (DX) cooling and gas heating? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the make and model of the HVAC system and furnace to determine the HVAC system type | The system type is limited to Direct Expansion (DX) cooling and gas heating | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 83
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | An installation report should indicate the implementer or contractor who performed the work | The manufacturer may be listed as the implementer or contractor who performed the work | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | An installation report should indicate the implementer or contractor who performed the work | The model number may be listed as the implementer or contractor who performed the work | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any |  | EECP | 3 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Air Flow Rate | After implementation air flow rate? (cfm/ton) | Numeric Value | [8 empty] | Must be >= 350 | QA Checklist | An installation report should indicate the airflow rate after the refrigerant charge adjustment | The value should be above 350 cfm/ton 350 * tonnage of HVAC system = airflow rate | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any |  | EECP | 4 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Operational | Is the unit operational? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Inspect both the outdoor and indoor HVAC systems | Ensure both units are energized and functional | QA Checklist | The installation report should indicate the HVAC system was operational in the existing conditions performance data; i.e. airflows, power draw, etc. should not be zero | An installation report should indicate the airflow rate after the refrigerant charge adjustment |  | 2021-06-21 | Kenny Liljestrom |  | Add | 24
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any |  | EECP | 5 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | COAT | Before implementation condenser over ambient temperature (COAT) ? (degrees) | Numeric Value | [8 empty] | Must be >= 3 | QA Checklist | Review the submitted installation report or documentation in EECP for the condenser over ambient temperature (COAT) | Ensure the installation report shows the COAT is greater than or equal to 3 degrees | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 75
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any |  | EECP | 6 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | Assessment_Report | Before implementation of the measure was an assessment and report created in accordance with ACCA Standard 43 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Review the submitted installation report or documentation in EECP for ACCA Standard 4 requirements being met | The installation report or other documentation should clearly indicates the HVAC system is functional and not in need of any major repairs prior to the measures being installed | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 229
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any |  | EECP | 7 | The following prerequisites must be met before the Quality Maintenance (QM) treatments, such as air flow adjustments, can be implemented:  The unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to air flow are completed and before refrigerant charge is tested and/or adjusted.  The unit must be drawing power.  The unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.  An assessment and report are required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop QM treatment recommendations.  The customer must agree to a QM Service Agreement. | Yes | QM Service Agreement | Has Customer agreed to the QM Service Agreement? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | A service agreement or signed contract with the customer should be included in the submitted documentation | The document should indicate the customer has agreed to future quality maintenance performed at their residence (no requirement for the length or number of services performed) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 48
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any |  | EECP | 8 | This measure is applicable for residential single family, multifamily, and double-wide mobile homes that use central air-cooled direct expansion (DX) cooling and gas heating. | Yes | DX Cooling_Gas Heat | Does premise have central air-cooled direct expansion (DX) cooling and gas heating? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Use the make and model of the HVAC system and furnace to determine the HVAC system type | The system type is limited to Direct Expansion (DX) cooling and gas heating | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 83
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any |  | EECP | 9 | Legacy property | Yes | End Use | End Use | Text Box | [9 empty] | - | - | - | - | - | - | Possibly Legacy, if not active, remove | 2021-06-21 | Kenny Liljestrom |  | Add | 7
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any |  | EECP | 10 | Legacy property | Yes | Location | Location | Text Box | [9 empty] | - | - | - | - | - | - | Possibly Legacy, if not active, remove | 2021-06-21 | Kenny Liljestrom |  | Add | 8
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any |  | EECP | 11 | Legacy property | Yes | Serial Number | Serial Number | Text Box | [9 empty] | - | - | - | - | - | - | Possibly Legacy, if not active, remove | 2021-06-21 | Kenny Liljestrom |  | Add | 13
0 | SWSV009 | 1 | Air Flow Adjustment, Residential | Any | Any | Any |  | EECP | 12 | Legacy property | Yes | Sticker Number | Sticker Number | Text Box | [9 empty] | - | - | - | - | - | - | Possibly Legacy, if not active, remove | 2021-06-21 | Kenny Liljestrom |  | Add | 14
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | Any | Any | Any |  | EECP | 1 | The Return Duct Retrofit measure shall be installed by a residential HVAC contractor in a mobile home where there is an existing open belly return with a supply system in the ceiling. The Crossover Duct Replacement measure shall be installed by a residential HVAC contractor in an extended mobile home where two or more sections of the home has been joined. The crossover duct connects the supply ducting of two or more sections. | Yes |  | Installation contractor | Text Box | [9 empty] | QA Checklist | Review the submitted installation report to verify the contractor used for the project | The contractor used on the project should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 23
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | A | Any | Any |  | EECP | 2 | The Return Duct Retrofit measure shall be installed by a residential HVAC contractor in a mobile home where there is an existing open belly return with a supply system in the ceiling. | Yes |  | Photograph of open belly return duct submitted? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Review the submitted files in EECP or the installation report for a photograph of the existing conditions at the site | The photograph should contain an open duct (a duct that does not return back to the HVAC unit) | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 47
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | B | Any | Any |  | EECP | 3 | The ducting must be deteriorated, damaged, or not installed correctly to be eligible for this measure. | Yes |  | Photograph showing deterioration, damage, or poor installation of crossover duct submitted? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Review the submitted files in EECP or the installation report for a photograph of the existing conditions at the site | The photograph must show the duct as being damaged, deteriorated, or having gaps indicating poor installation | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 91
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | C | Any | Any |  | EECP | 4 | The Return Duct Retrofit measure shall be installed by a residential HVAC contractor in a mobile home where there is an existing open belly return with a supply system in the ceiling. | Yes |  | Photograph of open belly return duct submitted? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Review the submitted files in EECP or the installation report for a photograph of the existing conditions at the site | The photograph should contain an open duct (a duct that does not return back to the HVAC unit) | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 47
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | D | Any | Any |  | EECP | 5 | The ducting must be deteriorated, damaged, or not installed correctly to be eligible for this measure. | Yes |  | Photograph showing deterioration, damage, or poor installation of crossover duct submitted? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Review the submitted files in EECP or the installation report for a photograph of the existing conditions at the site | The photograph must show the duct as being damaged, deteriorated, or having gaps indicating poor installation | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 91
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | A | Any | Any |  | EECP | 6 | Installed return ducts shall be made from either galvanized steel, tinplated steel, or aluminum, or shall be listed as Class 0 or Class 1 air ducts under Underwriters' Laboratories, Inc. Standard for Air Ducts, UL181-1972. | Yes |  | Replacement duct material | Drop Down List | Galvanized steel;Tinplated steel;Aluminium;Class 0 air duct;Class 1 air duct; | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-01-20 | Kenny Liljestrom |  |  | 25
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | B | Any | Any |  | EECP | 7 | Installed return ducts shall be made from either galvanized steel, tinplated steel, or aluminum, or shall be listed as Class 0 or Class 1 air ducts under Underwriters' Laboratories, Inc. Standard for Air Ducts, UL181-1972. | Yes |  | Replacement duct material | Drop Down List | Galvanized steel;Tinplated steel;Aluminium; | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-01-20 | Kenny Liljestrom |  |  | 25
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | C | Any | Any |  | EECP | 8 | Installed return ducts shall be made from either galvanized steel, tinplated steel, or aluminum, or shall be listed as Class 0 or Class 1 air ducts under Underwriters' Laboratories, Inc. Standard for Air Ducts, UL181-1972. | Yes |  | Replacement duct material | Drop Down List | Galvanized steel;Tinplated steel;Aluminium;Class 0 air duct;Class 1 air duct; | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-01-20 | Kenny Liljestrom |  |  | 25
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | D | Any | Any |  | EECP | 9 | Installed return ducts shall be made from either galvanized steel, tinplated steel, or aluminum, or shall be listed as Class 0 or Class 1 air ducts under Underwriters' Laboratories, Inc. Standard for Air Ducts, UL181-1972. | Yes |  | Replacement duct material | Drop Down List | Galvanized steel;Tinplated steel;Aluminium; | [8 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-01-20 | Kenny Liljestrom |  |  | 25
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | A | Any | Any |  | EECP | 10 | Return ducts in unconditioned spaces shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. | Yes | Return Duct | Is the return duct in a conditioned space? | Drop Down List | Yes;No; | [8 empty] | Inspections | Locate the ducting for the HVAC unit | Make note of the ducting location because it determines the eligibility of the thermal insulation measure property | QA Checklist | Use the submitted invoice or installation report to determine where the ducting is located | Make note of the ducting location because it determines the eligibility of the thermal insulation measure property |  | 2022-01-20 | Kenny Liljestrom |  |  | 42
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | B | Any | Any |  | EECP | 11 | The crossover duct shall be supported and or prevented from ground contact. If located in interior areas, not exposed to outdoor air, crossover ducts shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. If the crossover duct is installed in an area that is exposed to outdoor air, such as outside the building’s envelope, the ducts shall be insulated with material having effective thermal resistance (R) of not less than 8.0. | Yes | Duct Location | Crossover duct location | Drop Down List | Interior;Exterior; | [8 empty] | Inspections | Locate the ducting for the HVAC unit | Make note of the ducting location because it determines the eligibility of the thermal insulation measure property | QA Checklist | Use the submitted invoice or installation report to determine where the ducting is located | Make note of the ducting location because it determines the eligibility of the thermal insulation measure property |  | 2022-01-20 | Kenny Liljestrom |  |  | 23
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | C | Any | Any |  | EECP | 12 | Return ducts in unconditioned spaces shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. | Yes | Return Duct | Is the return duct in a conditioned space? | Drop Down List | Yes;No; | [8 empty] | Inspections | Locate the ducting for the HVAC unit | Make note of the ducting location because it determines the eligibility of the thermal insulation measure property | QA Checklist | Use the submitted invoice or installation report to determine where the ducting is located | Make note of the ducting location because it determines the eligibility of the thermal insulation measure property |  | 2022-01-20 | Kenny Liljestrom |  |  | 42
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | D | Any | Any |  | EECP | 13 | The crossover duct shall be supported and or prevented from ground contact. If located in interior areas, not exposed to outdoor air, crossover ducts shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. If the crossover duct is installed in an area that is exposed to outdoor air, such as outside the building’s envelope, the ducts shall be insulated with material having effective thermal resistance (R) of not less than 8.0. | Yes | Duct Location | Crossover duct location | Drop Down List | Interior;Exterior; | [8 empty] | Inspections | Locate the ducting for the HVAC unit | Make note of the ducting location because it determines the eligibility of the thermal insulation measure property | QA Checklist | Use the submitted invoice or installation report to determine where the ducting is located | Make note of the ducting location because it determines the eligibility of the thermal insulation measure property |  | 2022-01-20 | Kenny Liljestrom |  |  | 23
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | A | Any | Any |  | EECP | 14 | Return ducts in unconditioned spaces shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. | Yes |  | Return duct insulation thermal resistance (R) | Numeric Value | [8 empty] | If Return Duct is 'No' then Must be >= 4 | Inspections | Locate the ducting for the HVAC unit | If the return ducting is in a conditioned space, the ducting does not require insulation; If the return ducting is in an unconditioned space, the ducting must have insulation covering it | QA Checklist | Use the submitted invoice or installation report to determine where the ducting is located | If the return ducting is in a conditioned space, the ducting does not require insulation; If the return ducting is in an unconditioned space, the ducting must have insulation covering it and the thermal resistance rating (R) must be >= 4; the insulation rating can be determined with a submittal of the insulation specification sheet or statement in the installation report |  | 2022-01-20 | Kenny Liljestrom |  |  | 45
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | B | Any | Any |  | EECP | 15 | The crossover duct shall be supported and or prevented from ground contact. If located in interior areas, not exposed to outdoor air, crossover ducts shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. If the crossover duct is installed in an area that is exposed to outdoor air, such as outside the building’s envelope, the ducts shall be insulated with material having effective thermal resistance (R) of not less than 8.0. | Yes |  | Crossover duct insulation thermal resistance (R) | Numeric Value | [8 empty] | If Duct Location is Interior then must be >= 4 If Duct Location is Exterior then must be >= 8 | Inspections | Locate the ducting for the HVAC unit | If the return ducting is in a conditioned space, the ducting does not require insulation; If the return ducting is in an unconditioned space, the ducting must have insulation covering it | QA Checklist | Use the submitted invoice or installation report to determine where the ducting is located | If the return ducting is located in the interior of the mobile home, the ducting must have insulation covering it and the thermal resistance rating (R) must be >= 4; If the return ducting is located on the exterior of the mobile home, the ducting must have insulation covering it and the thermal resistance rating (R) must be >= 8; the insulation rating can be determined with a submittal of the insulation specification sheet or statement in the installation report |  | 2022-01-20 | Kenny Liljestrom |  |  | 48
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | C | Any | Any |  | EECP | 16 | Return ducts in unconditioned spaces shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. | Yes |  | Return duct insulation thermal resistance (R) | Numeric Value | [8 empty] | If Return Duct is 'No' then Must be >= 4 | Inspections | Locate the ducting for the HVAC unit | If the return ducting is in a conditioned space, the ducting does not require insulation; If the return ducting is in an unconditioned space, the ducting must have insulation covering it | QA Checklist | Use the submitted invoice or installation report to determine where the ducting is located | If the return ducting is in a conditioned space, the ducting does not require insulation; If the return ducting is in an unconditioned space, the ducting must have insulation covering it and the thermal resistance rating (R) must be >= 4; the insulation rating can be determined with a submittal of the insulation specification sheet or statement in the installation report |  | 2022-01-20 | Kenny Liljestrom |  |  | 45
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | D | Any | Any |  | EECP | 17 | The crossover duct shall be supported and or prevented from ground contact. If located in interior areas, not exposed to outdoor air, crossover ducts shall be insulated with material having an effective thermal resistance (R) of not less than 4.0. If the crossover duct is installed in an area that is exposed to outdoor air, such as outside the building’s envelope, the ducts shall be insulated with material having effective thermal resistance (R) of not less than 8.0. | Yes |  | Crossover duct insulation thermal resistance (R) | Numeric Value | [8 empty] | If Duct Location is Interior then must be >= 4 If Duct Location is Exterior then must be >= 8 | Inspections | Locate the ducting for the HVAC unit |  | QA Checklist | Use the submitted invoice or installation report to determine where the ducting is located | If the return ducting is located in the interior of the mobile home, the ducting must have insulation covering it and the thermal resistance rating (R) must be >= 4; If the return ducting is located on the exterior of the mobile home, the ducting must have insulation covering it and the thermal resistance rating (R) must be >= 8; the insulation rating can be determined with a submittal of the insulation specification sheet or statement in the installation report |  | 2022-01-20 | Kenny Liljestrom |  |  | 48
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | A | Any | Any |  | EECP | 18 | Belly return systems shall be verified by a pre and post total leakage duct test at 25 pascals on the return side of the duct system only. This shall be achieved by separating the supply from return side of the duct system by sealing at the air handler/furnace, typically at the filter slot to eliminate supply side leakage from the test. | Yes |  | Pre leakage rate (%) | Numeric Value | [8 empty] | Must be >= 50% | QA Checklist | Use the installation report to verify the pre-installation leakage rate of the system | The leakage rate should be listed as a percentage; if the percentage is not listed in the installation report, it can be determined by one of the following formulas: Leakage Rate (cfm) / Total Airflow Rate (cfm) = % Leakage Leakage Pressure / Total Pressure = % leakage The leakage rate must be >= 50% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 20
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | B | Any | Any |  | EECP | 19 | Belly return systems shall be verified by a pre and post total leakage duct test at 25 pascals on the return side of the duct system only. This shall be achieved by separating the supply from return side of the duct system by sealing at the air handler/furnace, typically at the filter slot to eliminate supply side leakage from the test. | Yes |  | Pre leakage rate (%) | Numeric Value | [8 empty] | Must be >= 35% | QA Checklist | Use the installation report to verify the pre-installation leakage rate of the system | The leakage rate should be listed as a percentage; if the percentage is not listed in the installation report, it can be determined by one of the following formulas: Leakage Rate (cfm) / Total Airflow Rate (cfm) = % Leakage Leakage Pressure / Total Pressure = % leakage The leakage rate must be >= 35% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 20
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | C | Any | Any |  | EECP | 20 | Belly return systems shall be verified by a pre and post total leakage duct test at 25 pascals on the return side of the duct system only. This shall be achieved by separating the supply from return side of the duct system by sealing at the air handler/furnace, typically at the filter slot to eliminate supply side leakage from the test. | Yes |  | Pre leakage rate (%) | Numeric Value | [8 empty] | Must be >= 50% | QA Checklist | Use the installation report to verify the pre-installation leakage rate of the system | The leakage rate should be listed as a percentage; if the percentage is not listed in the installation report, it can be determined by one of the following formulas: Leakage Rate (cfm) / Total Airflow Rate (cfm) = % Leakage Leakage Pressure / Total Pressure = % leakage The leakage rate must be >= 50% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 20
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | D | Any | Any |  | EECP | 21 | Belly return systems shall be verified by a pre and post total leakage duct test at 25 pascals on the return side of the duct system only. This shall be achieved by separating the supply from return side of the duct system by sealing at the air handler/furnace, typically at the filter slot to eliminate supply side leakage from the test. | Yes |  | Pre leakage rate (%) | Numeric Value | [8 empty] | Must be >= 35% | QA Checklist | Use the installation report to verify the pre-installation leakage rate of the system | The leakage rate should be listed as a percentage; if the percentage is not listed in the installation report, it can be determined by one of the following formulas: Leakage Rate (cfm) / Total Airflow Rate (cfm) = % Leakage Leakage Pressure / Total Pressure = % leakage The leakage rate must be >= 35% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 20
1 | SWSV013 | 2 | Duct Optimization, Mobile Home | Any | Any | Any |  | EECP | 22 | Belly return systems shall be verified by a pre and post total leakage duct test at 25 pascals on the return side of the duct system only. This shall be achieved by separating the supply from return side of the duct system by sealing at the air handler/furnace, typically at the filter slot to eliminate supply side leakage from the test. | Yes |  | Post leakage rate (%) | Numeric Value | [8 empty] | Must be <= 15% | QA Checklist | Use the installation report to verify the post-installation leakage rate of the system | The leakage rate should be listed as a percentage; if the percentage is not listed in the installation report, it can be determined by one of the following formulas: Leakage Rate (cfm) / Total Airflow Rate (cfm) = % Leakage Leakage Pressure / Total Pressure = % leakage The leakage rate must be <= 15% | EECP | Trust Implementer response in EECP | Trust implementer response in EECP |  | 2022-01-20 | Kenny Liljestrom |  |  | 21
0 | SWWH001 | 2 | Faucet Aerator, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWWH001 | 2 | Faucet Aerator, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWWH001 | 2 | Faucet Aerator, Residential | Any | Any | Any |  | EECP | 3 | The existing faucet must have a flow rate of at least 2.2 gpm. | Yes | Existing Flow Rate | Existing Flow Rate (gpm) | Numeric Value | [8 empty] | Must be >= 2.2 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 24
0 | SWWH001 | 2 | Faucet Aerator, Residential | Any | Any | Any |  | EECP | 4 | Revisit | Yes | Flow Rate | Flow Rate of Installed Unit (gpm) | Numeric Value | [9 empty] | QA Checklist | Cross check manufacturer and model number with flow rate | The flow rate of the installed unit must match the flow entered in EECP and be less than or equal to the flowrate required by the measure. | Inspections | Using a measuring cup or flow rate measuring device, fill the device for 6 seconds, record the amount of Oz of water in the device; gallons per minute can be calculated as: Measured Oz * 0.078125 = GPM | The flow rate of the installed unit must match the flow entered in EECP and be less than or equal to the flowrate required by the measure. |  | 2021-06-21 | Kenny Liljestrom |  | Add | 33
0 | SWWH001 | 2 | Faucet Aerator, Residential | Any | Any | Any |  | EECP | 5 | Revisit | Yes | Natural Gas WH | Does the facility utilize natural gas water heating equipment? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Locate the water heater for the building and determine if the unit is fueled by natural gas (yellow pipe) | The water heater must be fueled by natural gas | QA Checklist | A photograph of the water heater showing the yellow gas pipe; or the make and model of the water heater which can be cross referenced with the manufacturer specification sheet to identify of the unit is gas fired | The water heater must be fueled by natural gas |  | 2021-06-21 | Kenny Liljestrom |  | Add | 62
0 | SWWH001 | 2 | Faucet Aerator, Residential | Any | AR | Any |  | EECP | 6 | For accelerated replacement application types, the retrofit faucet must have an existing faucet aerator. For all other application types, the faucet must not have an aerator installed. | Yes | Existing Aerator | Does the faucet have an existing aerator installed? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | A photograph of the existing faucet aerator is sufficient documentation if available | Must be 'Yes' for AR measures and show an existing aerator | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-03-11 | Kenny Liljestrom | Updated to make the validation rules more clear | Add | 51
0 | SWWH001 | 2 | Faucet Aerator, Residential | Any | AOE | Any |  | EECP | 6 | For accelerated replacement application types, the retrofit faucet must have an existing faucet aerator. For all other application types, the faucet must not have an aerator installed. | Yes | Existing Aerator | Does the faucet have an existing aerator installed? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | QA Checklist | A photograph of the existing faucet aerator is sufficient documentation if available | An aerator must not be installed on the faucet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-03-11 | Kenny Liljestrom | Updated to make the validation rules more clear |  | 51
0 | SWWH001 | 2 | Faucet Aerator, Residential | Any | Any | Any |  | QA Checklist | 7 | The measure is not applicable to new faucets that meet or exceed the 2016 California Appliance Efficiency Regulations (Title 20) code requirement of 1.2 gpm flow rate for lavatory faucet and 1.8 gpm flow rate for kitchen faucet. | No | Title 20 | Was this measure installed on a new faucet that met or exceeded the 2016 California Appliance Efficiency Regulations (Title 20) code requirement of 1.2 gpm flow rate for lavatory faucet and 1.8 gpm flow rate for kitchen faucet? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Property label needs to be updated | 2022-03-11 | Kenny Liljestrom | Property removed since contractors and implementors are required to install within local and state codes | Add | 227
1 | SWWH002 | 2 | Low-Flow Showerhead - Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph of installed showerhead, if nameplate is visible on the threaded connector or showerhead, document or photograph the model number | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
1 | SWWH002 | 2 | Low-Flow Showerhead - Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph of installed showerhead, if nameplate is visible on the threaded connector or showerhead, document or photograph the model number | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
1 | SWWH002 | 2 | Low-Flow Showerhead - Residential | Any | Any | Any |  | EECP | 3 | Good to have | Yes | Existing Flow Rate | Existing Flow Rate (gpm) | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-06-21 | Kenny Liljestrom |  | Add | 24
1 | SWWH002 | 2 | Low-Flow Showerhead - Residential | Any | Any | Any |  | EECP | 4 | Good to have | Yes | Flow Rate | Flow Rate of Installed Unit (gpm) | Numeric Value | [9 empty] | Inspections | Using a measuring cup or flow rate measuring device, fill the device for 6 seconds, record the amount of Oz of water in the device; gallons per minute can be calculated as: Measured Oz * 0.078125 = GPM | The flow rate of the installed unit must match the flow entered in EECP and be less than or equal to the flowrate required by the measure. | QA Checklist | Cross check manufacturer and model number with flow rate | The flow rate of the installed unit must match the flow entered in EECP and be less than or equal to the flowrate required by the measure. | Request to remove | 2021-06-21 | Kenny Liljestrom |  | Add | 33
1 | SWWH002 | 2 | Low-Flow Showerhead - Residential | Any | Any | Any |  | EECP | 5 | Measure Description | Yes | Natural Gas WH | Does the facility utilize natural gas water heating equipment? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Locate the water heater for the building and determine if the unit is fueled by natural gas (yellow pipe) | The water heater must be fueled by natural gas | QA Checklist | Use the installation report to verify the type of water heater used to heat the domestic hot water | The water heater must be fueled by natural gas | Request to remove | 2021-06-21 | Kenny Liljestrom |  | Add | 62
1 | SWWH002 | 2 | Low-Flow Showerhead - Residential | Any | AR | Any |  | EECP | 6 | To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers • Customer/site information • Make/model of pre-existing equipment and/or • Performance/flowrate measurements of pre-existing equipment, and/or • Photograph of pre-existing equipment in place and operating | Yes | Preponderance of Evidence | Has required Preponderance of Evidence (POE) been submitted in accordance with the workpaper? | Drop Down List | Yes;No; | [7 empty] | Must be ''Yes' | QA Checklist | Review the POE documentation and determine if it is adequate based on required criteria. | Has required Preponderance of Evidence (POE) been submitted to include but not limited to: Targeted segment of the market or customers, customer/site information, make/model of pre-existing equipment and/or performance/flowrate measurements of pre-existing equipment and/or photograph of pre-existing equipment in place and operating, or one of the three alternatives listed in Section 7.3 of POEV 2.0? | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-25 | Kenny Liljestrom |  | Add | 93
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any |  | EECP | 3 | Thermostatic shower valve (TSV): Any TSV certified by applicable standards (e.g., ANSI, ASPE, etc.) is eligible. | Yes | Certified | Is the TSV certified by applicable standards (e.g., ANSI, ASPE, etc.) ? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Using the make and model, cross reference the ANSI or ASPE databases to ensure the model is listed | The make and model must be listed in one of the approved databases | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 71
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any |  | EECP | 4 | The make and model number and a copy of the customer receipt must be submitted with the application. | Yes | Receipt | Was a copy of the purchase receipt submitted? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Review the submitted documents in EECP | Ensure a copy of the receipt or invoice is included in the submitted documentation | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any |  | EECP | 5 | Good to have | Yes | Flow Rate | Flow Rate of Installed Unit (gpm) | Numeric Value | [9 empty] | QA Checklist | Use the manufacturer spec sheet to validate the flow rate of the newly installed unit | The flow rate listed in EECP should match what is on the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 33
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any |  | EECP | 6 | This measure is not applicable where recirculation pumps are used or where potential crossover between hot water and cold water may occur. | Yes | Recirculation Pump | Was the measure installed where recirculation pumps are used or where potential crossover between hot water and cold water may occur? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | Inspections | In the hot water piping system, near the water heater, document if there is a small pump that runs when the demand for water is off or zero | There should be only a small pump that is off unless there is a demand for hot water; a photograph of the hot water pump make and model number can also suffice | QA Checklist | Use the make and model of the hot water pump to determine if it is a recirculation pump or an on demand pump | The pump type should not be circulation or recirculation |  | 2021-06-21 | Kenny Liljestrom |  | Add | 133
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any |  | EECP | 7 | The measure is not applicable where tankless water heaters are used; instantaneous tankless water heaters may have different effect on savings with temperature-initiated flow-restriction valves. | Yes | Tankless | Does the facility utilize tankless water heaters? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | Inspections | Locate and photograph the water heater serving the domestic hot water systems (showers, faucets, etc.) | Ensure the water heater is not a tankless water heater (typically installed on a wall inside/outside of the garage) | QA Checklist | The make and model of the water heater may be provided in an installation report; the water heater type should not be instantaneous or tankless | The water heater type should not be instantaneous or tankless |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any |  | EECP | 8 | Measure Description | Yes | Natural Gas WH | Does the facility utilize natural gas water heating equipment? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Photograph the water heater showing the gas pipe (yellow pipe) going into the water heater | Determine if the water heater is fueled by natural gas (yellow pipe); the nameplate showing the make and model will also suffice | QA Checklist | The make and model of the water heater may be provided in an installation report | the water heater type should not be instantaneous or tankless |  | 2021-06-21 | Kenny Liljestrom |  | Add | 62
0 | SWWH003 | 1 | TSV with and without an Integrated Low-Flow Showerhead, Residential | Any | Any | Any |  | EECP | 9 | The measure is not applicable where the showerhead is installed in tub/shower combination systems. (However, note that the gross savings installation adjustment (GSIA) factor accounts for expected leakage. See Gross Savings Installation Adjustment.) | Yes |  | Is the showerhead is installed in tub/shower combination system? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | Inspections | Photograph the shower the thermostatic valve is installed in | The shower should not be a shower/tub combo | QA Checklist | Photographs from the implementer showing the configuration of the shower will show what type of shower the equipment is installed in | The shower should not be a shower/tub combo | Revisit | 2021-08-25 | Kenny Liljestrom |  | Add | 64
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any |  | EECP | 1 | - | No | Manufacturer | Manufacturer | Text Box | [9 empty] | - | - | - | - | - | - |  | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 12
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any |  | EECP | 2 | - | No | Model | Model | Text Box | [9 empty] | - | - | - | - | - | - |  | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 5
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any |  | EECP | 3 | - | No | LFR Served By Gas | Is the installed LFR served by natural gas water heating equipment? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - |  | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 67
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any |  | EECP | 4 | - | No | Existing Flow Rate | Existing flow rate (gpm) | Numeric Value | [9 empty] | - | - | - | - | - | - |  | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 24
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any |  | EECP | 5 | - | No | Flow Rate | Flow rate of installed unit (gpm) | Numeric Value | [9 empty] | - | - | - | - | - | - |  | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 33
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any |  | EECP | 6 | Eligibility requirements for the laminar flow restrictor measure include: • The device must be installed only in health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation/inspection requirements. • The device must meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation. • The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | No | LFR Labeled Vandal | Is the LFR labeled as “Vandal Proof” or can not be removed without a proprietary tool, except for dialysis and scrub sink locations? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - |  | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 132
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any |  | EECP | 7 | Eligibility requirements for the laminar flow restrictor measure include: • The device must be installed only in health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation/inspection requirements. • The device must meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation. • The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | No | Meets Code | Does the installed device meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - |  | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 115
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any |  | QA Checklist | 8 | Eligibility requirements for the laminar flow restrictor measure include: • The device must be installed only in health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation/inspection requirements. • The device must meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation. • The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | No |  | Is the device installed in a health care facility subject to the OSHPD code and regulation/inspection requirements? | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 115
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any |  | QA Checklist | 9 | Eligible building types for this measure are health care facilities and/or medical buildings of any vintage that adhere to the Office of Statewide Health Planning and Development (OSHPD) regulations in the State of California that also utilize natural gas-powered water heating equipment. These facilities include (but are not limited to): • Hospitals (large regional or local) • Emergency rooms • In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals • Doctor offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.) • Clinics and nursing homes | No |  | Is the facility: • Hospitals (large regional or local) • Emergency rooms • In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals • Doctor offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.) • Clinics and nursing homes | Drop Down List | Yes;No | [7 empty] | Must be Yes | - | - | - | - | - | - | Not configured in original upload | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 315
1 | SWWH004 | 1 | Laminar Flow Restrictor | Any | Any | Any |  | QA Checklist | 10 | New construction health care facilities are not eligible. | No |  | New Construction | Drop Down List | Yes;No | [7 empty] | Must be No | - | - | - | - | - | - | Not configured in original upload | 2021-07-12 | Kenny Liljestrom | Workpaper expired 3/20/21, no longer active | Add | 16
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 12
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 5
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any |  | EECP | 3 | Savings limited to gas fired water heaters only | Yes | LFR Served By Gas | Is the installed LFR served by natural gas water heating equipment? | Drop Down List | Yes;No | [7 empty] | Must be Yes | Inspections | Photograph the water heater showing the gas pipe (yellow pipe) going into the water heater | Determine if the water heater is fueled by natural gas (yellow pipe); the nameplate showing the make and model will also suffice | QA Checklist | The make and model of the water heater may be provided in an installation report | the water heater type should not be instantaneous or tankless |  | 2021-07-12 | Kenny Liljestrom |  | Add | 67
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any |  | EECP | 4 | good to have | Yes | Existing Flow Rate | Existing flow rate (gpm) | Numeric Value | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Can probably remove with measure case descriptions and QA checks | 2021-07-12 | Kenny Liljestrom |  | Add | 24
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any |  | EECP | 5 | Measure Description | Yes | Flow Rate | Flow rate of installed unit (gpm) | Numeric Value | [9 empty] | QA Checklist | Use the manufacturer spec sheet to validate the flow rate of the newly installed unit | The flow rate listed in EECP should match what is on the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Can probably remove with measure case descriptions and QA checks | 2021-07-12 | Kenny Liljestrom |  | Add | 33
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any |  | EECP | 6 | Eligibility requirements for the laminar flow restrictor measure include: • The device must be installed only in health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation/inspection requirements. • The device must meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation. • The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | Yes | LFR Labeled Vandal | Is the LFR labeled as “Vandal Proof” or can not be removed without a proprietary tool, except for dialysis and scrub sink locations? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Use the manufacturer spec sheet to determine if the unit is identified as a Vandal Proof model or requires a specialty tool to remove | The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 132
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any |  | EECP | 7 | Eligibility requirements for the laminar flow restrictor measure include: • The device must be installed only in health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation/inspection requirements. • The device must meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation. • The LFR must be labeled as “Vandal Proof” or must not be removable without a proprietary tool, except for dialysis and scrub sink locations. | Yes | Meets Code | Does the installed device meet the Office of Statewide Health Planning and Development (OSHPD) code and regulation? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-07-12 | Kenny Liljestrom |  | Add | 115
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any |  | QA Checklist | 9 | Eligible building types for this measure are health care facilities and/or medical buildings of any vintage that adhere to the Office of Statewide Health Planning and Development (OSHPD) regulations in the State of California that also utilize natural gas-powered water heating equipment. These facilities include (but are not limited to): • Hospitals (large regional or local) • Emergency rooms • In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals • Doctor offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.) • Clinics and nursing homes | Yes |  | Is the facility: • Hospitals (large regional or local) • Emergency rooms • In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals • Doctor offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.) • Clinics and nursing homes | Drop Down List | Yes;No | [7 empty] | Must be Yes | Inspections | Make note of the building type at the inspection site | The facility must be one of the following: • Hospitals (large regional or local) • Emergency rooms • In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals • Doctor offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.) • Clinics and nursing homes | QA Checklist | Use the installation report or EECP to determine the building type | Is the facility: • Hospitals (large regional or local) • Emergency rooms • In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals • Doctor offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.) • Clinics and nursing homes | Not configured in original upload | 2021-07-12 | Kenny Liljestrom |  | Add | 315
0 | SWWH004 | 2 | Laminar Flow Restrictor | Any | Any | Any |  | QA Checklist | 10 | New construction health care facilities are not eligible. | Yes |  | New Construction | Drop Down List | Yes;No | [7 empty] | Must be No | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-12 | Kenny Liljestrom |  | Add | 16
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-12 | Kenny Liljestrom |  | Add | 12
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-12 | Kenny Liljestrom |  | Add | 5
1 | SWWH005 | 3 | Boiler, Commercial | Any | AR | Any |  | EECP | 3 | For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers, Customer/site information, Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating | Yes |  | Has all Preponderance of Evidence (POE) been included as defined in the workpaper? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Review the submitted documentation for Preponderance of Evidence (POE) | For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers, Customer/site information, Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-12 | Kenny Liljestrom |  | Add | 82
1 | SWWH005 | 3 | Boiler, Commercial | Any | AR | Any |  | EECP | 5 | Good to have | No |  | Who was the party that filled out the POE documentation? | Drop Down List | Tenant;Owner;Owner Representative;Implementer; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-10-20 | Kenny Liljestrom | Implementers responsible for POE documentation | Add | 56
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any |  | EECP | 6 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description and must comply with emission limits per air district, if applicable. Note that Tier 2 & 3 hot water heaters are condensing and often require flue modifications to handle the condensate. • Only gas-for-gas replacement installations are eligible. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use. • Have an input rating of at least 4,000 Btu/hr/gal of stored water. | Yes | Emission Limits Boiler | Does the boiler installation comply with emission limits per air district, if applicable? (Note that Tier 2 hot water heaters are condensing and often require flue modifications to handle the condensate.) | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-05-28 | Kenny Liljestrom |  | Add | 204
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any |  | EECP | 7 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description and must comply with emission limits per air district, if applicable. Note that Tier 2 & 3 hot water heaters are condensing and often require flue modifications to handle the condensate. • Only gas-for-gas replacement installations are eligible. Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use. • Have an input rating of at least 4,000 Btu/hr/gal of stored water. | Yes | Replacing Gas_Gas | Replacing gas unit with gas unit? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | The installation report should indicate the existing conditions including the fuel type of the existing boiler | The existing and proposed boilers must be fueled by natural gas | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-05-28 | Kenny Liljestrom |  | Add | 33
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any |  | EECP | 8 | This measure does not include water heaters or hot water boilers used for space conditioning, industrial (process) end-use applications, pools, or spas. | Yes | Boiler Use | Is the hot water boiler used for space conditioning, industrial (process) end-use applications, pools, or spas? | Drop Down List | Yes;No | [7 empty] | Must be No | Inspections | While on site, ask the customer if this boiler is used for domestic hot water or for service (HVAC) hot water | The boiler must be used for domestic hot water (showerheads, faucets, etc.), not HVAC equipment or other processes | QA Checklist | The installation report should indicate what equipment the hot water boiler serves | The hot water boiler must serve the domestic hot water load at the facility (showers, faucets, etc.); the boiler can NOT serve HVAC systems or manufacturing processes |  | 2021-05-28 | Kenny Liljestrom | Moved to FAI to check by inspections team | Add | 111
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any |  | EECP | 10 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description and must comply with emission limits per air district, if applicable. Note that Tier 2 & 3 hot water heaters are condensing and often require flue modifications to handle the condensate. • Only gas-for-gas replacement installations are eligible. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use. • Have an input rating of at least 4,000 Btu/hr/gal of stored water. | Yes |  | Does the installed unit only provide hot water when there is a hot water draw from the end use? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-05-28 | Kenny Liljestrom | Moved to FAI to check by inspections team | Add | 95
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any |  | EECP | 11 | This measure cannot be used to supply hot water to a circulation loop without an intermediary hot water storage tank. | Yes | Circulation Loop | Does the boiler supply hot water to a circulation loop without an intermediary hot water storage tank? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-05-28 | Kenny Liljestrom |  | Add | 102
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any |  | EECP | 12 | Good to have | Yes | Size | Size (kBtu/hr) | Numeric Value | [9 empty] | Inspections | Photograph the nameplate showing the Input Rating (Btu/hr) of the unit | The Input Rating (Btu/hr) listed in EECP should match what is listed on the nameplate; to convert from Btu/hr to kBtu/hr use the following formula: Input Rating (Btu/hr) / 1,000 (Btu/kBtu) = Input Rating (kBtu/hr) | QA Checklist | Use the manufacturer spec sheet to validate the Input Rating (Btu/hr) | The Input Rating (Btu/hr) listed in EECP should match what is listed on the spec sheet; to convert from Btu/hr to kBtu/hr use the following formula: Input Rating (Btu/hr) / 1,000 (Btu/kBtu) = Input Rating (kBtu/hr) | Remove validation criteria | 2021-07-12 | Kenny Liljestrom |  | Add | 14
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any |  | EECP | 13 | Good to have | Yes | Energy Factor | Uniform Energy Factor | Numeric Value | [9 empty] | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor (UEF) | The UEF listed in EECP should match what is listed on the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Remove validation criteria | 2021-07-12 | Kenny Liljestrom |  | Add | 21
1 | SWWH005 | 3 | Boiler, Commercial | Any | Any | Any |  | EECP | 14 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description and must comply with emission limits per air district, if applicable. Note that Tier 2 & 3 hot water heaters are condensing and often require flue modifications to handle the condensate. • Only gas-for-gas replacement installations are eligible. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use. • Have an input rating of at least 4,000 Btu/hr/gal of stored water. | Yes | Input Rating | Input Rating (btu/hr/gallon of stored water) | Numeric Value | [8 empty] | Must be >=4000 | QA Checklist | Use the manufacturer spec sheet to validate the Input Rating (Btu/hr-gallon) | The Input Rating (Btu/hr-gallon) listed in EECP should match what is listed on the spec sheet; if not listed, the value can be calculated as: Input Rating (Btu/hr) / Storage Capacity (gallons) = Input Rating (Btu/hr-gallon) This value needs to be >= 4,000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Validation criteria needs to be updated to reflect the >= 4000 requirement | 2021-07-12 | Kenny Liljestrom |  | Add | 44
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-12 | Kenny Liljestrom |  | Add | 12
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-12 | Kenny Liljestrom |  | Add | 5
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | AR | Any |  | EECP | 3 | To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. | Yes |  | Was the customer approached directly by a direct installation implementer? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-12 | Kenny Liljestrom |  | Add | 74
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | AR | Any |  | EECP | 4 | For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. | Yes |  | Has all Preponderance of Evidence (POE) been submitted as defined by the workpaper? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Review the submitted documentation in EECP for POE | For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-12 | Kenny Liljestrom |  | Add | 83
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | AR | Any |  | EECP | 5 | Good to have | No |  | Who was the party that filled out the POE documentation? | Drop Down List | Tenant;Owner;Owner Representative;Implementer; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-10-20 | Kenny Liljestrom | Implementers responsible for POE documentation | Add | 56
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | A | Any | Any |  | EECP | 6 | Measure Description | Yes | Energy Factor | Uniform Energy Factor | Numeric Value | [8 empty] | Must be >= 0.81 | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor | The Uniform Energy Factor Must be >= 0.81 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 21
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | B | Any | Any |  | EECP | 7 | Measure Description | Yes | Energy Factor | Uniform Energy Factor | Numeric Value | [8 empty] | Must be >= 0.87 | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor | The Uniform Energy Factor Must be >= 0.87 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 21
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | C | Any | Any |  | EECP | 8 | Measure Description | Yes | EFFICIENCY | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 0.80% | QA Checklist | Use the manufacturer spec sheet to validate the Thermal Efficiency (%) | The Thermal Efficiency (%) Must be >= 0.80% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 22
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | D | Any | Any |  | EECP | 9 | Measure Description | Yes | EFFICIENCY | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 0.90% | QA Checklist | Use the manufacturer spec sheet to validate the Thermal Efficiency (%) | The Thermal Efficiency (%) Must be >= 0.90% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 22
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | E | Any | Any |  | EECP | 10 | Measure Description | Yes | EFFICIENCY | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 0.90% | QA Checklist | Use the manufacturer spec sheet to validate the Thermal Efficiency (%) | The Thermal Efficiency (%) Must be >= 0.90% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 22
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | F | Any | Any |  | EECP | 11 | Measure Description | Yes | EFFICIENCY | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 0.96% | QA Checklist | Use the manufacturer spec sheet to validate the Thermal Efficiency (%) | The Thermal Efficiency (%) Must be >= 0.96% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 22
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | Any | Any |  | EECP | 12 | Measure Description | Yes | Size | Size (kBtu/hr) | Numeric Value | [9 empty] | Inspections | Photograph the nameplate showing the Input Rating (Btu/hr) of the unit | The Input Rating (Btu/hr) listed in EECP should match what is listed on the nameplate; to convert from Btu/hr to kBtu/hr use the following formula: Input Rating (Btu/hr) / 1,000 (Btu/kBtu) = Input Rating (kBtu/hr) | QA Checklist | Use the manufacturer spec sheet to validate the Input Rating (Btu/hr) | The Input Rating (Btu/hr) listed in EECP should match what is listed on the spec sheet; to convert from Btu/hr to kBtu/hr use the following formula: Input Rating (Btu/hr) / 1,000 (Btu/kBtu) = Input Rating (kBtu/hr) |  | 2021-07-12 | Kenny Liljestrom |  | Add | 14
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | NR | Any |  | EECP | 13 | For normal replacement (NR) measure application type, only gas-for-gas replacements are eligible | Yes | Replacing Gas_Gas | Replacing gas unit with gas unit? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | The installation report should indicate the existing conditions including the fuel type of the existing boiler | The existing and proposed boilers must be fueled by natural gas | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 33
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | Any | Any |  | EECP | 14 | Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use • Have an input rating of at least 4,000 Btu/hr per gallon of stored water | Yes | Input Rating | Input Rating (btu/hr/gallon of stored water) | Numeric Value | [8 empty] | Must be >= 4000 | QA Checklist | Use the manufacturer spec sheet to validate the Input Rating (Btu/hr-gallon) | The Input Rating (Btu/hr-gallon) listed in EECP should match what is listed on the spec sheet; if not listed, the value can be calculated as: Input Rating (Btu/hr) / Storage Capacity (gallons) = Input Rating (Btu/hr-gallon) This value needs to be >= 4,000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-12 | Kenny Liljestrom |  | Add | 44
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | Any | Any |  | EECP | 15 | Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use • Have an input rating of at least 4,000 Btu/hr per gallon of stored water | Yes |  | Does the installed unit only provide hot water when there is a hot water draw from the end use? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-12 | Kenny Liljestrom |  | Add | 95
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | Any | Any |  | EECP | 16 | Meet the definition of a tankless water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water • Provide hot water only when there is a hot water draw from the end use • Have an input rating of at least 4,000 Btu/hr per gallon of stored water This measure does not include water heaters or hot water boilers used for space conditioning, industrial (process) end-use applications, pools, or spas. | Yes | Primary Use Domestic Water | Primarily used for domestic water? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | While on site, ask the customer if this boiler is used for domestic hot water or for service (HVAC) hot water | The boiler must be used for domestic hot water (showerheads, faucets, etc.), not HVAC equipment or other processes | QA Checklist | The installation report should indicate what equipment the hot water boiler serves | The hot water boiler must serve the domestic hot water load at the facility (showers, faucets, etc.); the boiler can NOT serve HVAC systems or manufacturing processes | Not configured in original upload | 2021-05-28 | Kenny Liljestrom |  | Add | 34
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | AR | Any |  | EECP | 17 | This measure cannot be used to supply hot water to a circulation loop without an intermediary hot water storage tank. | Yes |  | For hot water circulation loops, is there an intermediary hot water storage tank? | Drop Down List | Yes;No;N/A; | [7 empty] | Must be: Yes or N/A | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-05-28 | Kenny Liljestrom |  | Add | 81
0 | SWWH006 | 5 | Tankless Water Heater, Commercial | Any | Any | Any |  | EECP | 18 | - | Yes | Market Cost | Market Cost | Formula | [9 empty] | - | - | - | - | - | - | Remove if legacy (not used in programs) | 2021-08-25 | Kenny Liljestrom |  | Add | 11
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-19 | Kenny Liljestrom |  | Add | 12
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-19 | Kenny Liljestrom |  | Add | 5
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | AR | Any |  | EECP | 3 | For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers, Customer/site information, Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating | Yes |  | Has all Preponderance of Evidence (POE) been submitted as defined by the workpaper? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Review the submitted documentation in EECP for POE | For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers, Customer/site information, Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 83
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | AR | Any |  | EECP | 5 | Good to have | No |  | Who was the party that filled out the POE documentation? | Drop Down List | Tenant;Owner;Owner Representative;Implementer; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-10-20 | Kenny Liljestrom | Implementers responsible for POE documentation | Add | 56
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | NR | Any |  | EECP | 6 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes | Replacing Gas_Gas | Replacing gas unit with gas unit? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | The installation report should indicate the existing conditions including the fuel type of the existing boiler | The existing and proposed boilers must be fueled by natural gas | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 33
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | Any | Any |  | EECP | 7 | Water heaters or hot water boilers used for space conditioning, industrial (process) end-use applications, pools, or spas are not eligible. | Yes |  | Installed in a commercial domestic (or “service”) hot water application in a NonRes facility? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 93
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | Any | Any |  | EECP | 8 | Good to have | Yes |  | Cap-kBtuh | Numeric Value | [9 empty] | Inspections | Photograph the nameplate showing the Input Rating (Btu/hr) of the unit | The Input Rating (Btu/hr) listed in EECP should match what is listed on the nameplate; to convert from Btu/hr to kBtu/hr use the following formula: Input Rating (Btu/hr) / 1,000 (Btu/kBtu) = Input Rating (kBtu/hr) | QA Checklist | Use the manufacturer spec sheet to validate the Input Rating (Btu/hr) | The Input Rating (Btu/hr) listed in EECP should match what is listed on the spec sheet; to convert from Btu/hr to kBtu/hr use the following formula: Input Rating (Btu/hr) / 1,000 (Btu/kBtu) = Input Rating (kBtu/hr) | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 9
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | Any | Any |  | EECP | 9 | Good to have | Yes |  | Size (gallons) | Numeric Value | [9 empty] | Inspections | Photograph the nameplate showing the Storage Capacity or Volume (gallons) of the unit | The Storage Capacity or Volume (gallons) listed in EECP should match what is listed on the nameplate | QA Checklist | Use the manufacturer spec sheet to validate the Storage Capacity or Volume (gallons) | The Storage Capacity or Volume (gallons) listed in EECP should match what is listed on the spec sheet | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 14
1 | SWWH007 | 4 | Storage Water Heater, Commercial | A | Any | Any |  | EECP | 10 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Uniform Energy Factor (UEF) | Numeric Value | [8 empty] | Must be >= 0.68 | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor (UEF) | The Uniform Energy Factor (UEF) Must be >= 0.68 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 27
1 | SWWH007 | 4 | Storage Water Heater, Commercial | B | Any | Any |  | EECP | 11 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Uniform Energy Factor (UEF) | Numeric Value | [8 empty] | Must be >= 0.64 | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor (UEF) | The Uniform Energy Factor (UEF) Must be >= 0.64 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 27
1 | SWWH007 | 4 | Storage Water Heater, Commercial | C | Any | Any |  | EECP | 12 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Uniform Energy Factor (UEF) | Numeric Value | [8 empty] | Must be >= 0.68 | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor (UEF) | The Uniform Energy Factor (UEF) Must be >= 0.68 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 27
1 | SWWH007 | 4 | Storage Water Heater, Commercial | D | Any | Any |  | EECP | 13 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Uniform Energy Factor (UEF) | Numeric Value | [8 empty] | Must be >= 0.64 | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor (UEF) | The Uniform Energy Factor (UEF) Must be >= 0.64 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 27
1 | SWWH007 | 4 | Storage Water Heater, Commercial | E | Any | Any |  | EECP | 14 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Uniform Energy Factor (UEF) | Numeric Value | [8 empty] | Must be >= 0.68 | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor (UEF) | The Uniform Energy Factor (UEF) Must be >= 0.68 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 27
1 | SWWH007 | 4 | Storage Water Heater, Commercial | F | Any | Any |  | EECP | 15 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Uniform Energy Factor (UEF) | Numeric Value | [8 empty] | Must be >= 0.64 | QA Checklist | Use the manufacturer spec sheet to validate the Uniform Energy Factor (UEF) | The Uniform Energy Factor (UEF) Must be >= 0.64 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 27
1 | SWWH007 | 4 | Storage Water Heater, Commercial | G | Any | Any |  | EECP | 16 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 83% | QA Checklist | Use the manufacturer spec sheet to validate the Thermal Efficiency (%) | The Thermal Efficiency (%) Must be >= 83% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 22
1 | SWWH007 | 4 | Storage Water Heater, Commercial | H | Any | Any |  | EECP | 17 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 90% | QA Checklist | Use the manufacturer spec sheet to validate the Thermal Efficiency (%) | The Thermal Efficiency (%) Must be >= 90% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 22
1 | SWWH007 | 4 | Storage Water Heater, Commercial | I | Any | Any |  | EECP | 18 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes |  | Thermal Efficiency (%) | Numeric Value | [8 empty] | Must be >= 96% | QA Checklist | Use the manufacturer spec sheet to validate the Thermal Efficiency (%) | The Thermal Efficiency (%) Must be >= 96% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 22
1 | SWWH007 | 4 | Storage Water Heater, Commercial | Any | Any | Any |  | EECP | 19 | Eligible commercial storage water heaters must meet the following requirements: • Meet minimum qualifying efficiency ratings in the Measure Case Description. • For normal replacement installations, only gas-for-gas replacements are eligible. Meet the definition of a storage water heater, as defined by the California Energy Commission: • Be used primarily for domestic hot water. • Have an input rating of less than 4,000 Btu/hr/gal of stored water. | Yes | Input Rating | Input Rating (btu/hr/gallon) | Numeric Value | [8 empty] | Must be <=4000 | QA Checklist | Use the manufacturer spec sheet to validate the Input Rating (Btu/hr-gallon) | The Input Rating (Btu/hr-gallon) listed in EECP should match what is listed on the spec sheet; if not listed, the value can be calculated as: Input Rating (Btu/hr) / Storage Capacity (gallons) = Input Rating (Btu/hr-gallon) This value needs to be <= 4,000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-07-19 | Kenny Liljestrom |  | Add | 28
0 | SWWH008 | 1 | Boiler, Process | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the manufacturer of the unit | The manufacturer listed in EECP should match the manufacturer listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-19 | Kenny Liljestrom |  | Add | 12
0 | SWWH008 | 1 | Boiler, Process | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the nameplate showing the model number of the unit | The model number listed in EECP should match the model number listed on the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-19 | Kenny Liljestrom |  | Add | 5
0 | SWWH008 | 1 | Boiler, Process | A | Any | Any |  | EECP | 3 | Water boilers must have an input rating ≤ 200,000 kBtu/hr. The combustion efficiency must have a documented combustion efficiency of 85% or greater under full load conditions. Steam boilers must have an input rating ≤ 200,000 kBtu/hr. The combustion efficiency must have a documented combustion efficiency of 83% or greater under full load conditions. | Yes | EFFICIENCY | Combustion Efficiency (%) | Numeric Value | [8 empty] | Must be >= 85% | QA Checklist | Use the manufacturer spec sheet to validate the Combustion Efficiency (%) | The Combustion Efficiency (%) Must be >= 85% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Only configured for a single implementation, needs to be expanded across all SWWH008 implementations | 2021-07-19 | Kenny Liljestrom |  | Add | 25
0 | SWWH008 | 1 | Boiler, Process | B | Any | Any |  | EECP | 4 | Water boilers must have an input rating ≤ 200,000 kBtu/hr. The combustion efficiency must have a documented combustion efficiency of 85% or greater under full load conditions. Steam boilers must have an input rating ≤ 200,000 kBtu/hr. The combustion efficiency must have a documented combustion efficiency of 83% or greater under full load conditions. | Yes | EFFICIENCY | Combustion Efficiency (%) | Numeric Value | [8 empty] | Must be >= 90% | QA Checklist | Use the manufacturer spec sheet to validate the Combustion Efficiency (%) | The Combustion Efficiency (%) Must be >= 90% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Only configured for a single implementation, needs to be expanded across all SWWH008 implementations (A, B, C), Update property label and validation to account for % | 2021-07-19 | Kenny Liljestrom |  | Add | 25
0 | SWWH008 | 1 | Boiler, Process | C | Any | Any |  | EECP | 5 | Water boilers must have an input rating ≤ 200,000 kBtu/hr. The combustion efficiency must have a documented combustion efficiency of 85% or greater under full load conditions. Steam boilers must have an input rating ≤ 200,000 kBtu/hr. The combustion efficiency must have a documented combustion efficiency of 83% or greater under full load conditions. | Yes | EFFICIENCY | Combustion Efficiency (%) | Numeric Value | [8 empty] | Must be >= 83% | QA Checklist | Use the manufacturer spec sheet to validate the Combustion Efficiency (%) | The Combustion Efficiency (%) Must be >= 83% | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Only configured for a single implementation, needs to be expanded across all SWWH008 implementations (A, B, C) | 2021-07-19 | Kenny Liljestrom |  | Add | 25
0 | SWWH008 | 1 | Boiler, Process | Any | Any | Any |  | EECP | 6 | Good to have | Yes |  | Size ( kBtu/hr) | Numeric Value | [8 empty] | Must be <=20000 | Inspections | Photograph the nameplate showing the Input Rating (Btu/hr) of the unit | The Input Rating (Btu/hr) listed in EECP should match what is listed on the nameplate; to convert from Btu/hr to kBtu/hr use the following formula: Input Rating (Btu/hr) / 1,000 (Btu/kBtu) = Input Rating (kBtu/hr) The value must be <= 20,000 kBtu/hr | QA Checklist | Use the manufacturer spec sheet to validate the Input Rating (Btu/hr) | The Input Rating (Btu/hr) listed in EECP should match what is listed on the spec sheet; to convert from Btu/hr to kBtu/hr use the following formula: Input Rating (Btu/hr) / 1,000 (Btu/kBtu) = Input Rating (kBtu/hr) The value must be <= 20,000 kBtu/hr | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 15
0 | SWWH008 | 1 | Boiler, Process | Any | Any | Any |  | EECP | 7 | This measure is not applicable to boilers used for space heating, domestic hot water, pools, or spas, and is not eligible for domestic hot water or space heating. | Yes | Boiler Use | Is the boiler used for space heating, domestic hot water, pools, or spas? | Drop Down List | Yes;No; | [7 empty] | Must be No | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-07-19 | Kenny Liljestrom |  | Add | 74
0 | SWWH008 | 1 | Boiler, Process | Any | Any | Any |  | EECP | 8 | This measure is not eligible for new construction installations. | Yes |  | Is this measure being installed on a new construction project? | Drop Down List | Yes;No; | [7 empty] | Must be No | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 62
0 | SWWH008 | 1 | Boiler, Process | Any | Any | Any |  | EECP | 9 | Eligible building types include all existing commercial, agriculture, and industrial (nonresidential) buildings of any vintage. This measure is available to industrial end-use customers that manufacture a saleable product, typically (but not limited to) NAICS codes 31, 32, and 33. | Yes |  | Installed in a NAICS code 31, 31, or 33? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | Use the NAICS database to determine if the building type is considered to be in building types beginning with 31, 32, or 33 | This measure is available to industrial end-use customers that manufacture a saleable product, typically (but not limited to) NAICS codes 31, 32, and 33. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-19 | Kenny Liljestrom |  | Add | 40
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | UpDeemed |  | EECP | 0 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 7
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | UpDeemed |  | EECP | 5 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 12
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | Any |  | EECP | 10 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 12
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | Any |  | EECP | 15 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 5
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | UpDeemed |  | EECP | 20 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 13
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | Any |  | EECP | 25 | Only gas-for-gas normal replacements or for new construction installations are eligible. Normal replacements must replace a storage water heater with another storage water heater. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | AR | Any |  | EECP | 30 | Only storage water heaters as defined by the California Energy Commission qualify, and they must: Be used primarily for domestic hot water. Water heaters used for space conditioning, process end use applications, pools or spas are not eligible. | Yes | Primary Use Domestic Water | Water heater is primarily used for domestic hot water, not for space conditioning, pools or spas? | Drop Down List | Yes;No |  | Equal | Yes |  |  |  |  | Must be Yes | Inspections | Ask the customer if the water heater is used primarily for domestic hot water (i.e. not connected to the HVAC system) | The domestic water heater should be used primarily for hot water loads such as showers and faucets | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  | Add | 97
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | Any |  | EECP | 35 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). “Storage water heater” means a water heater that heats and stores water within the appliance at a thermostatically-controlled temperature for delivery on demand, and that has an input less than 4,000 Btu/hr/gal of stored water. | Yes | Input Rating | Input rating (kBtu/hr) | Numeric Value |  |  |  |  | General | 0 | 75 | 1 | Must be < = 75 | Inspections | Photograph the equipment nameplate to capture the input capacity (Btu/hr) | The listed input capacity in EECP should match the nameplate by using the following conversion: kBtu/hr = Btu/hr / 1,000 | QA Checklist | Review the manufacturer specficiation sheet to check for the input capacity (Btu/hr) of the installed equipment | The listed input capacity in EECP should match the nameplate by using the following conversion: kBtu/hr = Btu/hr / 1,000 |  | 2022-06-13 | Kenny Liljestrom |  |  | 22
1 | SWWH012 | 2 | Storage Water Heater, Residential | E | Any | Any |  | EECP | 40 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 30 | 39.9 | 1 | Must be between 30 - 39.9 | Inspections | Photograph the equipment nameplate to capture the storage capacity (gallons) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the manufacturer specficiation sheet to check for the storage capacity (gallons) of the installed equipment | The equipment in EECP should have a storage capacity (gallons) that matches EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | F | Any | Any |  | EECP | 40 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 40 | 49.9 | 1 | Must be between 40 - 49.9 | Inspections | Photograph the equipment nameplate to capture the storage capacity (gallons) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the manufacturer specficiation sheet to check for the storage capacity (gallons) of the installed equipment | The equipment in EECP should have a storage capacity (gallons) that matches EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | G | Any | Any |  | EECP | 40 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 40 | 49.9 | 1 | Must be between 40 - 49.9 | Inspections | Photograph the equipment nameplate to capture the storage capacity (gallons) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the manufacturer specficiation sheet to check for the storage capacity (gallons) of the installed equipment | The equipment in EECP should have a storage capacity (gallons) that matches EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | H | Any | Any |  | EECP | 40 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 50 | 59.9 | 1 | Must be between 50 - 59.9 | Inspections | Photograph the equipment nameplate to capture the storage capacity (gallons) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the manufacturer specficiation sheet to check for the storage capacity (gallons) of the installed equipment | The equipment in EECP should have a storage capacity (gallons) that matches EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | I | Any | Any |  | EECP | 40 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 50 | 59.9 | 1 | Must be between 50 - 59.9 | Inspections | Photograph the equipment nameplate to capture the storage capacity (gallons) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the manufacturer specficiation sheet to check for the storage capacity (gallons) of the installed equipment | The equipment in EECP should have a storage capacity (gallons) that matches EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | J | Any | Any |  | EECP | 40 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 30 | 39.9 | 1 | Must be between 30 - 39.9 | Inspections | Photograph the equipment nameplate to capture the storage capacity (gallons) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the manufacturer specficiation sheet to check for the storage capacity (gallons) of the installed equipment | The equipment in EECP should have a storage capacity (gallons) that matches EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | K | Any | Any |  | EECP | 40 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 40 | 49.9 | 1 | Must be between 40 - 49.9 | Inspections | Photograph the equipment nameplate to capture the storage capacity (gallons) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the manufacturer specficiation sheet to check for the storage capacity (gallons) of the installed equipment | The equipment in EECP should have a storage capacity (gallons) that matches EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | L | Any | Any |  | EECP | 40 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 50 | 59.9 | 1 | Must be between 50 - 59.9 | Inspections | Photograph the equipment nameplate to capture the storage capacity (gallons) | The listed cooling capacity in EECP should match the nameplate | QA Checklist | Review the manufacturer specficiation sheet to check for the storage capacity (gallons) of the installed equipment | The equipment in EECP should have a storage capacity (gallons) that matches EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH012 | 2 | Storage Water Heater, Residential | E | Any | Any |  | EECP | 45 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 0.64 | 5 | 2 | Must be <= 0.64 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH012 | 2 | Storage Water Heater, Residential | F | Any | Any |  | EECP | 45 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 0.64 | 5 | 2 | Must be <= 0.64 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH012 | 2 | Storage Water Heater, Residential | G | Any | Any |  | EECP | 45 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 0.68 | 5 | 2 | Must be <= 0.68 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH012 | 2 | Storage Water Heater, Residential | H | Any | Any |  | EECP | 45 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 0.64 | 5 | 2 | Must be <= 0.64 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH012 | 2 | Storage Water Heater, Residential | I | Any | Any |  | EECP | 45 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 0.68 | 5 | 2 | Must be <= 0.68 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH012 | 2 | Storage Water Heater, Residential | J | Any | Any |  | EECP | 45 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 0.68 | 5 | 2 | Must be <= 0.68 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH012 | 2 | Storage Water Heater, Residential | K | Any | Any |  | EECP | 45 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 0.83 | 5 | 2 | Must be <= 0.83 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH012 | 2 | Storage Water Heater, Residential | L | Any | Any |  | EECP | 45 | Eligible water heaters must comply with the measure case specification (see Measure Case Description). | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 0.88 | 5 | 2 | Must be <= 0.88 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | UpDeemed |  | EECP | 190 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value |  |  |  |  | General |  |  | 0 |  | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 8
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | UpDeemed |  | EECP | 195 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 15
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | AR | Any |  | QA Checklist | 205 | For accelerated replacement application types, this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: targeted segment of the market or customers, Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating | Yes | POE Docs | Have POE requirements in the measure package been included in uploaded documentation? | None | [9 empty] | QA Checklist | Review the POE documentation and determine if it is adequate based on required criteria. | The POE documentation needs to list the targeted segment of the market or customers, Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating or one of the three alternatives listed in Section 7.3 of POEV 2.0 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-06-13 | Kenny Liljestrom |  | Add | 85
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | Any |  | QA Checklist | 210 | If necessary, customer must provide proof of unit efficiency (e.g., manufacturer’s equipment specification sheet). | Yes | - | Has the manufacturer specification sheet been submitted to prove the equipment efficiency? | Drop Down List | Yes;No |  | Equal | Yes |  |  |  |  | Must be Yes | QA Checklist | Review the EECP submitted documentation for the manufacturer specification sheet | The submitted specification sheet should list the manufacturer and model number listed in EECP and verified by inspections | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  | Add | 90
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | Any |  | QA Checklist | 215 | Equipment must comply with the test methods referenced in the California Building Energy Efficiency Standards (Title 24) and the California Appliance Efficiency Regulations (Title 20). | No | - | Does the water heater meet all Title 24 and Title 20 testing methods? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom | There is no way to check for this if the product is not on a qualified products list. | Add | 69
1 | SWWH012 | 2 | Storage Water Heater, Residential | Any | Any | Any |  | EECP | 220 | Additionally, the equipment must meet minimum emissions requirements as defined by local air quality management districts. See Code Requirements. | No | - | Water heater meet all emissions requirements as outlined by local air quality management districts? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom | This is difficult to prove, all water heaters on the market should qualify for this | Add | 99
0 | SWWH014 | 2 | Heat Pump Water Heater, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-20 | Kenny Liljestrom |  | Add | 12
0 | SWWH014 | 2 | Heat Pump Water Heater, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-20 | Kenny Liljestrom |  | Add | 5
0 | SWWH014 | 2 | Heat Pump Water Heater, Residential | Any | NC | Any |  | EECP | 3 | For new construction (NC), the baseline can be a gas-fired water heater. But, energy savings and measure cost are estimated and reported as the difference between the corresponding heat pump water heater and the baseline electric resistance water heater. (See also Base Case Description.) | Yes |  | What is the assumed baseline fuel type? | Drop Down List | Electric;Gas; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 39
0 | SWWH014 | 2 | Heat Pump Water Heater, Residential | Any | Any | Any |  | EECP | 4 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes |  | Is the installed equipment a residential-style electric storage water heater? | Drop Down List | Yes;No | [7 empty] | Must be Yes | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than or equal to 45-gallons | QA Checklist | Using the make and model, locate the equipment specifications and determine the equipment type, you may be able to do this with the EnergyStar database | The unit should not be listed as an “instantaneous” or “tankless” water heater | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 77
0 | SWWH014 | 2 | Heat Pump Water Heater, Residential | Any | Any | Any |  | EECP | 5 | A new heat pump water heater with storage capacity less than 45 gallons does not qualify. | Yes |  | Storage Capacity (gallons) | Numeric Value | [8 empty] | Must be >= 45 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than or equal to 45-gallons | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than or equal to 45-gallons and match what is listed in EECP | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | Any | Any | UpDeemed |  | EECP | 0 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 7
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | Any | Any | UpDeemed |  | EECP | 5 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 12
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | Any | Any | Any |  | EECP | 10 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 12
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | Any | Any | Any |  | EECP | 15 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 5
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | Any | Any | UpDeemed |  | EECP | 20 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 13
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | A | Any | Any |  | EECP | 25 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Instantaneous;Heat Pump;Electric Storage;Tankless; |  | Equal | Electric Storage |  |  |  |  | Must be 'Electric Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | B | Any | Any |  | EECP | 25 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Instantaneous;Heat Pump;Electric Storage;Tankless; |  | Equal | Electric Storage |  |  |  |  | Must be 'Electric Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | C | Any | Any |  | EECP | 25 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Instantaneous;Heat Pump;Electric Storage;Tankless; |  | Equal | Electric Storage |  |  |  |  | Must be 'Electric Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | D | Any | Any |  | EECP | 25 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Instantaneous;Heat Pump;Electric Storage;Tankless; |  | Equal | Electric Storage |  |  |  |  | Must be 'Electric Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | E | Any | Any |  | EECP | 25 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Instantaneous;Heat Pump;Electric Storage;Tankless; |  | Equal | Electric Storage |  |  |  |  | Must be 'Electric Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | F | Any | Any |  | EECP | 25 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Instantaneous;Heat Pump;Electric Storage;Tankless; |  | Equal | Electric Storage |  |  |  |  | Must be 'Electric Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | G | Any | Any |  | EECP | 25 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Instantaneous;Heat Pump;Electric Storage;Tankless; |  | Equal | Heat Pump |  |  |  |  | Must be 'Heat Pump' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | H | Any | Any |  | EECP | 25 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Instantaneous;Heat Pump;Electric Storage;Tankless; |  | Equal | Heat Pump |  |  |  |  | Must be 'Heat Pump' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | A | Any | Any |  | EECP | 30 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 45 | 55 | 0 | Must be >= 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | B | Any | Any |  | EECP | 30 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 45 | 55 | 0 | Must be >= 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | C | Any | Any |  | EECP | 30 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 45 | 55 | 0 | Must be >= 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | D | Any | Any |  | EECP | 30 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 45 | 55 | 0 | Must be >= 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | E | Any | Any |  | EECP | 30 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 45 | 55 | 0 | Must be >= 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | F | Any | Any |  | EECP | 30 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 45 | 55 | 0 | Must be >= 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than or equal to 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | G | Any | Any |  | EECP | 30 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 56 | 75 | 0 | Must be > 55 and <= 75 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 55-gallons and less than or equal to 75-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 55-gallons and less than or equal to 75-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | H | Any | Any |  | EECP | 30 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 75 |  | 0 | Must be > 75 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 75-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 75-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | A | Any | Any |  | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | B | Any | Any |  | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | C | Any | Any |  | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | D | Any | Any |  | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | E | Any | Any |  | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | F | Any | Any |  | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | G | Any | Any |  | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.33 |  | 2 | Must be >= 3.33 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | H | Any | Any |  | EECP | 35 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.42 |  | 2 | Must be >= 3.42 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | Any | Any | Any |  | EECP | 40 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | FHR | First Hour Rating (FHR) | Numeric Value |  |  |  |  | General | 0 |  | 0 | Must be > 0 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The First Hour Rating (FHR) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 23
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | Any | Any | UpDeemed |  | EECP | 190 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value |  |  |  |  | General |  |  | 0 |  | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 8
1 | SWWH014 | 3 | Heat Pump Water Heater, Residential | Any | Any | UpDeemed |  | EECP | 195 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 15
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | Any | Any | Any |  | EECP | 1 | - | Pending | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the controller nameplate to capture the manufacturer; the controller will most likely be mounted on or near the hot water boiler or tank | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-10-13 | Kenny Liljestrom |  |  | 12
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | Any | Any | Any |  | EECP | 2 | - | Pending | Model | Model | Text Box | [9 empty] | Inspections | Photograph the controller nameplate to capture the model number; the controller will most likely be mounted on or near the hot water boiler or tank | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-10-13 | Kenny Liljestrom |  |  | 5
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | A | Any | Any |  | EECP | 3 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | B | Any | Any |  | EECP | 4 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | C | Any | Any |  | EECP | 5 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | D | Any | Any |  | EECP | 6 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | E | Any | Any |  | EECP | 7 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | F | Any | Any |  | EECP | 8 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | G | Any | Any |  | EECP | 9 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | H | Any | Any |  | EECP | 10 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | I | Any | Any |  | EECP | 11 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | J | Any | Any |  | EECP | 12 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be multifamily | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Multifamily | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | K | Any | Any |  | EECP | 13 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | L | Any | Any |  | EECP | 14 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | M | Any | Any |  | EECP | 15 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | N | Any | Any |  | EECP | 16 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | O | Any | Any |  | EECP | 17 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | P | Any | Any |  | EECP | 18 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | Q | Any | Any |  | EECP | 19 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | R | Any | Any |  | EECP | 20 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | S | Any | Any |  | EECP | 21 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | T | Any | Any |  | EECP | 22 | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Pending | Building Type | This measure is applicable for qualifying multifamily, hotel, motel, nursing home, and university dormitories with a central water heating system. | Text Box | [9 empty] | QA Checklist | Use the installation report or customer address to confirm the building type is one of the eligible types | Building type must be hotel, motel, nursing home, and university dormitories | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | This property can be configured at the enrollment level to only include: Education - University Dormitory, Hotel, Motel, Nursing Home | 2021-10-13 | Kenny Liljestrom |  |  | 146
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | Any | Any | Any |  | EECP | 23 | This measure qualifies only for central hot-water systems used primarily for domestic hot-water heating. | Pending |  | Domestic hot water served by central system? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | Locate and photograph the domestic hot water heater system | The domestic hot water heater must be a centralized system; these can be identified typically by their locations which can be in mechanical equipment rooms, on the roof, or on the exterior of a building; central hot water systems are defined as units that serve an entire building, not individual or several units | QA Checklist | Use the installation report to determine the type of domestic hot water system at the facility | The domestic hot water heater must be a centralized system; these can be identified typically by their locations which can be in mechanical equipment rooms, on the roof, or on the exterior of a building; central hot water systems are defined as units that serve an entire building, not individual or several units |  | 2021-10-13 | Kenny Liljestrom |  |  | 44
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | Any | Any | Any |  | EECP | 24 | Central hot water systems with demand-controlled recirculation pump are not eligible. | Pending |  | Existing domestic hot water system had demand-controlled recirculation pump? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | QA Checklist | Use the installation report or photos of existing equipment to determine the recirculation pump controls | Existing systems must not already have demand-control recirculation pumps | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-10-13 | Kenny Liljestrom |  |  | 76
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | Any | Any | Any |  | EECP | 25 | Facilities that must maintain hot water temperature of 140°F to control Legionella bacteria are not eligible. Local, state, and federal regulations must be followed to avoid the risk of Legionella growth and scalding. | Pending |  | Domestic hot water loop temperature (F) | Numeric Value | [8 empty] | Must be >= 140 | Inspections | Photograph and record the loop temperature of the domestic hot water system | The hot water temperature must be greater than 140F | QA Checklist | Use the installation report to determine the hot water loop temperature (F) | The hot water temperature must be greater than 140F |  | 2021-10-13 | Kenny Liljestrom |  |  | 39
0 | SWWH016 | 2 | Domestic Hot Water Loop Temperature Controller, Multifamily & Commercial | Any | Any | Any |  | QA Checklist | 26 | Data to be collected will include manufacturer and model numbers of controllers installed. Controller invoice amount and installation cost will be required to be collected to calibrate cost data. | Pending | Data Collection | Data to be collected will include manufacturer and model numbers of controllers installed. Controller invoice amount and installation cost will be required to be collected to calibrate cost data. | Text Box | [9 empty] | QA Checklist | Ensure all documentation has been uploaded by the implementer | Data to be collected will include manufacturer and model numbers of controllers installed. Invoice amount and installation cost will be required to be collected to calibrate cost data. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-10-13 | Kenny Liljestrom |  |  | 195
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 0 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 5 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | A | Any | Any |  | EECP | 10 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | B | Any | Any |  | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | C | Any | Any |  | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | J | Any | Any |  | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | K | Any | Any |  | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | L | Any | Any |  | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | S | Any | Any |  | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | T | Any | Any |  | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | U | Any | Any |  | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AB | Any | Any |  | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AC | Any | Any |  | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AD | Any | Any |  | EECP | 15 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam. | Yes | Type | Type of insulation | Drop Down List | Elastomeric Foam Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | The insulation type should match what is listed in EECP (Elastomeric Foam Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | D | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | E | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | F | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | G | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | H | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | I | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | M | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | N | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | O | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | P | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Q | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | R | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | V | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | W | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | X | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Y | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Z | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AA | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AE | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AF | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AG | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AH | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AI | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AJ | Any | Any |  | EECP | 15 | Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass, and rigid mineral wool. | Yes | Type | Type of insulation | Drop Down List | Silicone Foam Rubber Melamine Foam;Rigid Urethane-Based Foam;Cellular Glass;Rigid Fiberglass;Rigid Mineral Wool | [8 empty] | QA Checklist | The make and model can be used to cross reference the manufacturer specification sheet; the insulation type should match what is listed in EECP | the insulation type should match what is listed in EECP (Silicone Foam Rubber Melamine Foam; Rigid Urethane-Based Foam; Cellular Glass; Rigid Fiberglass; Rigid Mineral Wool) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 20 | The manufacturer specification sheet must be submitted with the application. | Yes | Manufacturer Cut Sheet Submitted | Insulation manufacturer specification sheet submitted with the application? | Drop Down List | Yes;No |  | Equal | Yes |  |  |  |  | Must be Yes | QA Checklist | Review the EECP submitted documentation for the manufacturer specification sheet | An insulation specification sheet should be included in the submitted documentation | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 75
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 25 | A minimum of one inch of pipe insulation must be added to existing bare commercial or industrial steel or copper pipe. | Yes | Pipe Insulation Added | At least 1-in of insulation added to existing bare commercial or industrial steel or copper pipe? | Drop Down List | Yes;No |  | Equal | Yes |  |  |  |  | Must be Yes | Inspections | Locate the insulated piping and look at the diameter of the bare pipe | The insulation thickness should be greater than or equal to 1-inch and the piping should be either copper or steel (i.e. not PVC or other materials) | QA Checklist | The make and model of the insulation should indicate on the manufacturer specification sheet the insulation thickness; a photograph of the piping system in an installation report may show the type of piping installed | The insulation thickness should be greater than or equal to 1-inch and the eligible types are piping include copper and steel |  | 2021-06-21 | Kenny Liljestrom |  | Add | 97
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 30 | The hours of operation must be indicated on the top of the application. | Yes | Hours of operation | Hours of operation of the hot water system | Numeric Value |  |  |  |  | General | 0 | 8760 | 0 | Must be <= 8760 | QA Checklist | The application form should indicate the hours of operation for the hot water system | No validation criteria | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 42
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 35 | The minimum qualifying pipe diameter is ½-inch. | Yes | Size | Pipe Diameter (in) | Numeric Value |  |  |  |  | General | 0.5 | 10 | 2 | Must be >= 0.5 in (1/2-in) | Inspections | Using a ruler or best judgement, estimate the diameter of the hot water piping and record the value | The value should match what is listed in EECP | QA Checklist | An installation report may show the piping diameter | Piping must be greater than 1/2-inch |  | 2022-03-15 | Kenny Liljestrom |  | Add | 18
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | D | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  | Add | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | E | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | F | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | G | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | H | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | I | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | M | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | N | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | O | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | P | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Q | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | R | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | V | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | W | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | X | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Y | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Z | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AA | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AE | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AF | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AG | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AH | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AI | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | AJ | Any | Any |  | EECP | 40 | If the fluid is steam, the pressure of the steam must also be indicated. | Yes | PSIG | Steam Pressure (psig) | Numeric Value |  |  |  |  | General |  |  | 0 |  | Inspections | Locate the steam gauge in the steam piping system; photograph or record the steam pressure in PSIG | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report may indicate the steam operating pressure | No validation criteria |  | 2022-03-15 | Kenny Liljestrom |  |  | 21
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 45 | The length of insulation to be installed with each pipe size must be indicated. | No | Length | Length of piping in linear feet | Numeric Value |  |  |  |  | General |  |  | 1 |  | Inspections | Using a measuring wheel or best estimate; measure the length (in feet) of the piping insulation | The value should be within 10% of what is listed in EECP | QA Checklist | An installation report should indicate the length of the insulation installed | No validation criteria |  | 2021-06-21 | Kenny Liljestrom | This is captured with the measure quantity | Add | 31
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 45 | Insulation required by California Building Energy Efficiency Standards (Title 24) or employee safety laws (Occupational Safety and Health Administration, OSHA) is not eligible. | Yes | Title 24 | In the installed insulation required by California Building Energy Efficiency Standards (Title 24) or employee safety laws (Occupational Safety and Health Administration, OSHA)? | Drop Down List | Yes;No |  | Equal | Yes |  |  |  |  | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Property label should be updated to correct the front end: "Is the installed…" | 2021-06-21 | Kenny Liljestrom |  | Add | 177
1 | SWWH017 | 2 | Hot Water Pipe Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 50 | Replacement of damaged (existing) insulation is not eligible. | Yes | Existing Insulation | Does the piping have existing insulation that is damaged or being replaced? | Drop Down List | Yes;No |  | Equal | No |  |  |  |  | Must be No | Inspections | Photograph the piping system, indicate if there are any old glue marks, aged insulation, or mothballed insulation near or around the piping | There should be no signs of any previously installed insulation on the piping | QA Checklist | Photographs of the existing and installed measure conditions of the hot water piping | The existing piping should not have any insulation installed |  | 2021-06-21 | Kenny Liljestrom |  | Add | 75
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 1 | The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 2 | The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 3 | The tank must be coupled to gas-fired commercial, industrial, agriculture, or multifamily central equipment that transfers heat to the contained liquid or solution. | Yes | Coupled Tank | Is the tank that was insulated coupled to gas-fired commercial, industrial, or agriculture equipment that transfers heat to the contained liquid or solution? | Drop Down List | Yes;No | [7 empty] | Must be Yes | Inspections | Photograph the water heater and piping; ask the customer if the water heater is used for any purpose other than serving showerheads or faucets | Ensure the water heater is not serving any industrial process loads (heated water tanks, heat exchangers, etc.) | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 157
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 4 | The following conditions and applications are not eligible: • Tanks with pre-existing insulation • Replacement of old or damaged insulation • Tanks insulated to prevent burns. • Insulation for exposed hot-water tanks within seven feet of the floor that are not otherwise guarded in such manner as to prevent contact. The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Existing Insulation | Does the tank have existing insulation (in any condition) or evidence of prior insulation being installed ? | Drop Down List | Yes;No | [7 empty] | Must be No | Inspections | Inspect the area around the water heater to look for any clues of previous insulation being installed | Ensure the tank doesn't show any evidence of prior insulation being installed such as: scattered insulation on the floor around the tank, old glue marks on the outside of the tank, pieces of old insulation still on the tank, etc.) | QA Checklist | Photographs of the existing and installed measure conditions of the hot water tank | No insulation should be installed on the existing water tank |  | 2021-06-21 | Kenny Liljestrom |  | Add | 107
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 5 | The following conditions and applications are not eligible: • Tanks with pre-existing insulation • Replacement of old or damaged insulation • Tanks insulated to prevent burns. • Insulation for exposed hot-water tanks within seven feet of the floor that are not otherwise guarded in such manner as to prevent contact. | Yes | Insulation Required to Prevent Burns | Is the insulation required to prevent burns or is the tank located where burns can be sustained? | Drop Down List | Yes;No | [7 empty] | Must be No | Inspections | Check if the tank is in an area with high traffic or located within arms reach of an uncovered walkway | Indicate whether or not the tank is in a location where it would be easy to sustain a burn by walking by, the tank should not be located in an easily accessible location where burns could be sustained from walking by | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 96
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 6 | The following conditions and applications are not eligible: • Tanks with pre-existing insulation • Replacement of old or damaged insulation • Tanks insulated to prevent burns. • Insulation for exposed hot-water tanks within seven feet of the floor that are not otherwise guarded in such manner as to prevent contact. The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Exposed Hot Water Tanks | Is the insulation for exposed hot-water tanks within seven feet of the floor that are not otherwise guarded in such manner as to prevent contact? | Drop Down List | Yes;No | [7 empty] | Must be No | Inspections | Check if the tank is in an area with high traffic or located within arms reach of an uncovered walkway | Indicate whether or not the tank is in a location where it would be easy to sustain a burn by walking by, the tank should not be located in an easily accessible location where burns could be sustained from walking by | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 145
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 7 | The insulation thickness and process temperature (tank solution temperature) will determine the energy savings. The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Tank Temp | Temperature inside the tank (F) | Numeric Value | [9 empty] | Inspections | Photograph the thermometer installed at the top of the tank or along the piping indicating the temperature of the fluid inside the tank or piping | The value listed in EECP should be within 10% of the measured value in the field | QA Checklist | An installation report should indicate the water temperature inside the hot water tank | The value listed in EECP should be within 10% of the measured value in the field |  | 2021-06-21 | Kenny Liljestrom |  | Add | 31
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 8 | The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Insulation material type | Insulation material type | Text Box | [9 empty] | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the insulation material type | The insulation material listed in EECP should match the data in the installation report or spec sheet | EECP | Trust Implementer response in EECP | Not configured in original upload |  | 2021-06-21 | Kenny Liljestrom |  | Add | 24
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 9 | The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Insulation Material k-value rating | Insulation material k-value rating | Text Box | [9 empty] | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the insulation k-value rating | The insulation material k-value listed in EECP should match the data in the installation report or spec sheet | EECP | Trust Implementer response in EECP | Not configured in original upload |  | 2021-06-21 | Kenny Liljestrom |  | Add | 34
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 10 | The data collection requirements to ensure accurate determination of eligibility and to inform industry standard practice and future program design include: • Process temperature (temperature inside the tank) • Insulation material manufacturer • Insulation material type • Insulation material k-value rating • Type of tank material (steel, fiberglass, etc.) • Location where burns can be sustained (Yes/No) • Evidence of prior tank insulation (or any insulation fragments) | Yes | Type of tank material | Type of tank material (steel, fiberglass, etc.) | Text Box | [9 empty] | Inspections | Photograph the tank and make your best guess as to the material the tank is made of (i.e. steel, fiberglass, concrete, etc.) | There are not requirements for this just a best guess or judgement | QA Checklist | Use the submitted installation report or manufacturer spec sheet to validate the tank material type | The tank material type listed in EECP should match the data in the installation report or spec sheet (fiberglass, steel, etc.) |  | 2021-06-21 | Kenny Liljestrom |  | Add | 47
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 11 | - | Yes | Usage | Usage | Drop Down List | High;Medium; | [7 empty] | Measure case description dictates allowable use type | - | - | - | - | - | - | Request to remove property, in measure description | 2021-08-06 | Kenny Liljestrom |  | Add | 5
0 | SWWH018 | 2 | Hot Water Tank Insulation, Nonresidential and Multifamily | Any | Any | Any |  | EECP | 12 | - | Yes | Tank Location | Where is the tank located? | Drop Down List | Indoor;Outdoor; | [7 empty] | Measure case description dictates allowable use type | - | - | - | - | - | - | Request to remove property, in measure description | 2021-08-06 | Kenny Liljestrom |  | Add | 26
1 | SWWH019 | 3 | Faucet Aerator, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice, installation report, or manufacturer spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom |  | Add | 12
1 | SWWH019 | 3 | Faucet Aerator, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice, installation report, or manufacturer spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom |  | Add | 5
1 | SWWH019 | 3 | Faucet Aerator, Commercial | Any | Any | Any |  | EECP | 3 | This energy efficiency measure is applicable to an existing faucet in a commercial building that has a flow rate of 1.67 gpm or greater. | Yes |  | Existing Faucet Flow Rate (gpm) | Numeric Value | [8 empty] | Must be >= 1.67 | QA Checklist | Use the submitted installation report to verify existing flow rate of the faucet is listed | The existing flow rate needs to be greater than 1.67 gallons per minute (gpm) and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 31
1 | SWWH019 | 3 | Faucet Aerator, Commercial | Any | Any | Any |  | EECP | 4 | Good to have | Yes |  | New Faucet Flow Rate (gpm) | Numeric Value | [9 empty] | QA Checklist | Use the submitted invoice, installation report, or manufacturer spec sheet to validate the new faucet aerator flow rate is listed | The flow rate of the installed unit must match the flow entered in EECP and be less than or equal to the flowrate required by the measure. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Remove validation criteria from property, measure description captures the min flow rate | 2021-08-19 | Kenny Liljestrom |  | Add | 26
1 | SWWH019 | 3 | Faucet Aerator, Commercial | Any | Any | Any |  | EECP | 5 | Only facilities that utilize natural gas water heating equipment are eligible to receive incentives for this measure. | Yes |  | Is the existing faucet served by a natural gas fired water heater in an existing building? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | Inspections | Ask the customer to show you where the hot water heater is located that serves the domestic hot water loads (faucets, showerheads, etc.); Photograph the water heater and nameplate to determine if the water heater is natural gas fired (yellow corrugated pipe into the burner) | The water heater serving the faucet aerators must be served by a natural gas fired water heater; the water heater nameplate should list the 'Input Rating' in Btu/hr, kBtu/hr, or MMBtu/hr | QA Checklist | Have the implementer provide photos of the water heater serving the faucets; the photos can include a photo of the nameplate (showing make, model, and input rating) | The make and model can be used to locate the equipment specification sheet to identify the fuel type of the water heater, or the Input Rating can be used to identify the fuel type by having units of Btu/hr, kBtu/hr, or MMBtu/hr; The water heater must be served by natural gas | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 90
1 | SWWH019 | 3 | Faucet Aerator, Commercial | Any | Any | Any |  | EECP | 6 | Faucets at health care facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation (e.g. hospitals, clinics, skilled nursing facilities) are not applicable for this measure. The use of aerators is banned in the health care industry due to aerator flow control methods and components. The mixing of air and water within the aerator allows airborne bacteria to become waterborne and, in warm stagnant conditions, promote bacterial growth. Non-aerating laminar flow restrictors (LFRs) must be installed on faucets in these facilities | Yes |  | Is the existing building considered a Health Care facility as defined by OSHPD? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | Inspections | Document the type of building the aerator was installed in | The building type listed in EECP should match the building type during the inspection; the building can not be a healthcare type of facility (nursing home, hospital, clinic, etc.) | QA Checklist | Use the customer account information in EECP to determine the building/customer type | The building type entered by the implementer should match the building type in EECP and not be a healthcare type facility (hospital, nursing home, clinic, etc.) | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 79
0 | SWWH020 | 3 | Low-Flow Showerhead, Commercial | Any | Any | Any |  | EECP | 1 | Make and model number must be included with a copy of the invoice. | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice, installation report, or manufacturer spec sheet to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom |  | Add | 12
0 | SWWH020 | 3 | Low-Flow Showerhead, Commercial | Any | Any | Any |  | EECP | 2 | Make and model number must be included with a copy of the invoice. | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice, installation report, or manufacturer spec sheet to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom |  | Add | 5
0 | SWWH020 | 3 | Low-Flow Showerhead, Commercial | Any | Any | Any |  | EECP | 3 | The measure for the installation of low flow showerheads is applicable for the accelerated replacement of the existing showerhead of 2.5 gpm flow rate or greater with a low-flow showerhead of 1.8 gpm or lower flow rate. The installed low-flow showerhead shall meet the requirements of test procedure ANSI/ASME A112.18.1-2000, Section 5.5 The measure for the installation of flow control valves is applicable for the add-on equipment onto an existing showerhead with the flow rate of 2.5 gpm or greater, reducing the flow rate to 1.5 gpm or lower. | Yes | Existing Flow Rate | Existing Flow Rate (gpm) | Numeric Value | [8 empty] | Must be >= 2.5 | QA Checklist | Use the submitted installation report to verify existing flow rate of the showerhead is listed | The existing flow rate needs to be greater than 2.5 gallons per minute (gpm) and match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom |  | Add | 24
0 | SWWH020 | 3 | Low-Flow Showerhead, Commercial | Any | Any | Any |  | EECP | 4 | good to have | Yes | Flow Rate | Flow Rate of Installed Unit (gpm) | Numeric Value | [9 empty] | QA Checklist | Use the submitted invoice, installation report, or manufacturer spec sheet to validate the new showerhead flow rate is listed | The flow rate of the installed unit must match the flow entered in EECP and be less than or equal to the flowrate required by the measure. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Remove validation criteria, measure description captures the measure case flow rate | 2021-08-19 | Kenny Liljestrom |  | Add | 33
0 | SWWH020 | 3 | Low-Flow Showerhead, Commercial | Any | Any | Any |  | EECP | 5 | This measure is excluded from newly constructed buildings, additions to existing buildings, and alterations to existing buildings. | Yes | Unit Installed Building Type | Is the unit being installed in a newly constructed buildings, additions to existing buildings, and alterations to existing buildings? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | QA Checklist | Use the submitted invoice, installation report, or manufacturer spec sheet to validate the new showerhead flow rate is listed | The flow rate of the installed unit must match the flow entered in EECP and be less than or equal to the flowrate required by the measure. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-08-19 | Kenny Liljestrom |  | Add | 133
0 | SWWH020 | 3 | Low-Flow Showerhead, Commercial | Any | Any | Any |  | EECP | 6 | The facility must have natural gas as the water heating source fuel. | Yes | Natural Gas WH | Does the facility utilize natural gas water heating equipment? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Ask the customer to show you where the hot water heater is located that serves the domestic hot water loads (faucets, showerheads, etc.); Photograph the water heater and nameplate to determine if the water heater is natural gas fired (yellow corrugated pipe into the burner) | The water heater serving the showerheads must be served by a natural gas fired water heater; the water heater nameplate should list the 'Input Rating' in Btu/hr, kBtu/hr, or MMBtu/hr | QA Checklist | Have the implementer provide photos of the water heater serving the showerheads; the photos can include a photo of the nameplate (showing make, model, and input rating) | The make and model can be used to locate the equipment specification sheet to identify the fuel type of the water heater, or the Input Rating can be used to identify the fuel type by having units of Btu/hr, kBtu/hr, or MMBtu/hr; The water heater must be served by natural gas |  | 2021-08-19 | Kenny Liljestrom |  | Add | 62
0 | SWWH020 | 3 | Low-Flow Showerhead, Commercial | Any | Any | Any |  | EECP | 7 | For accelerated replacement measure application type (MAT), this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers Customer/site information Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating Specific documentation requirements will be determined by the program administrator and will be specified in the program implementation plan. Program influence evidence can be demonstrated through one of the three alternatives listed in Section 7.3 of POEV 2.0. This measure establishes the program-level evidence of program influence by adopting the net-to-gross (NTG) ratio from prior program evaluation results. | Yes |  | Have all POE requirements spelled out in the workpaper been included in the program documentation? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | For accelerated replacement measure application type (MAT), this measure adopts the program-level “Preponderance of Evidence Assessment” described in Version 2.0 of the Accelerated Replacement Using Preponderance of Evidence report developed by the utilities and stakeholders to provide guidance for the California programs (“POEV 2.0”, see Section 7). R914 “Continued viability” and “program influence” must be demonstrated as the evidence of accelerated replacement. To demonstrate the viability of the pre-existing system or to show that the program is replacing equipment that is “installed and operating,” the customer must be approached by a direct install implementer. Additionally, the program must obtain and provide additional documentation, including (but not limited to) the following: Targeted segment of the market or customers Customer/site information Make/model of pre-existing equipment and/or Performance/flowrate measurements of pre-existing equipment, and/or Photograph of pre-existing equipment in place and operating Specific documentation requirements will be determined by the program administrator and will be specified in the program implementation plan. Program influence evidence can be demonstrated through one of the three alternatives listed in Section 7.3 of POEV 2.0. This measure establishes the program-level evidence of program influence by adopting the net-to-gross (NTG) ratio from prior program evaluation results. | Verify all POE requirements are included in the submitted influence documentation | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-08-19 | Kenny Liljestrom |  | Add | 98
1 | SWWH021 | 1 | Recirculation Pump Timer, Commercial | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2021-07-20 | Kenny Liljestrom |  | Add | 12
1 | SWWH021 | 1 | Recirculation Pump Timer, Commercial | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-07-20 | Kenny Liljestrom |  | Add | 5
1 | SWWH021 | 1 | Recirculation Pump Timer, Commercial | Any | Any | Any |  | EECP | 3 | Good to have | Yes |  | Size of Recirculation Pump Motor | Numeric Value | [9 empty] | Inspections | Photograph the equipment nameplate to capture the power rating (hp) | The listed power rating (hp) in EECP should match the nameplate | QA Checklist | Use the submitted installation report to validate the motor power rating (hp) is listed | The power rating (hp) listed in EECP should match what is listed in the installation report | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 32
1 | SWWH021 | 1 | Recirculation Pump Timer, Commercial | Any | Any | Any |  | EECP | 4 | Eligibility requirements for this measure include the following: • The building must have a hot water recirculation system that can be turned OFF entirely for a set period of the day and/or week. • The building must have a centralized, gas-fired, hot-water system with a constant-flow, fractional-horsepower, uncontrolled recirculation pump. • The timer device must have seven-day (or better) scheduling capabilities. • There is no restriction on manufacturer or brand-naming. | Yes |  | Building has hot water recirculation system that can be turned OFF for a set period time? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | QA Checklist | Use the manufacturer spec sheet to validate if the controls include allowing the system to be turned OFF entirely for a set period of the day and/or week. | The building must have a hot water recirculation system that can be turned OFF entirely for a set period of the day and/or week. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 89
1 | SWWH021 | 1 | Recirculation Pump Timer, Commercial | Any | Any | Any |  | EECP | 5 | Eligibility requirements for this measure include the following: • The building must have a hot water recirculation system that can be turned OFF entirely for a set period of the day and/or week. • The building must have a centralized, gas-fired, hot-water system with a constant-flow, fractional-horsepower, uncontrolled recirculation pump. • The timer device must have seven-day (or better) scheduling capabilities. • There is no restriction on manufacturer or brand-naming. | Yes |  | Hot water is central, gas-fired, constant-flow, fractional horsepower, uncontrolled recirc pump? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 96
1 | SWWH021 | 1 | Recirculation Pump Timer, Commercial | Any | Any | Any |  | EECP | 6 | Eligibility requirements for this measure include the following: • The building must have a hot water recirculation system that can be turned OFF entirely for a set period of the day and/or week. • The building must have a centralized, gas-fired, hot-water system with a constant-flow, fractional-horsepower, uncontrolled recirculation pump. • The timer device must have seven-day (or better) scheduling capabilities. • There is no restriction on manufacturer or brand-naming. | Yes |  | Does the installed timer device have seven-day (or better) scheduling capabilities? | Drop Down List | Yes;No; | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 83
1 | SWWH021 | 1 | Recirculation Pump Timer, Commercial | Any | Any | Any |  | EECP | 7 | This measure is applicable to existing buildings and is limited to the commercial building types specified below. • Healthcare – outpatient • Service – fitness • Office – large • Office – small • Education – primary • Education - secondary | Yes |  | Building Type | Drop Down List | Healthcare – outpatient ;Service – fitness;Office – large ;Office – small ;Education – primary;Education - secondary;Other; | [7 empty] | Must not be 'Other' | Inspections | While on site, observe the building type | The building type must be one of the following: Healthcare – outpatient , Service – fitness, Office – large , Office – small , Education – primary, Education - secondary | QA Checklist | Use the installation report or EECP to determine the building type | The building type must be one of the following: Healthcare – outpatient , Service – fitness, Office – large , Office – small , Education – primary, Education - secondary | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 13
1 | SWWH021 | 1 | Recirculation Pump Timer, Commercial | Any | Any | Any |  | EECP | 8 | This measure is excluded from newly constructed buildings, additions to existing buildings, and alterations to existing buildings. | Yes |  | Measure installed on a newly constructed, additions or alterations to an existing building? | Drop Down List | Yes;No; | [7 empty] | Must be No | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2021-07-20 | Kenny Liljestrom |  | Add | 91
0 | SWWH023 | 1 | Diverting Tub Spout with TSV, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWWH023 | 1 | Diverting Tub Spout with TSV, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWWH023 | 1 | Diverting Tub Spout with TSV, Residential | Any | Any | Any |  | EECP | 3 | Revisit | Yes | Receipt | Was a copy of the purchase receipt submitted? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Review the submitted documentation in EECP | A copy of the invoice should be included in the submitted documentation | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
0 | SWWH023 | 1 | Diverting Tub Spout with TSV, Residential | Any | Any | Any |  | EECP | 4 | Revisit | Yes | Natural Gas WH | Does the facility utilize natural gas water heating equipment? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | Inspections | Photograph the water heater showing the gas pipe (yellow pipe) going into the water heater; the nameplate showing the make and model will also suffice | The water heater must be fueled by natural gas | QA Checklist | An installation report may indicate the water heater type or make and model which can be used to check the type | The water heater must be fueled by natural gas |  | 2021-06-21 | Kenny Liljestrom |  | Add | 62
0 | SWWH023 | 1 | Diverting Tub Spout with TSV, Residential | Any | Any | Any |  | EECP | 5 | Revisit | Yes | IAPMO | Is the installed product certified by International Association of Plumbing and Mechanical Officials (IAPMO)? | Drop Down List | Yes;No | [7 empty] | Must be 'Yes' | QA Checklist | Cross reference the make and model with the IAPMO database | The product needs to be listed in the database | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 109
0 | SWWH023 | 1 | Diverting Tub Spout with TSV, Residential | Any | Any | Any |  | EECP | 6 | Revisit | Yes | Tankless | Does the facility utilize tankless water heaters? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | Inspections | Photograph the water heater and make note of the water heater type | Ensure it is not a tankless type water heater (typically installed on a wall inside/outside of the garage) | QA Checklist | The make and model of the water heater may be provided in an installation report | The water heater type should not be instantaneous or tankless |  | 2021-06-21 | Kenny Liljestrom |  | Add | 49
0 | SWWH023 | 1 | Diverting Tub Spout with TSV, Residential | Any | Any | Any |  | EECP | 7 | Revisit | Yes | Wall Mounted Diverter | Does the shower have a wall-mounted diverter? | Drop Down List | Yes;No | [7 empty] | Must be 'No' | Inspections | Photograph the shower layout | There should be no diverter between the showerhead and the tub spout | QA Checklist | A photograph of the shower layout showing the tub spout and showerhead | There should be no diverter between the tub spout and showerhead |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
0 | SWWH023 | 1 | Diverting Tub Spout with TSV, Residential | Any | Any | Any |  | EECP | 9 | Revisit | Yes | Flow Rate | Flow Rate of Installed Unit (gpm) | Numeric Value | [9 empty] | QA Checklist | Use the manufacturer spec sheet to validate the flow rate of the newly installed unit | The flow rate listed in EECP should match what is on the spec sheet | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 33
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | UpDeemed |  | EECP | 0 | E-5152 Data Collection Requirements | Yes | Site ID | Site ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  | Add | 7
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | UpDeemed |  | EECP | 5 | E-5152 Data Collection Requirements | Yes | Equipment ID | Equipment ID | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  | Add | 12
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | Any |  | EECP | 10 | E-5152 Data Collection Requirements | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 12
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | Any |  | EECP | 15 | E-5152 Data Collection Requirements | Yes | Model | Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 5
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | UpDeemed |  | EECP | 20 | E-5152 Data Collection Requirements | Yes | Serial Number | Serial Number | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the serial number | The listed serial number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the serial number is listed | The serial number in EECP should match what is listed in the invoice or installation report |  | 2022-06-13 | Kenny Liljestrom |  |  | 13
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | DnDeemed |  | EECP | 25 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Electrification Infrastructure | If site required electric infrastructure upgrades, have itemized invoices with costs been submitted? | Drop Down List | Yes;No;N/A; |  | Not Equal | No |  |  |  |  | Must be 'Yes' or 'N/A' | QA Checklist | If implementer answered 'Yes', review EECP documentation for additional invoice data | In addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer. These are defined in Decision 19‐08‐009: What is the existing fuel type for the existing equipment? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  | Add | 100
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | DnDeemDI |  | EECP | 25 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Electrification Infrastructure | If site required electric infrastructure upgrades, have itemized invoices with costs been submitted? | Drop Down List | Yes;No;N/A; |  | Not Equal | No |  |  |  |  | Must be 'Yes' or 'N/A' | QA Checklist | If implementer answered 'Yes', review EECP documentation for additional invoice data | In addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer. These are defined in Decision 19‐08‐009: What is the existing fuel type for the existing equipment? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 100
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | DnDeemed |  | EECP | 30 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Electrification Measures | List other electrification measures installed with the heat pump water heater | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 77
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | DnDeemDI |  | EECP | 30 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Electrification Measures | List other electrification measures installed with the heat pump water heater | Text Box | [9 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 77
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | DnDeemed |  | EECP | 35 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Electrification Measures Costs | If site had electrification measures, have itemized infrastructure costs invoices been submitted? | Drop Down List | Yes;No;N/A; |  | Not Equal | No |  |  |  |  | Must be 'Yes' or 'N/A' | QA Checklist | If implementer answered 'Yes', review EECP documentation for additional invoice data | In addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer. These are defined in Decision 19‐08‐009: What is the existing fuel type for the existing equipment? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 98
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | DnDeemDI |  | EECP | 35 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Electrification Measures Costs | If site had electrification measures, have itemized infrastructure costs invoices been submitted? | Drop Down List | Yes;No;N/A; |  | Not Equal | No |  |  |  |  | Must be 'Yes' or 'N/A' | QA Checklist | If implementer answered 'Yes', review EECP documentation for additional invoice data | In addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer. These are defined in Decision 19‐08‐009: What is the existing fuel type for the existing equipment? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 98
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | DnDeemed |  | EECP | 40 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Heater Fuel | If installed in a conditioned space, existing space heating fuel type | Drop Down List | Electric;Gas;Unconditioned; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 69
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | DnDeemDI |  | EECP | 40 | For downstream deemed and downstream direct-install delivery types, in addition to the standard information such as building type, climate zone, and capacity of the units, the following data must be submitted with each project application by the project developer: What is the existing fuel type for space heating? Did the site require any electric infrastructure upgrades for the proposed electrification measure? If yes, provide the itemized invoices with infrastructure upgrade costs. Did the owner install any other electrification measures at this site? If yes, list the measures and provide the itemized invoices with infrastructure upgrade costs (if any). | Yes | Heater Fuel | If installed in a conditioned space, existing space heating fuel type | Drop Down List | Electric;Gas;Unconditioned; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 69
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | A | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | B | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | C | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | D | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | E | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | F | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | G | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | H | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | I | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | J | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | K | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | M | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | O | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | P | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Q | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | R | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | S | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | T | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | U | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | V | Any | DnDeemed |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | A | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | B | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | C | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | D | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | E | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | F | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | G | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | H | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | I | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | J | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | K | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | M | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | O | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | P | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Q | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | R | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | S | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | T | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Tankless |  |  |  |  | Must be 'Tankless' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a tankless water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | U | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | V | Any | DnDeemDI |  | EECP | 45 | Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. Replacement of an “instantaneous” or “tankless” water heater does not qualify. | Yes | Existing Equipment Type | Existing water heater type | Drop Down List | Gas Storage;Heat Pump;Instantaneous;Tankless; |  | Equal | Gas Storage |  |  |  |  | Must be 'Gas Storage' | QA Checklist | The implementer should provide a photo or proof of the existing conditions of the water heating equipment; this can be done also with the make and model of the existing water heater | The existing water heater must be a storage tank water heater which can be verified by a photo or using the manufacturer specification sheet to validate the equipment type | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 26
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | Any |  | EECP | 50 | Existing base equipment must be disposed. | Yes | Disposal Method | Has the existing equipment been properly disposed of and not abandoned in place? | Drop Down List | Yes;No | [7 empty] | Must be Yes | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - | Not configured in original upload | 2022-06-13 | Kenny Liljestrom |  | Add | 80
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | NC | DnDeemed |  | EECP | 50 | NC is only eligible for downstream delivery under the following conditions. These are defined as new services in fuel substitution technical guidance: Measures are installed in new areas of an existing building, Measures are installed in a major renovation of an existing building, or Measures are installed in capacity expansions of existing systems to serve existing and/or new load retrofits that require a new energy service. | Yes | New Area | For NC, select the 'new services' condition | Drop Down List | New area;Major renovation;Capacity expansion; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  | Add | 43
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | Any |  | EECP | 55 | In addition, for midstream delivery method, the implementer should provide the retailer or distribution location where the product was sold, rated capacity, and proposed building type where the product will be installed. | Yes | Input Rating | Input rating (kBtu/hr) | Numeric Value |  |  |  |  | General | 0 |  | 2 | Must be >= 0 | [7 empty] | 2022-06-13 | Kenny Liljestrom |  |  | 22
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | A | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | B | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | C | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | D | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | E | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | F | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | G | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | H | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | I | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | J | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | K | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 56 | 75 | 0 | Must be > 55 and <= 75 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 55-gallons and less than or equal to 75-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 55-gallons and less than or equal to 75-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | M | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 75 |  | 0 | Must be > 75 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 75-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 75-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | O | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 45 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | P | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 45 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Q | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 45 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | R | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 45 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | S | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 0 | 45 | 0 | Must be <= 45 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be less than or equal to 45-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be less than or equal to 45-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | T | Any | Any |  | EECP | 60 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Only residential-style electric storage water heaters are eligible and the installed water heater storage capacity must be 45 gallons or greater. | Yes | Storage Capacity | Heat pump water heater storage capacity (gallons) | Numeric Value |  |  |  |  | General | 0 | 45 | 0 | Must be <= 45 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be less than or equal to 45-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be less than or equal to 45-gallons and match what is listed in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 49
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | A | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | B | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | C | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | D | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | E | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | F | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | G | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | H | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | I | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | J | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | K | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.33 |  | 2 | Must be >= 3.33 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | M | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.42 |  | 2 | Must be >= 3.42 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | O | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | P | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Q | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | R | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | S | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | T | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | U | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.5 |  | 2 | Must be >= 3.5 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | V | Any | Any |  | EECP | 65 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.5 |  | 2 | Must be >= 3.5 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 27
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | Any |  | EECP | 70 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: • Measure case equipment specifications including: o Manufacturer and model number o UEF o Storage volume in gallons o First Hour Rating (FHR) • Customer site information including: o Climate Zone o Building Type (for downstream measures) | Yes | FHR | First Hour Rating (FHR) | Numeric Value |  |  |  |  | General | 0 |  | 0 | Must be > 0 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The First Hour Rating (FHR) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-13 | Kenny Liljestrom |  |  | 23
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | UpDeemed |  | EECP | 190 | E-5152 Data Collection Requirements | Yes | ZC | Zip Code | Numeric Value |  |  |  |  | General |  |  | 0 |  | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 8
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | Any | UpDeemed |  | EECP | 195 | E-5152 Data Collection Requirements | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-13 | Kenny Liljestrom |  |  | 15
1 | SWWH025 | 4 | Heat Pump Water Heater, Residential, Fuel Substitution | Any | AR | Any |  | QA Checklist | 205 | Preponderance of evidence (POE) must be documented for all accelerated replacement application types. Notably, programs shall document if measure was replaced as a direct result of information, recommendations, and support provided by the program administrator, and programs shall require the collection and submission of documentation to ensure proper conformance to eligibility and implementation requirements. The following are the types of information that will be required for all projects: Customer/site information Specifications of existing equipment Proof that water heater is still operating as intended Existing water heater nameplate data with manufacturer date to confirm remaining useful life Replacement water heater information To document POE, the implementer must complete the provided the survey, or similar. R1539 | Yes | POE Docs | Have POE requirements in the measure package been included in uploaded documentation? | None | [9 empty] | QA Checklist | Review the POE documentation and determine if it is adequate based on required criteria. | The POE documentation needs to list the: Customer/site information, Specifications of existing equipment, Proof that water heater is still operating as intended, Existing water heater nameplate data with manufacturer date to confirm remaining useful life, Replacement water heater information. | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | Not configured in original upload | 2022-06-13 | Kenny Liljestrom |  |  | 85
0 | SWWH026 | 1 | Water Heater Pipe Wrap, Residential | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | Manufacturer | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 12
0 | SWWH026 | 1 | Water Heater Pipe Wrap, Residential | Any | Any | Any |  | EECP | 2 | - | Yes | Model | Model | Text Box | [9 empty] | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 5
0 | SWWH026 | 1 | Water Heater Pipe Wrap, Residential | Any | Any | Any |  | EECP | 3 | Program eligibility requirements for the addition of insulation to hot water and cold water pipes, within the first three feet of a storage water heater include: | Yes | Insulation Addition | Does the measure include addition of insulation to hot water and cold-water pipes within the first 3 feet of a storage water heater? | Drop Down List | Yes;No | [7 empty] | Must be Yes | Inspections | Photograph the pipe insulation, document whether or not the insulation is installed within 3-feet of the water heater. | The insulation must be located within approximately 3-feet of the storage tank water heater | QA Checklist | A photograph in the installation report may show the pipe wrap near the water heater | The pipe wrap must be located within 3-feet of the water heater or tank |  | 2021-06-21 | Kenny Liljestrom |  | Add | 132
0 | SWWH026 | 1 | Water Heater Pipe Wrap, Residential | Any | Any | Any |  | EECP | 4 | A minimum of 1-inch of pipe insulation must be added to existing bare pipe | Yes | Minimum Thickness | Was a minimum thickness of 1 inch of pipe insulation added to existing bare pipe? | Drop Down List | Yes;No | [7 empty] | Must be Yes | Inspections | Photograph the insulated piping showing both the insulation and any exposed piping | The insulation thickness should be greater than or equal to 1-inch and the piping should be either copper or steel (i.e. not PVC or other materials) | QA Checklist | The make and model of the insulation should indicate on the manufacturer specification sheet the insulation thickness | Insulation thickness should be greater than or equal to 1-inch; a photograph of the piping system in an installation report may show the type of piping installed, eligible types are copper and steel |  | 2021-06-21 | Kenny Liljestrom |  | Add | 81
0 | SWWH026 | 1 | Water Heater Pipe Wrap, Residential | Any | Any | Any |  | EECP | 5 | Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam, and rigid polyurethane foam | Yes | Type | Type of insulation for hot water pipes installed | Drop Down List | Elastomeric Foam;Rubber;Polyethylene Foam;UV-Resistant Polyethylene Foam;Rigid Polyurethane Foam | [8 empty] | QA Checklist | Cross-Check invoice or specification sheet with submitted data in EECP | Acceptable types of insulation should match EECP and are listed below: Elastomeric Foam; Rubber; Polyethylene Foam; UV-Resistant Polyethylene Foam; Rigid Polyurethane Foam | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 48
0 | SWWH026 | 1 | Water Heater Pipe Wrap, Residential | Any | Any | Any |  | EECP | 6 | Must be installed by an authorized implementer | Yes | Approved Contractor | Was the installation of the measure completed by a utility-approved contractor? | Drop Down List | Yes;No | [7 empty] | Must be Yes | QA Checklist | Cross-Check invoice with submitted data in EECP, determine if contractor is on Trade-Pro list | The trade pro from the installation report should be in the approved trade pro list | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 79
0 | SWWH026 | 1 | Water Heater Pipe Wrap, Residential | Any | Any | Any |  | EECP | 7 | Must verify no existing pipe insulation as the existing condition | Yes | Existing Insulation | Did the pipes have existing pipe insulation ? | Drop Down List | Yes;No | [7 empty] | Must be No | Inspections | Photograph of pipe insulation, look for signs of existing insulation which may include small pieces still glued to the pipe, glue lines along the piping, pieces of old insulation on the floor around the water heater. | There should not be any signs of previously installed insulation | QA Checklist | Photographs of the existing and installed measure piping systems; the existing system should not have any insulation installed | There should not be any signs of previously installed insulation |  | 2021-06-21 | Kenny Liljestrom |  | Add | 45
0 | SWWH026 | 1 | Water Heater Pipe Wrap, Residential | Any | Any | Any |  | EECP | 8 | This measure is not applicable for commercial or industrial applications. This measure is not eligible for new construction applications as defined by the California Plumbing Code. | Yes | New Construction | Was the measure installed in a new construction application? | Drop Down List | Yes;No | [7 empty] | Must be No | QA Checklist | Check the billing history in EECP; the customer should have several months of billing data | The building should be existing, not new | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-06-21 | Kenny Liljestrom |  | Add | 61
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | Any | Any | Any |  | EECP | 0 | - | Yes | Manufacturer | HPWH Manufacturer | Text Box | [9 empty] | Inspections | Photograph the nameplate of the heat pump water heater to capture the manufacturer | The manufacturer listed in EECP should match the nameplate on the equipment | QA Checklist | Use an installation report or invoice to determine the manufacturer of the heat pump water heater (HPWH) | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report |  | 2022-06-20 | Kenny Liljestrom |  |  | 17
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | Any | Any | Any |  | EECP | 5 | - | Yes | Model | HPWH Model | Text Box | [9 empty] | Inspections | Photograph the nameplate of the heat pump water heater to capture the model number | The model number listed in EECP should match the nameplate on the equipment | QA Checklist | Use an installation report or invoice to determine the model number of the heat pump water heater (HPWH) | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2022-06-20 | Kenny Liljestrom |  |  | 10
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | A | Any | Any |  | EECP | 10 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity | HPWH Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 31
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | B | Any | Any |  | EECP | 10 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity | HPWH Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 31
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | C | Any | Any |  | EECP | 10 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity | HPWH Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 31
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | D | Any | Any |  | EECP | 10 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity | HPWH Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 31
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | E | Any | Any |  | EECP | 10 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity | HPWH Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 31
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | F | Any | Any |  | EECP | 10 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity | HPWH Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 46 | 55 | 0 | Must be > 45 and <= 55 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 45-gallons and less than or equal to 55-gallons and match what is listed in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 31
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | G | Any | Any |  | EECP | 10 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity | HPWH Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 56 | 75 | 0 | Must be > 55 and <= 75 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 55-gallons and less than or equal to 75-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 55-gallons and less than or equal to 75-gallons and match what is listed in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 31
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | H | Any | Any |  | EECP | 10 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | Storage Capacity | HPWH Storage Capacity (gallons) | Numeric Value |  |  |  |  | General | 76 |  | 0 | Must be > 75 | Inspections | Photograph the equipment nameplate to capture the storage capacity | The storage capacity of the unit should be greater than 75-gallons and match what is listed in EECP | QA Checklist | Using the make and model, locate the equipment specifications and determine the storage volume of the equipment | The storage capacity of the unit should be greater than 75-gallons and match what is listed in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 31
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | A | Any | Any |  | EECP | 15 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 27
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | B | Any | Any |  | EECP | 15 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 27
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | C | Any | Any |  | EECP | 15 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 27
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | D | Any | Any |  | EECP | 15 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 27
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | E | Any | Any |  | EECP | 15 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.09 |  | 2 | Must be >= 3.09 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 27
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | F | Any | Any |  | EECP | 15 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.31 |  | 2 | Must be >= 3.31 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 27
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | G | Any | Any |  | EECP | 15 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.33 |  | 2 | Must be >= 3.33 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 27
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | H | Any | Any |  | EECP | 15 | The heat pump water heater must meet the storage capacity and minimum efficiency requirements set forth in the Measure Case Description. Existing base equipment must be disposed. In some cases, heat pump water heaters may contain multiple heat pump units. The efficiency of the measure case must be the efficiency of the package unit, not the efficiency of individual heat pumps that makeup the unit. Split-system heat pump unit assemblies are eligible. However, they shall be treated as one package of one or more heat pumps serving a storage tank. Efficiency and performance ratings for the entire package shall be provided by the manufacturer. The efficiency of an individual heat pump within the package shall not be sufficient. | Yes | UEF | Uniform Energy Factor (UEF) | Numeric Value |  |  |  |  | General | 3.42 |  | 2 | Must be >= 3.42 | QA Checklist | Use the manufacturer and model number to locate a specification or submittal sheet; the implementer may provide this as part of the enrollment package upload in EECP | The Uniform Energy Factor (UEF) on the submittal/specification sheet should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 27
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | Any | Any | Any |  | EECP | 20 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | FHR | HPWH First Hour Rating (FHR) | Numeric Value |  |  |  |  | General |  |  | 0 |  | QA Checklist | Use the make and model number in EECP to locate the specification sheet for the heat pump water heater to find the first hour rating (FHR); the specification sheet may have been submitted by the 3PI, so check the documents section of EECP | The FHR should match what is listed in EECP | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2022-06-20 | Kenny Liljestrom |  |  | 28
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | Any | Any | Any |  | EECP | 25 | Replacement of an "instantaneous" or "tankless" water heater does not qualify. | Yes | Disposal Method | Existing water heater was a storage tank style and disposed of (not retrofitted)? | Drop Down List | Yes;No; |  | Equal | Yes |  |  |  |  | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2022-06-20 | Kenny Liljestrom |  |  | 81
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | Any | Any | DnDeemed |  | EECP | 0 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | No | - | Building type | Drop Down List | Asm;Com;ECC;EPr;ERC;ESe;EUn;Gro;HGR;Hsp;Htl;MBT;MLI;Mtl;Nrs;OfL;OfS;RFF;RSD;Rt3;RtL;RtS;SCn;SUn;WRf; | [8 empty] | Inspections | Make note of the building type at the inspection site | The building type must match what is listed in EECP | QA Checklist | Use the installation report to determine the building type of the customer | The building type listed in EECP must match what is on the installation report | Property can be configured at the enrollment level | 2022-06-20 | Kenny Liljestrom | Property is configured at the enrollment level, don't need another property type |  | 13
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | Any | Any | Any |  | EECP | 190 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | ZC | Zip Code | Numeric Value |  |  |  |  | General |  |  | 0 |  | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-20 | Kenny Liljestrom |  |  | 8
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | Any | Any | Any |  | EECP | 195 | To ensure that the appropriate incentives, savings, and cost effectiveness values are applied for each application, the following data must be collected for each application: Measure case equipment specifications including: Manufacturer and model number UEF Storage volume in gallons First hour rating (FHR) Customer site information including: Climate zone Building type (for downstream measures) | Yes | ClimateZone | CA Climate Zone | Formula | [9 empty] | EECP | Trust Implementer response in EECP | Trust implementer response in EECP | - | - | - |  | 2022-06-20 | Kenny Liljestrom |  |  | 15
1 | SWWH031 | 1 | Heat Pump Water Heater, Commercial | Any | Any | Any |  | QA Checklist | 205 | Deployment of the program may require rebates or financial incentives to participants that exceed the incremental measure cost (IMC). Incentives or rebates that exceed the IMC for a measure must be justified by individual program administrators (PAs) in addendum to measure submissions to document program implementation practice prior to program implementation. | Yes | - | IMC | None | [9 empty] | QA Checklist | Deployment of the program may require rebates or financial incentives to participants that exceed the incremental measure cost (IMC). Incentives or rebates that exceed the IMC for a measure must be justified by individual program administrators (PAs) in addendum to measure submissions to document program implementation practice prior to program implementation. | No processing checks to be made for this property, just notice of measure requirements | - | - | - |  | 2022-06-20 | Kenny Liljestrom |  |  | 3
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any |  | EECP | 1 | - | Yes | Manufacturer | VFD Manufacturer | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the manufacturer | The listed manufacturer in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the manufacturer is listed | The manufacturer listed in EECP should match the manufacturer listed in the invoice or installation report | Quantity of measure should be limited to 1 in order to capture all the manufacturer and model numbers of the VFDs | 2021-11-23 | Kenny Liljestrom |  |  | 16
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any |  | EECP | 2 | - | Yes | Model | VFD Model | Text Box | [9 empty] | Inspections | Photograph the equipment nameplate to capture the model number | The listed model number in EECP should match the nameplate | QA Checklist | Use the submitted invoice or installation report to validate the model number is listed | The model number listed in EECP should match the model number listed in the invoice or installation report |  | 2021-11-23 | Kenny Liljestrom |  |  | 9
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any |  | EECP | 3 | The VFD must be installed on the pump motor with a minimum operation of 1,000 hours per year. | Yes |  | Pump annual hours of operation (hr/yr) | Numeric Value | [8 empty] | Must be >= 1000 | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 38
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any |  | EECP | 4 | To substantiate conformance with program requirements, the customer must supply an invoice or other supporting documentation that includes the following: • Quantity of VFDs • Type (well and/or booster) • Horsepower rating of motor(s) and VFD(s) • Area map showing physical location of pumps • Manufacturer make/models of each VFD installed | Yes |  | Pump type | Drop Down List | Well;Booster;Well and Booster; | [8 empty] | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 9
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any |  | EECP | 5 | To substantiate conformance with program requirements, the customer must supply an invoice or other supporting documentation that includes the following: • Quantity of VFDs • Type (well and/or booster) • Horsepower rating of motor(s) and VFD(s) • Area map showing physical location of pumps • Manufacturer make/models of each VFD installed | Yes |  | Pump horsepower (hp) | Numeric Value | [9 empty] | Inspections | Photograph the pump motor nameplate to capture the power (hp) rating | The pump horsepower (hp) on the motor nameplate should match what is listed in EECP | QA Checklist | Using a photograph or pump make and manufacturer, identify the motor horsepower | The pump horsepower must match what is listed in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 20
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any |  | EECP | 6 | To substantiate conformance with program requirements, the customer must supply an invoice or other supporting documentation that includes the following: • Quantity of VFDs • Type (well and/or booster) • Horsepower rating of motor(s) and VFD(s) • Area map showing physical location of pumps • Manufacturer make/models of each VFD installed The customer must have an existing electrically operated agricultural booster or well pump installed on site or plans to install a new agricultural booster or well pump. | Yes |  | A map of the pump service area has been submitted? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist | Review the submitted documents in the enrollment package or EECP for a map of the location the pump is/will serve | A map of the pump service location must be submitted by the customer or implementer | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 50
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any |  | EECP | 7 | The variable frequency drive (VFD) must be used to adjust operation of a pump to meet flow/pressure requirements and not be used simply as a soft starter or for cavitation control. | Yes |  | VFD is used for flow/pressure control, not for soft start or cavitation? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 72
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any |  | EECP | 8 | The pumping application must currently have the means to vary the pressure/flow (i.e. throttle valve, control valve, etc.). | Yes |  | Existing pump has means to vary the pressure or flow (i.e. throttle valve, control valve, etc.)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | QA Checklist |  |  | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP |  | 2021-11-23 | Kenny Liljestrom |  |  | 96
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any |  | EECP | 9 | The VFD must be installed on a pressurized irrigation system (no flood irrigation). | Yes |  | VFD is installed on a pressurized irrigation system (no flood irrigation)? | Drop Down List | Yes;No; | [7 empty] | Must be 'Yes' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 74
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any |  | EECP | 10 | This measure cannot be used for the following pumping applications: • A well pump used to fill a reservoir, • A well pump discharging directly into a canal, and/or • A mixed flow pump (high volume, low head). | Yes |  | Is the pump is used as a well pump to fill a reservoir or discharging into a canal? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 83
0 | SWWP002 | 2 | VFD on AG Pump | Any | Any | Any |  | EECP | 11 | This measure cannot be used for the following pumping applications: • A well pump used to fill a reservoir, • A well pump discharging directly into a canal, and/or • A mixed flow pump (high volume, low head). | Yes |  | Is the pump a mixed flow pump with high volume and low head? | Drop Down List | Yes;No; | [7 empty] | Must be 'No' | EECP | Trust Implementer response in EECP | Trust Implementer response in EECP | - | - | - |  | 2021-11-23 | Kenny Liljestrom |  |  | 60

## Field names
Category Fields | E-5152 |  | E-5152 |  | Combine fields | Permutation also |  | Inspection Documentation | QPL | MAT specific; video link | Formulas, Capacity
Workpaper ID | SWFS001 | SWAP006 | SWHC012 | SWHC001 | SWHC031 | SWCR017 | SWFS010 | SWHC038 | SWFS004 | SWWH001 | SWHC013 | SWFS003 | SWHC004 | SWHC005 | SWWH006 | SWHC018 | Measure ID | SWHC004
Revision # | 2 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 5 | 2 | Measure Version ID | 2
WP Name | Convection Oven, Commercial | Dishwasher, Residential | Classroom HVAC Occupancy Sensor | Wall Furnace, Residential | High Efficiency Furnace, Residential | High Efficiency Ultra-Low Temperature Freezers | Commercial Hand-Wrap Machine, Electric | Brushless Fan Motor Replacement, Residential | Griddle, Commercial | Faucet Aerator, Residential | Unitary Air-Cooled Ac Or Heat Pump, ≥ 65 kBtuh, Commercial | Combination Oven, Commercial | Space Heating Boiler | Water-Cooled Chiller | Tankless Water Heater, Commercial | VSD for HVAC Fan Controls, Commercial | Measure Name | Space Heating Boiler
WP Offering ID | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | A | D | E | Q | A | Any | Offering ID – Offering ID referenced from Offering ID value table within the measure | Any
MeasAppType | Any | Any | Any | Any | Any | Any | Any | Any | Any | AR | Any | Any | Any | Any | Any | Any | MeasAppType – Measure application type (choice) | Any
DeliveryType | Any | Any | UpDeemed | UpDeemed | UpDeemed | Any | Any | Any | Any | DnDeemDI | Any | Any | Any | Any | Any | Any | DeliveryType – Delivery type (choice) | Any
Vintage | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Any | Vintage – Building vintage (choice)
Property Fields
Sort Order | 2 | 1 | 5 | 2 | 8 | 3 | 3 | 3 | 5 | 4 | 39 | 34 | 11 | 36 | 6 |  | Sort Order – sequential/unique order of validation data records | 5
Source Record (Item from Workpaper requiring Property) | E-5152 Data Collection Requirements | E-5152 Data Collection Requirements | E-5152 Data Collection Requirements | E-5152 Data Collection Requirements | E-5152 Data Collection Requirements | This measure is applicable for the following existing building types Eun = Com-Education - University Hsp = Com-Health/Medical - Hospital IPH = Ind-Manufacturing Pharmaceutical MBT = Ind-Manufacturing Biotech | Used or rebuilt equipment are not eligible. | The HVAC system must be functional/operable and drawing power. | This measure includes electric and gas commercial griddles that are ENERGY STAR®-qualified or meet the requirements in the Measure Case Description. | The existing faucet must have a flow rate of at least 2.2 gpm. | E-5152 Data Collection Requirements | This measure includes new commercial steam/convection combination ovens that meet the requirements in the Measure Case Description. | The boiler must meet efficiency requirements based on input ratings and types shown in the Measure Case Description. | Units are required to meet both full load and integrated part load efficiency requirements specified in the Measure Case Description. | Measure Description | This measure requires the installation of a VSD and associated controls on a motor driving a ventilation fan. Eligibility requirements include: • The fan must be ≤ 100 hp. • As an add-on equipment installation, the VSD must be applied to the HVAC supply or return air system. • Any other throttling devices, such as inlet vanes or bypass dampers, and throttling valves, must be removed or permanently disabled. | Source Record – copied text from the measure package to directly connect to the Property Name.
Property Enabled | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes
Property Name | Model | Manufacturer | Serial Number | Equipment ID | RetailPrice | Building Type | New Equipment | Operational | Energy Star Qualified | Flow Rate | Capacity (kBtuh) | Steam Efficiency | Thermal Efficiency (%) | Full Load Energy Efficiency (kW/ton) | Energy Factor | Input Rating | Property Name – validation property name that can be chosen from a list of common properties or created as a custom entry. Common properties are preferred to drive consistency across measure packages. | RefNum
Property - Label | Model | Manufacturer | Serial Number | Equipment ID | Retail Price | Building Type | Is the equipment new (not used or rebuilt)? | Is the HVAC system functional/operable and drawing power? | ENERGY STAR Qualified? | Flow Rate of Installed Unit (gpm) | Cooling Capacity (kBtu/hr) | Steam Mode Cooking Efficiency (%) | Thermal Efficiency (%) | Full Load Energy Efficiency (kW/ton) | Uniform Energy Factor | Input rating (hp) | Property – Label – further description of the name to make the property easier to interpret; sometimes can be modified to a question. | AHRI Reference Number
Property - Installation - Control Type | Text Box | Text Box | Text Box | Text Box | Number | Drop Down List | Drop Down List | Drop Down List | Drop Down List | Number | Number | Number | Number | Number | Number | Number | Property - Installation - Control Type – choice (Date, List, Text, Number, Formula, None)
Property - Installation - Values - Custom | Any: Education – University;Health/Medical – Hospital;Manufacturing – Biotech;Manufacturing – Pharmaceuticals;Other;; Any: Yes;No; Any: Yes;No; Any: Yes;No | Property – Installation – Values – Custom – choice from List values
Property Comment | (comment should provide advice on what the photo should be taken of to capture the model number) | (comment should provide advice on what the photo should be taken of to capture the manufacturer) | (comment should provide advice on what the photo should be taken of to capture the serial number) | (add comment) | (add comment) | Building type from customer NAICS code can be different from application, but justification required (ie, customer affidavit) | (add comment) | (add comment) | (add comment) | (add comment) | (add comment) | (add comment) | (add comment) - are other efficiencies likely (combustion) | (add comment) | (add comment) - conversions? | (add comment) | Property Comment – measure specific comment to provide context or specific instructions
Validation Fields
Validation Rule | [5 empty] | Must not be 'Other' | Must be 'Yes' | Must be 'Yes' | Must be 'Yes' | Must be <= 2.2 | Must be 65 <= x < 134 | Must be >= 38% | Must be >= 83% | Must be <= 0.497 | Must be >= 0.81 | Must be ≤ 100 | Validation Rule – logical statement or assertion that describes the passing state
Validation criteria | [5 empty] | Not equal to Other | Equal to Yes | Equal to Yes | Yes | LTE 2.2 gpm | GTE 65 kBtu/hr and LT 134 kBtu/hr | GTE 38% | GTE 83% | LTE 0.497 kW/ton | GTE 0.81 | LTE 100 hp | Validation Criteria – logical statement of how the correct answer can vary (ie, Equal to, Greater than, etc)
Validation Correct Answer | [5 empty] | Not equal | Equal | Equal | Equal | LTE | GTE and LT | GTE | GTE | LTE | GTE | LTE | Validation Correct Answer – value that designates the passing criteria
Numeric Type | Any: US Dollars; Any: Number; A: Number; D: Percentage; E: Percentage; Q: Number; A: Number; Any: Number | Numeric Type – number type (currency, number, percent, none)
Min Value | A: 65; D: 38%; E: 83%; Q: 0; A: 0.81; Any: 0 | Min Value – minimum range of the value allowed
Max Value | Any: 2.2; A: 134; D: 100%; E: 100%; Q: 0.497; A: 1; Any: 100 | Max Value – maximum range of the value allowed
Decimal Places | [16 empty] | Decimal Places
Validation Checkpoint | Inspections | Inspections | Application | Application | Application | QA Checklist | QA Checklist | Inspections | QA Checklist | QA Checklist | Inspections | QA Checklist | Inspections | QA Checklist | QA Checklist | Inspections | Validation Checkpoint – when is data expected to be collected (Application, Inspection, QA Checklist) | EECP
Validation Verification | Photograph of the nameplate showing the model number of the unit | Photograph the equipment nameplate to capture the manufacturer | Trust Implementer response in application | Trust Implementer response in application | Trust Implementer response in application | Verify the building type is Education – University; Health/Medical – Hospital; Manufacturing – Biotech; or Manufacturing – Pharmaceuticals | Use the submitted invoice or installation report to validate the equipment is new | Ask the customer if they are able to start the AC unit and observe the equipment (outdoor condenser and indoor vents) | Use the EnergyStar database and compare the listed make and model in application to the list | Cross check manufacturer and model number with flow rate | Photograph the equipment nameplate to capture the capacity (tons or Btu/hr) | Using the submitted manufacturer spec sheet, validate the Steam Mode Cooking Efficiency (%) | Photograph the equipment nameplate to capture the equipment thermal efficiency (%) | Use the submitted invoice, installation report, or spec sheet to validate the Full Load Efficiency (kW/ton) is listed | Use the manufacturer spec sheet to validate the Uniform Energy Factor | Photograph the nameplate of the HVAC Fan motor to capture the power rating, hp (if accessible and safe). | Validation Verification – What data should be used and how should data be used to validate this item | Trust Implementer response in EECP
Pass Criteria | The model number listed in application should match the model number listed on the nameplate | The listed manufacturer in the application should match the nameplate | Trust Implementer response in application | Trust Implementer response in application | Trust Implementer response in application | The building type must be Education – University; Health/Medical – Hospital; Manufacturing – Biotech; or Manufacturing – Pharmaceuticals | The equipment should be listed as new, not used or rebuilt | Check the HVAC system to see if it is energized and functional (operating without issues) | The database needs to have the make and model listed in application as being EnergyStar qualified; if not, criteria below must be met (https://www.energystar.gov/productfinder/product/certified-commercial-griddles/results) | The flow rate of the installed unit must match the flow entered in application and be less than or equal to the flowrate required by the measure. | The listed capacity in application should match the nameplate if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (Btu/hr) / 1,000 = kBtu/hr Capacity (tons) * 12 = kBtu/hr | The Steam Mode Cooking Efficiency (%) Must be >= 38% | The value on the nameplate should match what is listed in Application | The Full Load Efficiency listed in application should match the value listed in the invoice, installation report, or spec sheet; Value Must be <= 0.497 kW/ton | The Uniform Energy Factor Must be >= 0.81 | Use the nameplate power rating (hp) to validate what is listed in application; the power rating must be <= 100 hp | Pass Criteria – statement of what passing data should look like | Trust Implementer response in EECP AHRI - Boiler, Commercial Link: https://www.ahridirectory.org/NewSearch?programId=30&searchTypeId=3
Alternative Validation Fields | [17 empty] | -
Alternate Validation Checkpoint | QA Checklist | QA Checklist |  |  |  | Inspections | Application | QA Checklist | Application | Inspections | QA Checklist | Application | QA Checklist | Application | Application | QA Checklist | Alternate Validation Checkpoint – when is data expected to be collected; only required if primary validation data is not available | -
Alternate Validation Verification | Use the submitted invoice or installation report to validate the model number is listed | Use the submitted invoice or installation report to validate the manufacturer is listed |  |  |  | During inspection verify building type | Trust Implementer response in application | A detailed report from the implementer showing the baseline operating performance (tested data before and after) | Trust Implementer response in application | Using a measuring cup or flow rate measuring device, fill the device for 6 seconds, record the amount of Oz of water in the device; gallons per minute can be calculated as: Measured Oz * 0.078125 = GPM | Use the submitted invoice, installation report, or spec sheet to validate the capacity (in tons or Btu/hr) is listed | Trust Implementer response in application | Use the manufacturer specification sheet to validate the Thermal Efficiency (%) is listed | Trust Implementer response in application | Trust Implementer response in application | Use photographs of the manufacturer spec sheet to validate the power rating (hp) of the fan motor | Alternate Validation Verification – how should data be used to validate this item | -
Alternate Pass Criteria | The model number listed in application should match the model number listed in the invoice or installation report | The manufacturer listed in system should match the manufacturer listed in the invoice or installation report |  |  |  | The building type must be Education – University; Health/Medical – Hospital; Manufacturing – Biotech; or Manufacturing – Pharmaceuticals | Trust Implementer response in application | The existing conditions should show before data values indicating the fan was working | Trust Implementer response in application | The flow rate of the installed unit must match the flow entered in application and be less than or equal to the flowrate required by the measure. | The listed capacity in application should match the invoice, installation report, or spec sheet if listed in tons; if the capacity on the nameplate is listed in Btu/hr, the conversion from Btu/hr to kBtu/hr can be done with the following formula: Capacity (Btu/hr) / 1,000 = kBtuh Capacity (tons) * 12 = kBtu/hr | Trust Implementer response in application | The Thermal Efficiency (%) listed in application should match the value listed in the specification sheet | Trust Implementer response in application | Trust Implementer response in application | The power rating of the fan motor must be <= 100 hp | Alternate Pass Criteria – statement of what passing data should look like
Additional Flags
Data Use Category (Eligibility / EM&V) | EM&V | EM&V | EM&V | EM&V | EM&V | Eligibility | Eligibility | Eligibility | Eligibility | Eligibility | EM&V | Eligibility | Eligibility | Eligibility | Eligibility | Eligibility | Data Use Category (Eligibility / EM&V) – choice on whether the data is used to determine eligibility (‘Eligibility’) or required as part of a data collection requirement (‘EM&V’) | Eligibility
Check (Required / Recommended) | Required | Required | Required | Required | Required | Required | Required | Required | Required | Required | Required | Required | Required | Required | Required | Required | Check (Required / Recommended) – choice on whether data is 'Required’ since it is explicitly documented in the measure package or ‘Recommended’ | Required
Note on B1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Note that "E-5152" up/mid requirement, but any delivery type. Reply: Compare to Column E (SWHC012)
Note on D1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should there be items where the Application is the only check - ie, not also part of inspection process.
Note on F1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: We are likely to combine "Property-Installation-Control Type" and "Numeric Type". Concerns.
Note on G1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should Validation Criteria ever overlap with something that is captured in the permutation list?
Note on I1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should there be detail on how to document the answer to an inspection question?
Note on J1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: How should QPLs be integrated now and in the future? - Add a separate field? Reply: Would you need multiple links sometimes?
Note on K1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Are AR requirements handled differently? Complex example of procedure for checking - could include a video? Reply: Potential rejection from AR may convert to NR.
Note on L1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Formulas: What does the format of the equation need to look like to integrate with PA systems? Can we consider removing "Validation Criteria"? Capacity: Be careful about units - many need several "Capacity" items. Reply: Who are the right contacts at PAs?

## Property Name
Category Fields
Workpaper ID | SWHC018 | Measure ID
Revision # | 2 | Measure Version ID
WP Name | VSD for HVAC Fan Controls, Commercial | Measure Name
WP Offering ID | Any | Offering ID – Offering ID referenced from Offering ID value table within the measure
MeasAppType | Any | MeasAppType – Measure application type (choice)
DeliveryType | Any | DeliveryType – Delivery type (choice)
Vintage | Any | Vintage – Building vintage (choice)
Property Fields
Sort Order | 1 | Sort Order – sequential/unique order of validation data records
Source Record (Item from Workpaper requiring Property) | This measure requires the installation of a VSD and associated controls on a motor driving a ventilation fan. Eligibility requirements include: • The fan must be ≤ 100 hp. | Source Record – copied text from the measure package to directly connect to the Property Name. | How much should be copied; should some text be formatted (for emphasis)? Previously tried "linking", but this becomes very complex when we consider that text can change with versioning.
Property Enabled | Yes
Property Name | Input Rating (HP) | Property Name – validation property name that can be chosen from a list of common properties or created as a custom entry. Common properties are preferred to drive consistency across measure packages. | Some properties vary across equipment types, such as capacity. Should there be multiple options in the common library for capacity (as an example)? Should these ever include Properties already covered by permutations (BT, CZ, etc)
Property - Label | What is the input power rating on the fan motor (HP)? | Property – Label – further description of the name to make the property easier to interpret; sometimes can be modified to a question. | Should the Label and Comment be combined?
Property - Installation - Control Type | Number | Property - Installation - Control Type – choice (Date, List, Text, Number, Formula, None) | Should the Numeric Type be integrated, so that Number becomes currency, number, or percentage.
Property - Installation - Values - Custom |  | Property – Installation – Values – Custom – choice from List values | Examples: Yes, No AC, HP CZ01, CZ02, ...
Property Comment | Input power located typically on the motor, not the fan. | Property Comment – measure specific comment to provide context or specific instructions | Should the Label and Comment be combined?
Validation Fields
Validation Rule | Must be ≤ 100 hp | Validation Rule – logical statement or assertion that describes the passing state
Validation Criteria | LTE 100 hp | Validation Criteria – logical statement of how the correct answer can vary (ie, Equal to, Greater than, etc)
Validation Correct Answer | LTE | Validation Correct Answer – value that designates the passing criteria
Numeric Type | General | Numeric Type – number type (currency, number, percent, none)
Min Value | 0 | Min Value – minimum range of the value allowed
Max Value | 100 | Max Value – maximum range of the value allowed
Decimal Places |  | Decimal Places
Validation Checkpoint | Inspections | Validation Checkpoint – when is data expected to be collected (Application, Inspection, QA Checklist)
Validation Verification | Photograph the nameplate of the HVAC Fan to capture the power rating, hp (if accessible). | Validation Verification – What data should be used and how should data be used to validate this item
Pass Criteria | Use the nameplate power rating (hp) to validate what is listed in application; the power rating must be <= 100 hp | Pass Criteria – statement of what passing data should look like
Alternative Validation Fields
Alternate Validation Checkpoint | QA Checklist | Alternate Validation Checkpoint – when is data expected to be collected; only required if primary validation data is not available
Alternate Validation Verification | Use photographs of the manufacturer spec sheet to validate the power rating (hp) of the fan motor | Alternate Validation Verification – how should data be used to validate this item
Alternate Pass Criteria | The power rating of the fan must be <= 100 hp | Alternate Pass Criteria – statement of what passing data should look like
Additional Flags
Data Use Category (Eligibility / EM&V) | Eligibility | Data Use Category (Eligibility / EM&V) – choice on whether the data is used to determine eligibility (‘Eligibility’) or required as part of a data collection requirement (‘EM&V’)
Check (Required / Recommended) | Required | Check (Required / Recommended) – choice on whether data is 'Required’ since it is explicitly documented in the measure package or ‘Recommended’

## Validation Rule
Category Fields
Workpaper ID | SWHC018 | Measure ID
Revision # | 2 | Measure Version ID
WP Name | VSD for HVAC Fan Controls, Commercial | Measure Name
WP Offering ID | Any | Offering ID – Offering ID referenced from Offering ID value table within the measure
MeasAppType | Any | MeasAppType – Measure application type (choice)
DeliveryType | Any | DeliveryType – Delivery type (choice)
Vintage | Any | Vintage – Building vintage (choice)
Property Fields
Sort Order | 1 | Sort Order – sequential/unique order of validation data records
Source Record (Item from Workpaper requiring Property) | This measure requires the installation of a VSD and associated controls on a motor driving a ventilation fan. Eligibility requirements include: • The fan must be ≤ 100 hp. | Source Record – copied text from the measure package to directly connect to the Property Name.
Property Enabled | Yes
Property Name | Input Rating (HP) | Property Name – validation property name that can be chosen from a list of common properties or created as a custom entry. Common properties are preferred to drive consistency across measure packages.
Property - Label | What is the input power rating on the fan motor (HP)? | Property – Label – further description of the name to make the property easier to interpret; sometimes can be modified to a question.
Property - Installation - Control Type | Number | Property - Installation - Control Type – choice (Date, List, Text, Number, Formula, None)
Property - Installation - Values |  | Property – Installation – Values – Custom – choice from List values
Property Comment |  | Property Comment – measure specific comment to provide context or specific instructions
Validation Fields
Validation Rule | Must be ≤ 100 hp | Validation Rule – logical statement or assertion that describes the passing state | Question: Do we need to be careful to avoid the CEDARS non-ascii characters?
Validation Criteria | LTE 100 hp | Validation Criteria – logical statement of how the correct answer can vary (ie, Equal to, Greater than, etc) | Question for PAs: Is there a special format that this equation should take to best be input by your systems?
Validation Correct Answer | LTE | Validation Correct Answer – value that designates the passing criteria | Should this value only be filled in when it is a clear choice or set of choices?
Numeric Type | Number | Numeric Type – number type (currency, number, percent, none) | Do we need the "formula" choice?
Min Value | 3 | Min Value – minimum range of the value allowed
Max Value | 100 | Max Value – maximum range of the value allowed
Decimal Places | 0 | Decimal Places | Recommend deleting - will be handled by unit type. Does it provide value to external systems?
Validation Checkpoint | Inspections | Validation Checkpoint – when is data expected to be collected (Application, Inspection, QA Checklist) | Are there only three QC checkpoints: Application - confirm data directly entered in the application QA Checklist - take data supplied with the application to validate item Inspection - on site inspection data used to validate item
Validation Verification | Photograph the nameplate of the HVAC fan motor to capture the power rating, hp (if accessible). | Validation Verification – What data should be used and how should data be used to validate this item
Pass Criteria | Use the nameplate power rating (hp) to validate what is listed in application; the power rating must be <= 100 hp | Pass Criteria – statement of what passing data should look like | * Should there be a separate field for the QPL list / location if that exists so that links can be included here?
Alternative Validation Fields
Alternate Validation Checkpoint | QA Checklist | Alternate Validation Checkpoint – when is data expected to be collected; only required if primary validation data is not available | Will we ever need a second alternate? Should the Alternate provide guidance on what to do if check is not clear.
Alternate Validation Verification | Use photographs of the manufacturer spec sheet to validate the power rating (hp) of the fan motor | Alternate Validation Verification – how should data be used to validate this item
Alternate Pass Criteria | The power rating of the fan must be <= 100 hp | Alternate Pass Criteria – statement of what passing data should look like
Additional Flags
Data Use Category (Eligibility / EM&V) | Eligibility | Data Use Category (Eligibility / EM&V) – choice on whether the data is used to determine eligibility (‘Eligibility’) or required as part of a data collection requirement (‘EM&V’) | Question for EM&V: How should verification change around the EM&V related items?
Check (Required / Recommended) | Required | Check (Required / Recommended) – choice on whether data is 'Required’ since it is explicitly documented in the measure package or ‘Recommended’ | Expect that recommended items are more focused on quality installation; should there be a process to transition recommended to required OR required to recommended. Should there be a comment on sensitivity due to this parameter.

## Category Fields
Category Fields
Workpaper ID | SWHC018 | Measure ID
Revision # | 02 | Measure Version ID
WP Name | VSD for HVAC Fan Controls, Commercial | Measure Name
WP Offering ID | Any | Offering ID – Offering ID referenced from Offering ID value table within the measure | Example: Common for HVAC (SEER between X and Y)
MeasAppType | Any | MeasAppType – Measure application type (choice) | Example: AR MAT may have additional POE requirements or existing conditions requirements
DeliveryType | Any | DeliveryType – Delivery type (choice) | Example: Upstream may have required Data Collection fields. DnDeemDI may have existing condition data.
Vintage | Any | Vintage – Building vintage (choice) | I don't have a good example... Should there be other category fields?
Property Fields
Sort Order | 1 | Sort Order – sequential/unique order of validation data records
Source Record (Item from Workpaper requiring Property) | This measure requires the installation of a VSD and associated controls on a motor driving a ventilation fan. Eligibility requirements include: • The fan must be ≤ 100 hp. | Source Record – copied text from the measure package to directly connect to the Property Name.
Property Enabled | Yes
Property Name | Input Rating (HP) | Property Name – validation property name that can be chosen from a list of common properties or created as a custom entry. Common properties are preferred to drive consistency across measure packages.
Property - Label | What is the input power rating on the fan motor (HP)? | Property – Label – further description of the name to make the property easier to interpret; sometimes can be modified to a question.
Property - Installation - Control Type | Number | Property - Installation - Control Type – choice (Date, List, Text, Number, Formula, None)
Property - Installation - Values - Custom |  | Property – Installation – Values – Custom – choice from List values
Property Comment | Input power located typically on the motor, not the fan. | Property Comment – measure specific comment to provide context or specific instructions
Validation Fields
Validation Rule | Must be ≤ 100 hp | Validation Rule – logical statement or assertion that describes the passing state
Validation Criteria | LTE 100 hp | Validation Criteria – logical statement of how the correct answer can vary (ie, Equal to, Greater than, etc)
Validation Correct Answer | LTE | Validation Correct Answer – value that designates the passing criteria
Numeric Type | General | Numeric Type – number type (currency, number, percent, none)
Min Value | 0 | Min Value – minimum range of the value allowed
Max Value | 100 | Max Value – maximum range of the value allowed
Decimal Places |  | Decimal Places
Validation Checkpoint | Inspections | Validation Checkpoint – when is data expected to be collected (Application, Inspection, QA Checklist)
Validation Verification | Photograph the nameplate of the HVAC Fan to capture the power rating, hp (if accessible). | Validation Verification – What data should be used and how should data be used to validate this item
Pass Criteria | Use the nameplate power rating (hp) to validate what is listed in application; the power rating must be <= 100 hp | Pass Criteria – statement of what passing data should look like
Alternative Validation Fields
Alternate Validation Checkpoint | QA Checklist | Alternate Validation Checkpoint – when is data expected to be collected; only required if primary validation data is not available
Alternate Validation Verification | Use photographs of the manufacturer spec sheet to validate the power rating (hp) of the fan motor | Alternate Validation Verification – how should data be used to validate this item
Alternate Pass Criteria | The power rating of the fan must be <= 100 hp | Alternate Pass Criteria – statement of what passing data should look like
Additional Flags
Data Use Category (Eligibility / EM&V) | Eligibility | Data Use Category (Eligibility / EM&V) – choice on whether the data is used to determine eligibility (‘Eligibility’) or required as part of a data collection requirement (‘EM&V’)
Check (Required / Recommended) | Required | Check (Required / Recommended) – choice on whether data is 'Required’ since it is explicitly documented in the measure package or ‘Recommended’